## 02-02-2019 (hidden)
Performance Sheet Chiller
Date :- 02/02/2019
CHILLER NO. 02
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 14: 2.4; Hours 15: 2.4; Hours 16: 2.4; Hours 17: 2.3; Hours 18: 2.2; Hours 19: 2.2; Hours 20: 2.1; Hours 21: 2.1 | 2.2625
2 | Small temperature difference of evaporator | ºC |  | Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.3; Hours 18: 0.3; Hours 19: 0.3; Hours 20: 0.6; Hours 21: 0.6 | 0.45
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 14: 14.7; Hours 15: 14.7; Hours 16: 14.7; Hours 17: 13.8; Hours 18: 13.7; Hours 19: 13.5; Hours 20: 13.5; Hours 21: 13.2 | 13.975
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 14: 8.1; Hours 15: 8.1; Hours 16: 8.1; Hours 17: 7.8; Hours 18: 7.9; Hours 19: 7.9; Hours 20: 8; Hours 21: 7.8 | 7.9625
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 14: 25.1; Hours 15: 25.1; Hours 16: 25.1; Hours 17: 25.2; Hours 18: 25; Hours 19: 24.7; Hours 20: 24.2; Hours 21: 23.8 | 24.775
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 14: 30; Hours 15: 30; Hours 16: 30; Hours 17: 29.7; Hours 18: 29.3; Hours 19: 28.9; Hours 20: 28.3; Hours 21: 28 | 29.275
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 14: 2119.246; Hours 15: 2119.246; Hours 16: 2119.246; Hours 17: 1926.5873; Hours 18: 1862.3677; Hours 19: 1798.1481; Hours 20: 1766.0384; Hours 21: 1733.9286 | 15444.8082
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1400 | 1400 | 1200 | 1200 | 1200 | 1200 | 1100 | 1400 | [9 empty] | 10400
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 14: 0.66061; Hours 15: 0.66061; Hours 16: 0.56624; Hours 17: 0.62286; Hours 18: 0.64434; Hours 19: 0.66735; Hours 20: 0.62286; Hours 21: 0.80742 | 0.65654
17 | Average iKW/TR |  |  | Hours 7: 0.65654 | 0.65654
18 | COP of chiller |  |  | Hours 14: 5.3223; Hours 15: 5.3223; Hours 16: 6.2094; Hours 17: 5.6449; Hours 18: 5.4567; Hours 19: 5.2686; Hours 20: 5.6449; Hours 21: 4.3546 | 5.403
19 | EER of Chiller |  |  | Hours 14: 18.1651; Hours 15: 18.1651; Hours 16: 21.1927; Hours 17: 19.266; Hours 18: 18.6238; Hours 19: 17.9816; Hours 20: 19.266; Hours 21: 14.8624 | 18.4404
20 | LMTD of Condenser | ºC |  | Hours 14: 4.4049; Hours 15: 4.4049; Hours 16: 4.4049; Hours 17: 4.1512; Hours 18: 3.9692; Hours 19: 3.9332; Hours 20: 3.7871; Hours 21: 3.823 | 4.1098
21 | LMTD of Evaporator | ºC |  | Hours 14: 2.4875; Hours 15: 2.4875; Hours 16: 2.4875; Hours 17: 1.9708; Hours 18: 1.9255; Hours 19: 1.8799; Hours 20: 2.3716; Hours 21: 2.3452 | 2.2444
Performance Sheet Chiller
Date :- 02/02/2019
CHILLER NO. 06
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 3.5 | 3.3 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 2.7 | 2.4 | 2.5 | 2.3 | 2.4 | 2.3 | 2.3 | 2.7 | 2.7 | 2.9 | 2.5 | 2.7 | 2.6 | 2.8 | 2.9 | 3.2 | 2.8333
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.2 | 0.3 | 0.2 | 0.2 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.4 | 0.3 | 0.4 | 0.34583
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.3 | 13.7 | 13.7 | 13.7 | 13.8 | 13.8 | 14.3 | 15 | 14.6 | 13.8 | 13.8 | 13.6 | 13.5 | 13.2 | 13.3 | 13 | 12.3 | 13 | 13.3 | 13.5 | 13.6 | 13.6 | 13.7 | 13.5917
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.6 | 5.6 | 5.6 | 5.5 | 5.6 | 5.7 | 6 | 6.5 | 7.9 | 8 | 8 | 8.1 | 8 | 7.9 | 7.1 | 5.9 | 5.6 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.5 | 6.3083
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.2 | 19.8 | 19.8 | 20.1 | 20 | 20.7 | 22 | 22.7 | 22.9 | 24.9 | 25.4 | 25.1 | 24.8 | 24.3 | 24 | 23.6 | 24.4 | 22.3 | 21.1 | 20.9 | 21.3 | 22 | 21.9 | 22.1 | 22.3458
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 25.4 | 25 | 25.1 | 25.5 | 25.4 | 26.3 | 27.7 | 28.5 | 28.7 | 30 | 29.6 | 29 | 28.6 | 28.1 | 27.7 | 28 | 29.5 | 27 | 26.1 | 26.1 | 26.6 | 27.3 | 27.3 | 27.6 | 27.3375
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | `
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2472.4537 | 2600.8929 | 2600.8929 | 2633.0026 | 2633.0026 | 2600.8929 | 2665.1124 | 2729.332 | 2151.3558 | 1862.3677 | 1862.3677 | 1766.0384 | 1766.0384 | 1701.8188 | 1990.8069 | 2279.795 | 2151.3558 | 2408.2341 | 2504.5635 | 2568.7831 | 2568.7831 | 2568.7831 | 2633.0026 | 56127.9101
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1400 | 1500 | 1400 | 1600 | 1500 | 1300 | 1300 | 1100 | 1200 | 1000 | 1100 | 1200 | 1300 | 1400 | 1300 | 1300 | 1300 | 1500 | 1500 | 1600 | 1400 | 1500 | 32500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58134 | 0.56624 | 0.53828 | 0.57673 | 0.53171 | 0.60767 | 0.57673 | 0.48778 | 0.47631 | 0.51131 | 0.64434 | 0.53695 | 0.62286 | 0.67949 | 0.76389 | 0.70323 | 0.57023 | 0.60427 | 0.53981 | 0.59891 | 0.58393 | 0.62286 | 0.54501 | 0.56969 | 0.58498
17 | Average iKW/TR |  |  | Hours 7: 0.58498 | 0.58498
18 | COP of chiller |  |  | 6.0481 | 6.2094 | 6.532 | 6.0965 | 6.6126 | 5.786 | 6.0965 | 7.2081 | 7.3818 | 6.8765 | 5.4567 | 6.5481 | 5.6449 | 5.1745 | 4.6028 | 4.9998 | 6.166 | 5.8186 | 6.5133 | 5.8707 | 6.0212 | 5.6449 | 6.4513 | 6.1718 | 6.0805
19 | EER of Chiller |  |  | 20.6422 | 21.1927 | 22.2936 | 20.8073 | 22.5688 | 19.7477 | 20.8073 | 24.6013 | 25.1941 | 23.4695 | 18.6238 | 22.3486 | 19.266 | 17.6605 | 15.7092 | 17.0642 | 21.0445 | 19.8588 | 22.2301 | 20.0367 | 20.5504 | 19.266 | 22.0183 | 21.0642 | 20.7528
20 | LMTD of Condenser | ºC |  | 5.7108 | 5.496 | 5.5333 | 5.4622 | 5.4622 | 5.5358 | 5.5724 | 5.6089 | 5.0575 | 4.4759 | 4.2604 | 3.9329 | 4.0039 | 3.8959 | 3.8588 | 4.5509 | 4.8074 | 4.8784 | 4.5512 | 4.8435 | 4.769 | 4.9894 | 5.1353 | 5.4991 | 4.9121
21 | LMTD of Evaporator | ºC |  | 2.5141 | 2.5597 | 2.6502 | 2.6502 | 2.6727 | 2.6727 | 2.6502 | 2.6951 | 2.5157 | 2.1271 | 2.1161 | 1.7053 | 1.857 | 1.6418 | 1.5992 | 2.2116 | 2.215 | 2.1271 | 2.5141 | 2.5824 | 2.4095 | 2.6277 | 2.4095 | 2.6727 | 2.3499

## 03-02-2019 (hidden)
Performance Sheet Chiller
Date :- 03/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 13: 2.6; Hours 14: 2.4; Hours 15: 2.4; Hours 16: 2.4; Hours 17: 2.2; Hours 18: 2.2; Hours 19: 2.2; Hours 20: 2.2; Hours 21: 2.1; Hours 22: 2.1; Hours 23: 2.2 | 2.2727
2 | Small temperature difference of evaporator | ºC |  | Hours 13: 0.3; Hours 14: 0.3; Hours 15: 0.3; Hours 16: 0.3; Hours 17: 0.3; Hours 18: 0.3; Hours 19: 0.4; Hours 20: 0.3; Hours 21: 0.3; Hours 22: 0.3; Hours 23: 0.3 | 0.30909
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 13: 14.3; Hours 14: 15; Hours 15: 14.4; Hours 16: 14.3; Hours 17: 14.3; Hours 18: 14.3; Hours 19: 14.3; Hours 20: 14; Hours 21: 13.9; Hours 22: 13.8; Hours 23: 13.8 | 14.2182
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 13: 10.1; Hours 14: 8.1; Hours 15: 7.8; Hours 16: 8; Hours 17: 8; Hours 18: 7.9; Hours 19: 7.9; Hours 20: 8; Hours 21: 8; Hours 22: 7.9; Hours 23: 7.9 | 8.1455
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 13: 19.3; Hours 14: 25.1; Hours 15: 26.6; Hours 16: 26.6; Hours 17: 26.2; Hours 18: 26.6; Hours 19: 26; Hours 20: 25.7; Hours 21: 25.5; Hours 22: 25; Hours 23: 25 | 25.2364
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 13: 24.3; Hours 14: 29.3; Hours 15: 30.8; Hours 16: 30.6; Hours 17: 30.2; Hours 18: 30.7; Hours 19: 30.1; Hours 20: 29.6; Hours 21: 29.3; Hours 22: 28.8; Hours 23: 28.7 | 29.3091
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 13: 1348.6111; Hours 14: 2215.5754; Hours 15: 2119.246; Hours 16: 2022.9167; Hours 17: 2022.9167; Hours 18: 2055.0265; Hours 19: 2055.0265; Hours 20: 1926.5873; Hours 21: 1894.4775; Hours 22: 1894.4775; Hours 23: 1894.4775 | 21449.3386
15 | Power Consumption of Chiller | KWH |  | Hours 13: 1400; Hours 14: 1400; Hours 15: 1300; Hours 16: 1300; Hours 17: 1300; Hours 18: 1300; Hours 19: 1300; Hours 20: 1300; Hours 21: 1400; Hours 22: 1400; Hours 23: 1400 | 14800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 13: 1.0381; Hours 14: 0.63189; Hours 15: 0.61343; Hours 16: 0.64264; Hours 17: 0.64264; Hours 18: 0.6326; Hours 19: 0.6326; Hours 20: 0.67477; Hours 21: 0.73899; Hours 22: 0.73899; Hours 23: 0.73899 | 0.70233
17 | Average iKW/TR |  |  | Hours 7: 0.70233 | 0.70233
18 | COP of chiller |  |  | Hours 13: 3.3869; Hours 14: 5.5643; Hours 15: 5.7317; Hours 16: 5.4712; Hours 17: 5.4712; Hours 18: 5.5581; Hours 19: 5.5581; Hours 20: 5.2107; Hours 21: 4.7578; Hours 22: 4.7578; Hours 23: 4.7578 | 5.1114
19 | EER of Chiller |  |  | Hours 13: 11.5596; Hours 14: 18.9908; Hours 15: 19.5624; Hours 16: 18.6732; Hours 17: 18.6732; Hours 18: 18.9696; Hours 19: 18.9696; Hours 20: 17.784; Hours 21: 16.2385; Hours 22: 16.2385; Hours 23: 16.2385 | 17.4453
20 | LMTD of Condenser | ºC |  | Hours 13: 4.6614; Hours 14: 4.1518; Hours 15: 4.1518; Hours 16: 4.0782; Hours 17: 3.8607; Hours 18: 3.897; Hours 19: 3.897; Hours 20: 3.8242; Hours 21: 3.6786; Hours 22: 3.6786; Hours 23: 3.7507 | 3.9663
21 | LMTD of Evaporator | ºC |  | Hours 13: 1.5509; Hours 14: 2.1711; Hours 15: 2.1049; Hours 16: 2.0381; Hours 17: 2.0381; Hours 18: 2.0605; Hours 19: 2.2589; Hours 20: 1.9708; Hours 21: 1.9481; Hours 22: 1.9481; Hours 23: 1.9481 | 2.0034
Performance Sheet Chiller
Date :- 03/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 3.2 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3 | 2.7 | 2.7 | 2.7 | 2.5 | 2.8 | 2.8 | 2.8 | 2.6 | 2.6 | 2.8 | 2.9 | 2.5 | 2.9 | 2.9 | 3 | 3.1 | 3.1 | 3.2 | 2.9375
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.46667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.6 | 13.7 | 14 | 14 | 14.2 | 14.3 | 14.8 | 15 | 14.4 | 14.3 | 14.2 | 14.2 | 14.2 | 14 | 13.8 | 13.7 | 13.7 | 13.5 | 12.1 | 12.7 | 13.4 | 13.7 | 13.7 | 13.7 | 13.8708
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.5 | 5.6 | 5.7 | 5.7 | 5.9 | 6.3 | 8 | 8 | 8 | 7.9 | 8 | 8 | 7.8 | 8 | 8 | 8 | 6.1 | 5.3 | 5.6 | 5.5 | 5.6 | 5.5 | 5.6 | 6.6333
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.9 | 22 | 21.6 | 21.2 | 21.5 | 22.2 | 22.4 | 24.7 | 26.5 | 26.3 | 26.1 | 26.4 | 25.7 | 25.6 | 25.1 | 24.8 | 24.7 | 25.6 | 25.3 | 22.6 | 22.4 | 22.2 | 22 | 21.9 | 23.7792
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.5 | 27.5 | 27.2 | 27 | 27.1 | 27.7 | 28.1 | 29.6 | 31.1 | 30.8 | 30.5 | 30.8 | 30.3 | 30 | 29.3 | 29.1 | 28.8 | 30.7 | 30.1 | 27.4 | 27.7 | 27.7 | 27.4 | 27.6 | 28.7917
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2633.0026 | 2697.2222 | 2665.1124 | 2729.332 | 2697.2222 | 2729.332 | 2247.6852 | 2055.0265 | 2022.9167 | 2022.9167 | 1990.8069 | 1990.8069 | 1990.8069 | 1862.3677 | 1830.2579 | 1830.2579 | 2376.1243 | 2183.4656 | 2279.795 | 2536.6733 | 2600.8929 | 2633.0026 | 2600.8929 | 55774.7024
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1300 | 1300 | 1300 | 1300 | 1300 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 33100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.54501 | 0.53171 | 0.51905 | 0.52531 | 0.51295 | 0.51905 | 0.47631 | 0.57837 | 0.6326 | 0.64264 | 0.64264 | 0.70323 | 0.70323 | 0.70323 | 0.75173 | 0.76492 | 0.76492 | 0.58919 | 0.64118 | 0.61409 | 0.5519 | 0.53828 | 0.53171 | 0.53828 | 0.60506
17 | Average iKW/TR |  |  | Hours 7: 0.60506 | 0.60506
18 | COP of chiller |  |  | 6.4513 | 6.6126 | 6.7739 | 6.6932 | 6.8545 | 6.7739 | 7.3818 | 6.0791 | 5.5581 | 5.4712 | 5.4712 | 4.9998 | 4.9998 | 4.9998 | 4.6772 | 4.5966 | 4.5966 | 5.9675 | 5.4836 | 5.7255 | 6.3707 | 6.532 | 6.6126 | 6.532 | 5.9256
19 | EER of Chiller |  |  | 22.0183 | 22.5688 | 23.1193 | 22.844 | 23.3945 | 23.1193 | 25.1941 | 20.748 | 18.9696 | 18.6732 | 18.6732 | 17.0642 | 17.0642 | 17.0642 | 15.9633 | 15.6881 | 15.6881 | 20.367 | 18.7156 | 19.5413 | 21.7431 | 22.2936 | 22.5688 | 22.2936 | 20.2241
20 | LMTD of Condenser | ºC |  | 5.5358 | 5.7156 | 5.7527 | 5.7179 | 5.6444 | 5.6075 | 5.0221 | 4.7348 | 4.6249 | 4.3705 | 4.6587 | 4.6587 | 4.7332 | 4.4427 | 4.3686 | 4.6213 | 4.6527 | 4.5869 | 4.9155 | 4.9155 | 5.2081 | 5.3903 | 5.3536 | 5.5724 | 5.0335
21 | LMTD of Evaporator | ºC |  | 2.6277 | 2.6727 | 2.7175 | 2.8941 | 2.9408 | 2.7175 | 2.7399 | 2.1931 | 2.0605 | 2.0381 | 2.0381 | 2.0158 | 5.5328 | 2.0158 | 1.9255 | 1.9027 | 1.9027 | 2.2803 | 2.3526 | 2.4222 | 2.6051 | 2.4308 | 2.4521 | 2.6502 | 2.5054

## 04-02-2019 (hidden)
Performance Sheet Chiller
Date :- 04/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 2.5 | 1.9 | 2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.6 | 2.6 | 2.6 | 2.4 | 2.2 | 2.3 | 2.3 | 2.3 | 2.2 | 2.3 | 2.3 | 2.3 | 2.3 | 2.4 | 2.5 | 2.2909
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.4 | 0.3 | 0.2 | 0.4 | 0.3 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.8 | 0.9 | 0.9 | 0.44545
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 14.3 | 14.3 | 12.8 | 13 | 13.2 | 13.3 | 13.6 | 13.7 | 13.8 | 13.9 | 14.1 | 14.2 | 14.2 | 14.1 | 13.6 | 13 | 12.3 | 13.1 | 13.6 | 13.8 | 14 | 14.1 | 13.6364
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 8 | 8 | 7.9 | 8 | 8 | 8.1 | 8.1 | 8.1 | 8.1 | 8 | 8 | 8 | 8 | 7.2 | 7 | 6.1 | 5.5 | 5.7 | 6 | 6.2 | 6.3 | 6.4 | 7.3045
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 23.8 | 23.8 | 24.1 | 24.2 | 24.5 | 24.7 | 25.3 | 25.2 | 26.9 | 27.1 | 27.2 | 27.2 | 27 | 27.2 | 27.2 | 27.3 | 26 | 24.2 | 23.9 | 23.8 | 23.6 | 23.5 | 25.35
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 28.5 | 28.5 | 27.8 | 28.1 | 28.3 | 28.7 | 29.5 | 29.5 | 31.3 | 31.8 | 31.8 | 31.8 | 31.7 | 32.4 | 32.2 | 32.5 | 31.1 | 29.7 | 29.6 | 29.5 | 29.3 | 29.3 | 30.1318
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2022.9167 | 2022.9167 | 1573.3796 | 1605.4894 | 1669.709 | 1669.709 | 1766.0384 | 1798.1481 | 1830.2579 | 1894.4775 | 1958.6971 | 1990.8069 | 1990.8069 | 2215.5754 | 2119.246 | 2215.5754 | 2183.4656 | 2376.1243 | 2440.3439 | 2440.3439 | 2472.4537 | 2472.4537 | 44728.9352
15 | Power Consumption of Chiller | KWH |  |  |  | 1500 | 1600 | 1000 | 700 | 1200 | 1200 | 1300 | 1300 | 1400 | 1300 | 1600 | 1400 | 1600 | 1600 | 1500 | 1400 | 1700 | 1600 | 1600 | 1600 | 1600 | 1700 | 31400
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.7415 | 0.79094 | 0.63557 | 0.436 | 0.71869 | 0.71869 | 0.73611 | 0.72297 | 0.76492 | 0.68621 | 0.81687 | 0.70323 | 0.80369 | 0.72216 | 0.7078 | 0.63189 | 0.77858 | 0.67337 | 0.65565 | 0.65565 | 0.64713 | 0.68758 | 0.7016
17 | Average iKW/TR |  |  | Hours 7: 0.7016 | 0.7016
18 | COP of chiller |  |  |  |  | 4.7417 | 4.4454 | 5.532 | 8.0641 | 4.8922 | 4.8922 | 4.7765 | 4.8633 | 4.5966 | 5.1238 | 4.3042 | 4.9998 | 4.3748 | 4.8687 | 4.9675 | 5.5643 | 4.5159 | 5.2215 | 5.3627 | 5.3627 | 5.4332 | 5.1136 | 5.0917
19 | EER of Chiller |  |  |  |  | 16.1835 | 15.172 | 18.8807 | 27.5229 | 16.6972 | 16.6972 | 16.302 | 16.5984 | 15.6881 | 17.4876 | 14.6904 | 17.0642 | 14.9312 | 16.617 | 16.9541 | 18.9908 | 15.4128 | 17.8211 | 18.3027 | 18.3027 | 18.5436 | 17.4528 | 17.3779
20 | LMTD of Condenser | ºC |  |  |  | 4.4432 | 3.7744 | 3.5328 | 3.7149 | 3.6786 | 3.7511 | 3.823 | 4.4057 | 4.4427 | 4.5527 | 4.2973 | 4.0763 | 4.2228 | 4.3993 | 4.3291 | 4.2868 | 4.3643 | 4.5037 | 4.5727 | 4.5727 | 4.686 | 4.8335 | 4.2393
21 | LMTD of Evaporator | ºC |  |  |  | 2.5795 | 2.0381 | 1.7177 | 1.7411 | 1.7877 | 1.7877 | 2.0437 | 1.8799 | 1.9027 | 2.1401 | 1.9933 | 1.7889 | 2.2116 | 2.1711 | 2.1049 | 2.3759 | 2.7067 | 2.8568 | 2.9064 | 3.2322 | 3.4114 | 3.4114 | 2.3086
Performance Sheet Chiller
Date :- 04/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 3.2 | 3.2 | 2.6 | 2.1 | 2.2 | 2.3 | 2.3 | 2.2 | 2.4 | 2.5 | 2.5 | 2.5 | 2.6 | 2.6 | 2.3 | 2.3 | [8 empty] | 2.4875
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.2 | 0.2 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | [8 empty] | 0.2875 | 1
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.8 | 14 | 14.4 | 14.6 | 12.9 | 13.1 | 13.4 | 13.5 | 13.7 | 13.8 | 13.8 | 14 | 14.2 | 14.3 | 14.3 | 14.2 | [8 empty] | 13.875
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.6 | 5.9 | 8.1 | 8 | 7.8 | 8.1 | 8 | 8 | 8 | 8.1 | 8.1 | 7.9 | 8 | 8 | 7.1 | [8 empty] | 7.5187
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.9 | 22 | 21.7 | 23.7 | 24.2 | 24.3 | 24.6 | 24.7 | 25.2 | 25.3 | 26.5 | 27.2 | 27.2 | 27.2 | 27.1 | 27.3 | [8 empty] | 25.0063
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.4 | 27.3 | 27.3 | 28.2 | 27.7 | 28 | 28.2 | 28.6 | 29.2 | 29.5 | 30.8 | 31.8 | 31.6 | 31.7 | 31.5 | 32.3 | [8 empty] | 29.4438
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2633.0026 | 2697.2222 | 2729.332 | 2087.1362 | 1573.3796 | 1701.8188 | 1701.8188 | 1766.0384 | 1830.2579 | 1862.3677 | 1830.2579 | 1894.4775 | 2022.9167 | 2022.9167 | 2022.9167 | 2279.795 | [8 empty] | 32655.6548
15 | Power Consumption of Chiller | KWH |  | 1400 | 1200 | 1100 | 1100 | 1100 | 1000 | 1100 | 1100 | 1100 | 1300 | 1400 | 1200 | 1500 | 1300 | 1500 | 1500 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53171 | 0.4449 | 0.40303 | 0.52704 | 0.69913 | 0.58761 | 0.64637 | 0.62286 | 0.60101 | 0.69804 | 0.76492 | 0.63342 | 0.7415 | 0.64264 | 0.7415 | 0.65795 | [8 empty] | 0.62148
17 | Average iKW/TR |  |  | Hours 7: 0.62148 | 0.62148
18 | COP of chiller |  |  | 6.6126 | 7.9029 | 8.7239 | 6.6712 | 5.0291 | 5.9836 | 5.4396 | 5.6449 | 5.8502 | 5.037 | 4.5966 | 5.5508 | 4.7417 | 5.4712 | 4.7417 | 5.3438 | [8 empty] | 5.8338
19 | EER of Chiller |  |  | 22.5688 | 26.9725 | 29.7748 | 22.769 | 17.1643 | 20.422 | 18.5655 | 19.266 | 19.9666 | 17.1912 | 15.6881 | 18.9449 | 16.1835 | 18.6732 | 16.1835 | 18.2385 | [8 empty] | 19.9108
20 | LMTD of Condenser | ºC |  | 5.4991 | 5.4252 | 4.8754 | 3.9297 | 3.6764 | 3.8588 | 3.8215 | 3.8242 | 4.0782 | 4.2604 | 4.2973 | 4.407 | 4.4427 | 4.4795 | 4.1152 | 4.3291 | [8 empty] | 4.3325
21 | LMTD of Evaporator | ºC |  | 2.6727 | 2.7175 | 2.253 | 1.851 | 1.7177 | 1.5992 | 1.8109 | 1.857 | 1.9027 | 1.9255 | 1.9027 | 1.9481 | 2.0381 | 2.0381 | 1.8097 | 2.215 | [8 empty] | 2.0162

## 05-02-2019 (hidden)
Performance Sheet Chiller
Date :- 05/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.5 | 2.5 | 2.5 | 2.6 | 2.1 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 2 | 1.9 | 1.9 | 1.8 | 1.8 | 1.8 | 1.7 | [7 empty] | 2.0059
2 | Small temperature difference of evaporator | ºC |  | 1.1 | 1.2 | 1.2 | 1.3 | 0.7 | 0.5 | 0.5 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | [7 empty] | 0.58824
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.1 | 14.1 | 14.6 | 14.7 | 15 | 15 | 14 | 13.7 | 13.9 | 14.1 | 14.3 | 14.4 | 14.1 | 14 | 13.7 | 13.6 | 13.3 | [7 empty] | 14.1529
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.5 | 6.5 | 6.8 | 7 | 7.1 | 8 | 7.8 | 8 | 8 | 8 | 7.2 | 7.2 | 7 | 7 | 7 | 6.6 | 6.4 | [7 empty] | 7.1824
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.4 | 22.8 | 22.4 | 22.4 | 22.5 | 25 | 25.5 | 25 | 26.8 | 27.1 | 27.4 | 27.2 | 27.4 | 27.5 | 27.3 | 27.4 | 27.7 | [7 empty] | 25.5765
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.2 | 28.6 | 28.3 | 28.3 | 28.5 | 30.2 | 30 | 29.5 | 31.3 | 31.7 | 32.8 | 32.6 | 32.7 | 32.7 | 32.4 | 32.7 | 32.9 | [7 empty] | 30.8471
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2440.3439 | 2504.5635 | 2472.4537 | 2536.6733 | 2247.6852 | 1990.8069 | 1830.2579 | 1894.4775 | 1958.6971 | 2279.795 | 2311.9048 | 2279.795 | 2247.6852 | 2151.3558 | 2247.6852 | 2215.5754 | [7 empty] | 38050.0992
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1400 | 1300 | 1600 | 1500 | 1800 | 1600 | [7 empty] | 25700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.61467 | 0.61467 | 0.59891 | 0.60668 | 0.59133 | 0.66735 | 0.75346 | 0.81956 | 0.79178 | 0.76582 | 0.65795 | 0.60556 | 0.57023 | 0.71184 | 0.69723 | 0.80082 | 0.72216 | [7 empty] | 0.68177
17 | Average iKW/TR |  |  | Hours 7: 0.68177 | 0.68177
18 | COP of chiller |  |  | 5.7202 | 5.7202 | 5.8707 | 5.7954 | 5.946 | 5.2686 | 4.6665 | 4.2901 | 4.4407 | 4.5912 | 5.3438 | 5.8062 | 6.166 | 4.9393 | 5.0428 | 4.3905 | 4.8687 | [7 empty] | 5.2275
19 | EER of Chiller |  |  | 19.5229 | 19.5229 | 20.0367 | 19.7798 | 20.2936 | 17.9816 | 15.9266 | 14.6422 | 15.156 | 15.6697 | 18.2385 | 19.8165 | 21.0445 | 16.8578 | 17.211 | 14.9847 | 16.617 | [7 empty] | 17.8413
20 | LMTD of Condenser | ºC |  | 4.8335 | 4.8335 | 4.8682 | 4.9808 | 4.4447 | 3.8288 | 3.5921 | 3.5921 | 3.5921 | 3.6263 | 4.1274 | 4.0118 | 3.9783 | 3.8288 | 3.7954 | 3.8621 | 3.7119 | [7 empty] | 4.0887
21 | LMTD of Evaporator | ºC |  | 3.675 | 3.8144 | 3.8712 | 3.9796 | 3.1494 | 2.5849 | 2.389 | 2.0921 | 1.9481 | 1.9933 | 2.4222 | 2.4453 | 2.215 | 2.1931 | 2.1271 | 2.3991 | 2.3759 | [7 empty] | 2.6867
Performance Sheet Chiller
Date :- 05/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [5 empty] | 2.4 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 2.3 | 2.1 | 2.3 | 2.4 | 2.4 | 2.1 | 2.3 | 2.4 | 2.6 | 2.6 | 2.5 | 2.6 | 2.7 | 2.6 | 2.35
2 | Small temperature difference of evaporator | ºC | [5 empty] | 0.3 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.34
3 | Entering Chilled Water Temp. (tchwe) | ºC | [5 empty] | 14.4 | 15.1 | 14.1 | 13.9 | 14 | 14.3 | 14.4 | 14.5 | 14.3 | 14.2 | 14 | 13.8 | 13.4 | 12.8 | 13.2 | 14.1 | 14.5 | 14.8 | 15 | 15.1 | 14.195
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [5 empty] | 10 | 8.1 | 8 | 8 | 8.1 | 8 | 8.1 | 7.5 | 7.3 | 7.2 | 7.1 | 6.7 | 6.5 | 6.1 | 5.8 | 6.3 | 6.6 | 6.7 | 6.7 | 6.7 | 7.275
5 | Entering Condenser Water Temp. (tcwe) | ºC | [5 empty] | 21.1 | 25.2 | 25.6 | 25.3 | 27.1 | 27.3 | 27.5 | 27.3 | 27.6 | 27.7 | 27.5 | 27.6 | 27.9 | 27.8 | 25.2 | 24.7 | 24.4 | 24.1 | 24.2 | 24 | 25.955
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [5 empty] | 26.8 | 29.6 | 29.5 | 29.1 | 30.7 | 31.3 | 31.6 | 31.9 | 32.1 | 32.1 | 32 | 32.2 | 32.3 | 32.2 | 29.8 | 29.5 | 29.3 | 29.2 | 29.4 | 29.1 | 30.485
7 | Chilled water inlet pressure | (Kg/Cm2) | [5 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4320
8 | Chilled water outlet pressure | (Kg/Cm2) | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [5 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [5 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [5 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [5 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [5 empty] | 1412.8307 | 2247.6852 | 1958.6971 | 1894.4775 | 1894.4775 | 2022.9167 | 2022.9167 | 2247.6852 | 2247.6852 | 2247.6852 | 2215.5754 | 2279.795 | 2215.5754 | 2151.3558 | 2376.1243 | 2504.5635 | 2536.6733 | 2600.8929 | 2665.1124 | 2697.2222 | 44439.9471
15 | Power Consumption of Chiller | KWH | [5 empty] | 1400 | 1500 | 1500 | 1500 | 1600 | 1600 | 1400 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 30000
16 | Specific power consumption of Chiller | (iKW/TR) | [5 empty] | 0.99092 | 0.66735 | 0.76582 | 0.79178 | 0.84456 | 0.79094 | 0.69207 | 0.66735 | 0.66735 | 0.66735 | 0.67703 | 0.65795 | 0.67703 | 0.69723 | 0.63128 | 0.59891 | 0.59133 | 0.57673 | 0.56283 | 0.55613 | 0.6886
17 | Average iKW/TR |  |  | Hours 7: 0.6886 | 0.6886
18 | COP of chiller | [6 empty] | 3.5482 | 5.2686 | 4.5912 | 4.4407 | 4.1631 | 4.4454 | 5.0804 | 5.2686 | 5.2686 | 5.2686 | 5.1933 | 5.3438 | 5.1933 | 5.0428 | 5.5696 | 5.8707 | 5.946 | 6.0965 | 6.247 | 6.3223 | 5.2084
19 | EER of Chiller | [6 empty] | 12.1101 | 17.9816 | 15.6697 | 15.156 | 14.2087 | 15.172 | 17.3394 | 17.9816 | 17.9816 | 17.9816 | 17.7248 | 18.2385 | 17.7248 | 17.211 | 19.0092 | 20.0367 | 20.2936 | 20.8073 | 21.3211 | 21.578 | 17.7764
20 | LMTD of Condenser | ºC | [5 empty] | 4.686 | 3.8943 | 3.7149 | 3.6786 | 3.6053 | 3.9697 | 4.0063 | 3.9649 | 4.1512 | 4.2249 | 4.2612 | 3.9649 | 4.1152 | 4.2249 | 4.5161 | 4.589 | 4.5153 | 4.6974 | 4.8435 | 4.6974 | 4.216
21 | LMTD of Evaporator | ºC | [5 empty] | 1.5991 | 1.9534 | 1.7681 | 1.9481 | 2.1401 | 2.2353 | 2.0381 | 2.1931 | 2.1931 | 2.1931 | 2.3759 | 2.215 | 2.3759 | 2.3293 | 2.4912 | 2.5824 | 2.6051 | 2.4308 | 2.6951 | 2.7175 | 2.254

## 06-02-2019 (hidden)
Performance Sheet Chiller
Date :- 06/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.7 | 2.6 | 2.4 | 2.1 | 1.9 | 1.7 | 1.9 | 1.8 | 1.8 | 1.9 | 1.9 | 2.1 | 1.9 | 1.9 | 2 | [9 empty] | 2.04
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | [9 empty] | 0.34
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.0845 | 15.3932 | 15.5446 | 14.4497 | 13.9903 | 13.9903 | 14.1398 | 14.2934 | 14.4422 | 14.4422 | 14.4422 | 14.29 | 13.6903 | 13.3921 | 13.0912 | [9 empty] | 14.3117
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 9.8 | 9.8 | 9.7697 | 9.3069 | 9.3069 | 9.3069 | 9.3069 | 9.4558 | 9.4558 | 9.4558 | 9.4558 | 8.8296 | 8.6767 | 8.5248 | 7.7152 | [9 empty] | 9.2111
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.3666 | 23.3641 | 24.4118 | 25.3502 | 25.3468 | 25.9653 | 26.2753 | 26.4268 | 26.1085 | 25.0244 | 24.2474 | 24.2437 | 23.9296 | 23.6217 | 23.7714 | [9 empty] | 24.7636
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.7897 | 28.6301 | 29.317 | 29.8025 | 29.1853 | 29.8057 | 30.419 | 30.5743 | 30.4158 | 29.1735 | 28.569 | 29.0259 | 28.2603 | 27.8042 | 28.2803 | [9 empty] | 29.2035
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [9 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [9 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [9 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [9 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [9 empty] | 971
14 | TR Genrated by Chiller | TR |  | 1696.8386 | 1795.9647 | 1854.2796 | 1651.346 | 1503.8401 | 1503.8401 | 1551.8442 | 1553.337 | 1601.1324 | 1601.1324 | 1601.1324 | 1753.3116 | 1609.8519 | 1562.8858 | 1726.2033 | [9 empty] | 24566.9403
15 | Power Consumption of Chiller | KWH |  | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | [9 empty] | 19095
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.75022 | 0.70881 | 0.68652 | 0.77089 | 0.8465 | 0.8465 | 0.82031 | 0.81953 | 0.79506 | 0.79506 | 0.79506 | 0.72605 | 0.79076 | 0.81452 | 0.73746 | [9 empty] | 0.78022
17 | Average iKW/TR |  |  | Hours 7: 0.78022 | 0.78022
18 | COP of chiller |  |  | 4.6866 | 4.9604 | 5.1215 | 4.561 | 4.1536 | 4.1536 | 4.2862 | 4.2903 | 4.4223 | 4.4223 | 4.4223 | 4.8426 | 4.4464 | 4.3167 | 4.7677 | [9 empty] | 4.5236
19 | EER of Chiller |  |  | 15.9955 | 16.9299 | 17.4796 | 15.5666 | 14.1762 | 14.1762 | 14.6287 | 14.6427 | 15.0933 | 15.0933 | 15.0933 | 16.5278 | 15.1755 | 14.7328 | 16.2723 | [9 empty] | 15.4389
20 | LMTD of Condenser | ºC |  | 4.9236 | 4.7568 | 4.4067 | 3.9128 | 3.4727 | 3.2506 | 3.5809 | 3.4702 | 3.5257 | 3.5828 | 3.6433 | 4.0288 | 3.6465 | 3.5946 | 3.821 | [9 empty] | 3.8411
21 | LMTD of Evaporator | ºC |  | 1.9911 | 2.0663 | 2.1101 | 1.7744 | 1.6666 | 1.6666 | 1.8796 | 1.703 | 1.738 | 1.738 | 1.9177 | 2.034 | 1.7443 | 1.71 | 1.8284 | [9 empty] | 1.8379
Performance Sheet Chiller
Date :- 06/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 2.3 | 1.9 | 2.1 | 1.7 | 2 | 2.1 | 2.1 | 1.7 | 1.7 | 1.8 | 1.8 | 1.7 | 1.8 | 1.7 | 1.9 | 2 | 2.1 | 2.1 | 2 | 2 | 2.1 | 2.1 | 1.9409
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.32273
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 15.5446 | 14.4497 | 13.9903 | 13.9903 | 14.1398 | 14.2934 | 14.4422 | 14.4422 | 14.4422 | 14.29 | 13.6903 | 13.3921 | 13.0912 | 12.4809 | 13.101 | 13.5529 | 13.8571 | 14.0096 | 14.0096 | 14.0096 | 14.0096 | 14.0096 | 13.9654
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 9.7697 | 9.3069 | 9.3069 | 9.3069 | 9.3069 | 9.4558 | 9.4558 | 9.4558 | 9.4558 | 8.8296 | 8.6767 | 8.5248 | 7.7152 | 8.9153 | 9.2206 | 9.5321 | 9.6843 | 9.8339 | 9.8339 | 9.8339 | 9.8339 | 9.8339 | 9.3222
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 24.4118 | 25.3502 | 25.3468 | 25.9653 | 26.2753 | 26.4268 | 26.1085 | 25.0244 | 24.2474 | 24.2437 | 23.9296 | 23.6217 | 23.7714 | 22.6867 | 21.2457 | 21.8578 | 22.0094 | 22.3171 | 22.3171 | 22.3171 | 22.3171 | 22.4754 | 23.8303
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 29.317 | 29.8025 | 29.1853 | 29.8057 | 30.419 | 30.5743 | 30.4158 | 29.1735 | 28.569 | 29.0259 | 28.2603 | 27.8042 | 28.2803 | 27.927 | 25.81 | 26.7365 | 27.1917 | 27.6682 | 27.5162 | 27.5162 | 27.6663 | 27.8257 | 28.4769
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 1854.2796 | 1651.346 | 1503.8401 | 1503.8401 | 1551.8442 | 1553.337 | 1601.1324 | 1601.1324 | 1601.1324 | 1753.3116 | 1609.8519 | 1562.8858 | 1726.2033 | 1144.8915 | 1245.9879 | 1291.0739 | 1339.8933 | 1340.786 | 1340.786 | 1340.786 | 1340.786 | 1340.786 | 32799.9134
15 | Power Consumption of Chiller | KWH |  |  |  | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 30600.02
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.75011 | 0.84229 | 0.92491 | 0.92491 | 0.89629 | 0.89543 | 0.8687 | 0.8687 | 0.8687 | 0.7933 | 0.864 | 0.88996 | 0.80576 | 1.2149 | 1.1163 | 1.0773 | 1.0381 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 0.94666
17 | Average iKW/TR |  |  | Hours 7: 0.94666 | 0.94666
18 | COP of chiller |  |  |  |  | 4.6873 | 4.1743 | 3.8015 | 3.8015 | 3.9228 | 3.9266 | 4.0474 | 4.0474 | 4.0474 | 4.4321 | 4.0695 | 3.9507 | 4.3636 | 2.8941 | 3.1497 | 3.2636 | 3.387 | 3.3893 | 3.3893 | 3.3893 | 3.3893 | 3.3893 | 3.7688
19 | EER of Chiller |  |  |  |  | 15.9978 | 14.247 | 12.9744 | 12.9744 | 13.3886 | 13.4015 | 13.8138 | 13.8138 | 13.8138 | 15.1267 | 13.889 | 13.4838 | 14.8929 | 9.8776 | 10.7498 | 11.1388 | 11.56 | 11.5677 | 11.5677 | 11.5677 | 11.5677 | 11.5677 | 12.8628
20 | LMTD of Condenser | ºC |  |  |  | 4.2957 | 3.6888 | 3.6926 | 3.2506 | 3.6922 | 3.8042 | 3.8613 | 3.3578 | 3.417 | 3.6883 | 3.5337 | 3.3693 | 3.5951 | 3.7252 | 3.7277 | 3.9495 | 4.1675 | 4.2253 | 4.0592 | 4.0592 | 4.2247 | 4.2251 | 3.8005
21 | LMTD of Evaporator | ºC |  |  |  | 1.9197 | 1.7744 | 1.6666 | 1.6666 | 1.2397 | 1.703 | 1.738 | 1.738 | 1.738 | 2.034 | 1.7443 | 1.71 | 1.6154 | 1.3949 | 1.473 | 1.6735 | 1.7127 | 1.7134 | 1.7134 | 1.7134 | 1.7134 | 1.7134 | 1.6868

## 07-02-2019 (hidden)
Performance Sheet Chiller
Date :- 07/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2 | 1.9 | 2 | 2.1 | 2.1 | 2 | 2 | 1.9 | 1.8 | 1.8 | 1.9 | 1.9 | 1.9 | 1.9 | 1.8 | 1.8 | 1.8 | 1.9 | 1.9 | 1.8 | 1.9 | 1.9 | 1.8 | 1.7 | 1.8958
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.42083
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.0096 | 14.0096 | 14.4628 | 14.6113 | 14.7594 | 14.4486 | 14.1418 | 13.8336 | 13.6815 | 13.9903 | 14.6091 | 15.2223 | 15.6821 | 15.6821 | 15.8307 | 15.8307 | 15.6725 | 15.367 | 15.0684 | 14.7655 | 14.461 | 14.1534 | 13.8532 | 13.7025 | 14.6604
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 9.8339 | 9.8339 | 10.1385 | 10.2873 | 10.4362 | 10.2847 | 9.9761 | 9.8238 | 9.6747 | 9.8301 | 10.2955 | 10.7454 | 11.0441 | 11.202 | 11.3548 | 11.3548 | 11.1985 | 10.8923 | 10.5867 | 10.2827 | 10.1338 | 9.8331 | 9.6817 | 9.6817 | 10.3503
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.1739 | 22.0247 | 21.8671 | 21.717 | 21.2523 | 21.4098 | 21.4098 | 21.4098 | 21.5584 | 21.4015 | 21.4015 | 21.5516 | 21.2414 | 21.084 | 21.2332 | 21.22 | 20.6094 | 20.4729 | 19.857 | 19.2453 | 19.3954 | 18.618 | 19.2416 | 19.3903 | 20.8661
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.5169 | 27.2163 | 27.2163 | 27.3654 | 26.9031 | 26.901 | 26.901 | 26.5887 | 26.733 | 26.4206 | 26.8772 | 27.0284 | 27.0102 | 26.855 | 27.0075 | 27.1566 | 26.5444 | 26.3836 | 25.766 | 25.0099 | 24.8713 | 24.0804 | 24.3892 | 24.3892 | 26.3805
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2704.795 | 2747.326 | 2766.03 | 2887.04 | 2820.556 | 2737.653 | 2729.095 | 2614.262 | 2639.521 | 2768.235 | 2842.169 | 3028.007 | 3096.169 | 2988.283 | 2957.869 | 2947.825 | 2971.645 | 2943.651 | 2981.607 | 2949.21 | 2801.469 | 2811.995 | 2707.899 | 2631.616 | 68073.927
15 | Power Consumption of Chiller | KWH |  | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.159 | 35500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.54687 | 0.5384 | 0.53476 | 0.51235 | 0.52442 | 0.5403 | 0.542 | 0.56581 | 0.56039 | 0.53434 | 0.52044 | 0.4885 | 0.47774 | 0.49499 | 0.50008 | 0.50178 | 0.49776 | 0.50249 | 0.4961 | 0.50155 | 0.528 | 0.52602 | 0.54624 | 0.56207 | 0.52264
17 | Average iKW/TR |  |  | Hours 7: 0.52264 | 0.52264
18 | COP of chiller |  |  | 6.4293 | 6.5304 | 6.5749 | 6.8625 | 6.7045 | 6.5074 | 6.4871 | 6.2141 | 6.2742 | 6.5801 | 6.7559 | 7.1976 | 7.3596 | 7.1032 | 7.0309 | 7.007 | 7.0636 | 6.9971 | 7.0873 | 7.0103 | 6.6591 | 6.6842 | 6.4367 | 6.2554 | 6.7422
19 | EER of Chiller |  |  | 21.9433 | 22.2884 | 22.4401 | 23.4218 | 22.8825 | 22.2099 | 22.1405 | 21.2088 | 21.4138 | 22.458 | 23.0578 | 24.5655 | 25.1184 | 24.2432 | 23.9964 | 23.915 | 24.1082 | 23.8811 | 24.189 | 23.9262 | 22.7276 | 22.813 | 21.9685 | 21.3498 | 23.0111
20 | LMTD of Condenser | ºC |  | 4.1081 | 3.9418 | 4.1102 | 4.3265 | 4.3273 | 4.1582 | 4.1582 | 3.9375 | 3.8203 | 3.7683 | 4.0371 | 4.0375 | 4.1344 | 4.1352 | 4.0184 | 4.0712 | 4.0707 | 4.1812 | 4.1806 | 4.0152 | 4.0372 | 4.0327 | 3.8113 | 3.6453 | 4.0444
21 | LMTD of Evaporator | ºC |  | 1.7134 | 1.7134 | 1.7514 | 1.9076 | 1.9074 | 1.7104 | 1.7108 | 1.6707 | 1.6699 | 1.8637 | 1.9048 | 1.9482 | 1.8308 | 1.791 | 1.7899 | 1.9479 | 1.7895 | 1.7896 | 1.7914 | 1.9498 | 1.7522 | 1.7504 | 1.544 | 1.5074 | 1.7794

## 08-02-2019 (hidden)
Performance Sheet Chiller
Date :- 08/02/2019
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [6 empty] | 1.1 | [18 empty] | 1.1
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.2 | [18 empty] | 0.2
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 13.6 | [18 empty] | 13.6
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 5.5 | [18 empty] | 5.5
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 19.3 | [18 empty] | 19.3
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 24.6 | [18 empty] | 24.6
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | [18 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | [18 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | [18 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | [18 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | [18 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | [18 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | [18 empty] | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 1300 | [18 empty] | 1300
15 | Power Consumption of Chiller | KWH | [6 empty] | 700 | [18 empty] | 700
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.53846 | [18 empty] | 0.53846
17 | Average iKW/TR |  |  | 0.53846 | [23 empty] | 0.53846
18 | COP of chiller | [7 empty] | 6.5297 | [18 empty] | 6.5297
19 | EER of Chiller | [7 empty] | 22.2859 | [18 empty] | 22.2859
20 | LMTD of Condenser | ºC | [6 empty] | 3.0097 | [18 empty] | 3.0097
21 | LMTD of Evaporator | ºC | [6 empty] | 2.1741 | [18 empty] | 2.1741
Performance Sheet Chiller
Date :- 08/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.7 | 1.7 | 1.8 | 2 | 1.1 | 1.7 | 1.7 | 1 | 1.8 | 1.8 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9 | 1.8 | 1.9 | 1.9 | 1.8 | 1.8 | 1.8 | 1.8 | 1.7 | 1.7458
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.3 | 0.4 | 0.3 | 0.4 | 0.2 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.3 | 0.3 | 0.4
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.5 | 13.4 | 13.6 | 13.5 | 13.5 | 13.6 | 13.8 | 13.3 | 13.9 | 14.2 | 14.5 | 14.3 | 14.3 | 14.4 | 14.2 | 13.8 | 13.6 | 13.5 | 13 | 12.6 | 12.5 | 12.3 | 12.1 | 11.8 | 13.4667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.4 | 5.3 | 5.5 | 5.5 | 5.6 | 5.5 | 6.9 | 5.6 | 5.6 | 5.5 | 5.5 | 5.5 | 5.6 | 5.4 | 5.6 | 5.4 | 5.4 | 5.5 | 5.5 | 5.5 | 5.6 | 5.5 | 5.5 | 5.4 | 5.5542
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 19.7 | 20.2 | 19 | 19 | 18.6 | 19.3 | 20 | 19.6 | 20 | 19.6 | 19.2 | 18.5 | 18.5 | 18.5 | 18.4 | 18.4 | 17 | 16.1 | 16.4 | 15.1 | 14.8 | 14.7 | 15 | 14.7 | 17.9292
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 25.1 | 25.6 | 24.3 | 24 | 23.9 | 24.6 | 24.7 | 24.6 | 25.6 | 25.3 | 24.8 | 24.3 | 24.3 | 24.4 | 23.9 | 24 | 22.3 | 21.2 | 21.2 | 19.8 | 19.1 | 19.1 | 19.4 | 18.9 | 23.1
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2615.985 | 2681.725 | 2717.21 | 2567.604 | 2674.935 | 4643.944 | 2389.636 | 2787.846 | 2843.38 | 2809.673 | 2892.838 | 2930.524 | 2926.163 | 2923.301 | 2820.71 | 2678.736 | 2671.518 | 2513.723 | 2284.683 | 2320.102 | 2206.934 | 2164.419 | 2220.954 | 2085.003 | 64371.546
15 | Power Consumption of Chiller | KWH |  | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.91 | 29300 | `
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.46668 | 0.45524 | 0.4493 | 0.47547 | 0.4564 | 0.26289 | 0.51089 | 0.43791 | 0.42936 | 0.43451 | 0.42202 | 0.41659 | 0.41721 | 0.41762 | 0.43281 | 0.45575 | 0.45698 | 0.48567 | 0.53435 | 0.5262 | 0.55318 | 0.56405 | 0.54969 | 0.58557 | 0.46651
17 | Average iKW/TR |  |  | 0.46651 | [23 empty] | 0.46651
18 | COP of chiller |  |  | 7.5341 | 7.7234 | 7.8256 | 7.3947 | 7.7038 | 13.3746 | 6.8822 | 8.029 | 8.189 | 8.0919 | 8.3314 | 8.4399 | 8.4274 | 8.4191 | 8.1237 | 7.7148 | 7.694 | 7.2395 | 6.5799 | 6.6819 | 6.356 | 6.2335 | 6.3964 | 6.0044 | 7.7246
19 | EER of Chiller |  |  | 25.7137 | 26.3599 | 26.7087 | 25.2382 | 26.2932 | 45.6475 | 23.4888 | 27.403 | 27.9489 | 27.6176 | 28.4351 | 28.8055 | 28.7626 | 28.7345 | 27.7261 | 26.3305 | 26.2596 | 24.7086 | 22.4572 | 22.8054 | 21.693 | 21.2751 | 21.8308 | 20.4931 | 26.364
20 | LMTD of Condenser | ºC |  | 3.8953 | 3.7776 | 3.7448 | 3.7618 | 4.0935 | 3.0097 | 3.5454 | 3.6457 | 2.9676 | 3.9941 | 3.9613 | 4.1447 | 4.1447 | 4.0594 | 3.9283 | 4.0785 | 3.8621 | 3.9109 | 3.8088 | 3.6604 | 3.5231 | 3.5577 | 3.5577 | 3.3753 | 3.7503
21 | LMTD of Evaporator | ºC |  | 2.6502 | 2.4308 | 2.6502 | 2.4095 | 2.6051 | 2.1741 | 2.1711 | 2.5597 | 2.6951 | 2.7844 | 3.2461 | 3.1982 | 2.9873 | 3.0566 | 2.7622 | 2.9175 | 2.8707 | 2.6277 | 2.5141 | 2.4222 | 2.1711 | 2.3526 | 2.1049 | 2.0605 | 2.6009

## 09-02-2019 (hidden)
Performance Sheet Chiller
Date :- 09/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.7 | 1.7 | 1.6 | 1.4 | 1.5 | 1.6 | 1.6 | 1.4 | 1.4 | 1.5 | 1.7 | 1.8 | 1.8 | 1.9 | 1.8 | 1.8 | 1.8 | 1.9 | 1.9 | 1.8 | 1.7 | 1.8 | 1.8 | 1.8 | 1.6958
2 | Small temperature difference of evaporator | ºC |  | 0.2 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.29167
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 11.9 | 11.7 | 11.8 | 11.8 | 12.1 | 12.2 | 11.7 | 11.5 | 11.3 | 11.3 | 11.5 | 12.3 | 13.3 | 13.8 | 13.8 | 14 | 13.5 | 13.5 | 13.3 | 13 | 12.8 | 12.8 | 12.5 | 12.4 | 12.4917
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.4 | 5.5 | 5.4 | 5.5 | 5.4 | 5.6 | 5.4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.6 | 5.5 | 5.5 | 5.5 | 5.4 | 5.5 | 5.5 | 5.4 | 5.5 | 5.6 | 5.5 | 5.4958
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 14.7 | 14.5 | 16 | 17.3 | 18 | 18.6 | 19.2 | 19.3 | 18.4 | 17.2 | 17.6 | 18.7 | 20 | 19.2 | 19.6 | 21.4 | 22.4 | 20.6 | 19 | 18.7 | 18.3 | 17.3 | 15.9 | 15.2 | 18.2125
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 18.8 | 18.3 | 20.2 | 21.6 | 22.3 | 22.9 | 23.1 | 23.3 | 22.2 | 21.2 | 21.4 | 23.2 | 24.8 | 24.6 | 25 | 27.1 | 27.8 | 25.7 | 24.2 | 23.6 | 23 | 22 | 20.3 | 19.7 | 22.7625
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2107.483 | 2075.459 | 2082.909 | 2171.181 | 2206.338 | 2062.525 | 2059.86 | 1948.581 | 1965.538 | 2002.774 | 2330.778 | 2548.849 | 2756.417 | 2730.439 | 2728.636 | 2660.282 | 2541.769 | 2585.251 | 2468.669 | 2344.403 | 2381.509 | 2408.323 | 2302.843 | 2319.441 | 55790.257
15 | Power Consumption of Chiller | KWH |  | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 27300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53974 | 0.54807 | 0.54611 | 0.52391 | 0.51556 | 0.55151 | 0.55222 | 0.58376 | 0.57872 | 0.56796 | 0.48803 | 0.44628 | 0.41267 | 0.4166 | 0.41687 | 0.42759 | 0.44752 | 0.44 | 0.46077 | 0.4852 | 0.47764 | 0.47232 | 0.49395 | 0.49042 | 0.49514
17 | Average iKW/TR |  |  | Hours 7: 0.49514 | 0.49514
18 | COP of chiller |  |  | 6.5142 | 6.4152 | 6.4382 | 6.7111 | 6.8198 | 6.3752 | 6.367 | 6.023 | 6.0755 | 6.1906 | 7.2044 | 7.8785 | 8.5201 | 8.4398 | 8.4342 | 8.2229 | 7.8566 | 7.991 | 7.6306 | 7.2465 | 7.3612 | 7.4441 | 7.1181 | 7.1694 | 7.1853
19 | EER of Chiller |  |  | 22.233 | 21.8951 | 21.9737 | 22.905 | 23.2759 | 21.7587 | 21.7306 | 20.5566 | 20.7355 | 21.1284 | 24.5886 | 26.8892 | 29.0789 | 28.8049 | 28.7859 | 28.0648 | 26.8145 | 27.2732 | 26.0433 | 24.7324 | 25.1238 | 25.4067 | 24.2939 | 24.469 | 24.5234
20 | LMTD of Condenser | ºC |  | 3.3409 | 3.2365 | 3.2612 | 3.0627 | 3.1795 | 3.2951 | 3.1585 | 2.9631 | 2.8959 | 3.0786 | 3.2365 | 3.5921 | 3.6943 | 4.0118 | 3.8953 | 3.9941 | 3.8953 | 3.9109 | 3.9447 | 3.7282 | 3.5454 | 3.6604 | 3.5577 | 3.5921 | 3.4888
21 | LMTD of Evaporator | ºC |  | 1.851 | 2.0158 | 1.8304 | 1.8097 | 1.8921 | 2.1049 | 1.8097 | 1.7472 | 1.7053 | 1.9255 | 1.9708 | 2.1271 | 2.3451 | 2.6727 | 2.4734 | 2.5157 | 2.4095 | 2.6502 | 2.5824 | 2.302 | 2.2803 | 2.4683 | 2.3759 | 2.1711 | 2.1682
6.9

## 10-02-2019 (hidden)
Performance Sheet Chiller
Date :- 10/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.1 | 2.1 | 1.9 | 1.9 | 1.9 | 2 | 2.2 | 2.1 | 2.1 | 2.2 | 2.4 | 2.4 | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1625
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.3 | 0.3 | 0.4 | 0.3 | 0.4 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.5 | 0.5 | 0.6 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 12.3 | 12.3 | 12.5 | 12.3 | 12.5 | 12.7 | 13.1 | 13.7 | 13.8 | 14.2 | 14.5 | 14.5 | 14.8 | 14.9 | 14.9 | 14.8 | 14.7 | 14.2 | 14 | 13.7 | 13.6 | 13.4 | 13.2 | 13.1 | 13.6542
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.5 | 5.6 | 5.5 | 5.6 | 5.6 | 5.5 | 5.5 | 5.5 | 5.6 | 5.5 | 5.6 | 5.8 | 6 | 5.8 | 5.7 | 5.6 | 5.5 | 5.5 | 5.4 | 5.5 | 5.4 | 5.5 | 5.6 | 5.575
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 15.8 | 15.8 | 16.6 | 17.2 | 18.3 | 18.6 | 19.3 | 19.4 | 19.2 | 20 | 20.3 | 19.9 | 20.6 | 20.9 | 20.2 | 20 | 19.3 | 18.9 | 19 | 19 | 18.7 | 18.5 | 19.1 | 18.5 | 18.8792
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 20.2 | 20.1 | 21 | 21.7 | 22.6 | 23.5 | 24.3 | 24.7 | 25 | 25.6 | 26.1 | 25.8 | 26.7 | 26.8 | 26.2 | 26.2 | 25.4 | 24.8 | 24.6 | 24.6 | 24.1 | 23.6 | 24 | 23.2 | 24.2
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2222.955 | 2168.9 | 2156.846 | 2244.776 | 2407.8 | 2546.323 | 2544.859 | 2681.12 | 2781.535 | 2906.901 | 2857.5 | 2906.838 | 2917.198 | 2924.279 | 2875.941 | 2871.351 | 2736.406 | 2828.295 | 2709.823 | 2651.108 | 2616.402 | 2410.532 | 2525.452 | 2516.42 | 63009.56
15 | Power Consumption of Chiller | KWH |  | 1190 | 1190 | 1180 | 1250 | 1250 | 1300 | 1370 | 1370 | 1400 | 1500 | 1380 | 1380 | 1400 | 1370 | 1370 | 1500 | 1300 | 1350 | 1350 | 1350 | 1250 | 1300 | 1300 | 1300 | 31900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53532 | 0.54867 | 0.5471 | 0.55685 | 0.51915 | 0.51054 | 0.53834 | 0.51098 | 0.50332 | 0.51601 | 0.48294 | 0.47474 | 0.47991 | 0.46849 | 0.47637 | 0.5224 | 0.47508 | 0.47732 | 0.49819 | 0.50922 | 0.47776 | 0.5393 | 0.51476 | 0.51661 | 0.50831
17 | Average iKW/TR |  |  | Hours 7: 0.50831 | 0.50831
18 | COP of chiller |  |  | 6.568 | 6.4083 | 6.4267 | 6.3141 | 6.7727 | 6.8868 | 6.5312 | 6.8809 | 6.9856 | 6.8138 | 7.2804 | 7.4061 | 7.3263 | 7.5049 | 7.3809 | 6.7304 | 7.4009 | 7.3661 | 7.0576 | 6.9047 | 7.3594 | 6.5196 | 6.8304 | 6.8059 | 6.9359
19 | EER of Chiller |  |  | 22.4166 | 21.8715 | 21.9342 | 21.55 | 23.1151 | 23.5047 | 22.2909 | 23.4845 | 23.8419 | 23.2554 | 24.848 | 25.2771 | 25.0048 | 25.6144 | 25.191 | 22.971 | 25.2594 | 25.1406 | 24.0875 | 23.5656 | 25.1177 | 22.2513 | 23.3121 | 23.2287 | 23.6722
20 | LMTD of Condenser | ºC |  | 3.8943 | 3.8587 | 3.6707 | 3.7054 | 3.6358 | 3.9568 | 4.2172 | 4.2079 | 4.3776 | 4.4245 | 4.7206 | 4.755 | 4.8237 | 4.5266 | 4.5604 | 4.6276 | 4.5941 | 4.5266 | 4.4245 | 4.4245 | 4.3559 | 4.2521 | 4.1822 | 4.1118 | 4.2848
21 | LMTD of Evaporator | ºC |  | 2.3526 | 2.1491 | 2.1711 | 2.3526 | 2.1711 | 2.4222 | 2.3236 | 2.6727 | 2.6951 | 2.9641 | 3.0566 | 3.2222 | 3.2461 | 3.0335 | 3.0796 | 3.2699 | 3.0796 | 2.7844 | 2.7399 | 2.6951 | 2.8472 | 2.8236 | 2.5597 | 2.5141 | 2.7177

## 11-02-2019 (hidden)
Performance Sheet Chiller
Date :- 11/2/2019
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 16: 0.3; Hours 17: 0.4; Hours 18: 0.4; Hours 19: 0.4; Hours 20: 0.4; Hours 21: 0.4; Hours 22: 0.4; Hours 23: 0.3 | 0.375
2 | Small temperature difference of evaporator | ºC |  | Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 16: 15.6667; Hours 17: 15.3889; Hours 18: 14.5; Hours 19: 14.0556; Hours 20: 13.7222; Hours 21: 13.6111; Hours 22: 13.3889; Hours 23: 13.1667 | 14.1875
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 16: 8.5; Hours 17: 8.1667; Hours 18: 7.8333; Hours 19: 7.8333; Hours 20: 7.9444; Hours 21: 7.9444; Hours 22: 8.0556; Hours 23: 7.1667 | 7.9306
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 16: 23.6667; Hours 17: 24.5556; Hours 18: 25.7222; Hours 19: 25.0556; Hours 20: 24.5; Hours 21: 23.9444; Hours 22: 23.5; Hours 23: 24.2778 | 24.4028
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 16: 28.9444; Hours 17: 29.5556; Hours 18: 30.5556; Hours 19: 29.4444; Hours 20: 28.6667; Hours 21: 28; Hours 22: 27.2222; Hours 23: 28.5556 | 28.8681
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 16: 2301.2026; Hours 17: 2319.0405; Hours 18: 2140.6527; Hours 19: 1997.9439; Hours 20: 1855.2316; Hours 21: 1819.5545; Hours 22: 1712.5226; Hours 23: 1926.5879 | 16072.7363
15 | Power Consumption of Chiller | KWH |  | Hours 16: 1225; Hours 17: 1225; Hours 18: 1225; Hours 19: 1225; Hours 20: 1225; Hours 21: 1225; Hours 22: 1225; Hours 23: 1225 | 9800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 16: 0.53233; Hours 17: 0.52824; Hours 18: 0.57226; Hours 19: 0.61313; Hours 20: 0.66029; Hours 21: 0.67324; Hours 22: 0.71532; Hours 23: 0.63584 | 0.61633
17 | Average iKW/TR |  |  | Hours 7: 0.61633 | 0.61633
18 | COP of chiller |  |  | Hours 16: 6.6049; Hours 17: 6.6561; Hours 18: 6.1441; Hours 19: 5.7345; Hours 20: 5.3249; Hours 21: 5.2225; Hours 22: 4.9153; Hours 23: 5.5297 | 5.7665
19 | EER of Chiller |  |  | Hours 16: 22.5426; Hours 17: 22.7173; Hours 18: 20.9698; Hours 19: 19.5719; Hours 20: 18.1739; Hours 21: 17.8244; Hours 22: 16.7759; Hours 23: 18.8729 | 19.6811
20 | LMTD of Condenser | ºC |  | Hours 16: 1.8057; Hours 17: 1.9211; Hours 18: 1.8797; Hours 19: 1.7679; Hours 20: 1.7111; Hours 21: 1.6825; Hours 22: 1.5957; Hours 23: 1.5697 | 1.7417
21 | LMTD of Evaporator | ºC |  | Hours 16: 2.6251; Hours 17: 2.6385; Hours 18: 2.5038; Hours 19: 2.3945; Hours 20: 2.2836; Hours 21: 2.2556; Hours 22: 2.1709; Hours 23: 2.3392 | 2.4014
Performance Sheet Chiller
Date :- 11/2/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 2.3 | 2.1 | 2.4 | 2.2 | 2.5 | 2.6 | 2.4 | 2.2 | 2.1 | 1.8 | 1.5 | 1.5 | 1.7 | 1.9 | 2.1 | 2 | 2.1 | 2.1 | 2.1 | 2 | 2.1 | 2.1 | 2.0818
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.35455
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 13.4 | 13 | 12.3 | 13.3 | 14.1 | 14.5 | 14.9 | 15.6 | 15.6 | 14.7 | 14.2 | 14 | 13.8 | 13.6 | 13.3 | 12.5 | 12.5 | 13.1 | 13.5 | 13.7 | 13.7 | 13.7 | 13.7727
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 6.5 | 5.4 | 5.5 | 5.4 | 5.8 | 6.2 | 6.6 | 7.3 | 8.1 | 7.8 | 8 | 7.8 | 8 | 8.1 | 7 | 5.8 | 5.5 | 5.6 | 5.6 | 5.7 | 5.8 | 5.7 | 6.5091
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 18.1 | 20.2 | 19.1 | 19.7 | 21 | 21.2 | 22.2 | 22.9 | 24.5 | 25.8 | 25.1 | 24.6 | 24 | 23.6 | 24.3 | 24.5 | 21.3 | 21.4 | 21.2 | 21.2 | 21.1 | 21 | 22.1818
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 21.1 | 24.8 | 23.3 | 24.6 | 26.1 | 26.5 | 27.3 | 28 | 29.2 | 30.1 | 29.1 | 28.5 | 27.7 | 27 | 28.4 | 28.6 | 25.6 | 26.1 | 26.1 | 26.1 | 26.1 | 26 | 26.65
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2215.5754 | 2440.3439 | 2183.4656 | 2536.6733 | 2665.1124 | 2665.1124 | 2665.1124 | 2665.1124 | 2408.2341 | 2215.5754 | 1990.8069 | 1990.8069 | 1862.3677 | 1766.0384 | 2022.9167 | 2151.3558 | 2247.6852 | 2408.2341 | 2536.6733 | 2568.7831 | 2536.6733 | 2568.7831 | 51311.4418
15 | Power Consumption of Chiller | KWH |  |  |  | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 31900
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.65446 | 0.59418 | 0.66408 | 0.57161 | 0.54407 | 0.54407 | 0.54407 | 0.54407 | 0.6021 | 0.65446 | 0.72835 | 0.72835 | 0.77858 | 0.82105 | 0.71679 | 0.67399 | 0.64511 | 0.6021 | 0.57161 | 0.56447 | 0.57161 | 0.56447 | 0.63107
17 | Average iKW/TR |  |  | Hours 7: 0.63107 | 0.63107
18 | COP of chiller |  |  |  |  | 5.3724 | 5.9174 | 5.2945 | 6.151 | 6.4624 | 6.4624 | 6.4624 | 6.4624 | 5.8396 | 5.3724 | 4.8274 | 4.8274 | 4.5159 | 4.2823 | 4.9052 | 5.2167 | 5.4502 | 5.8396 | 6.151 | 6.2289 | 6.151 | 6.2289 | 5.6555
19 | EER of Chiller |  |  |  |  | 18.336 | 20.1961 | 18.0702 | 20.9933 | 22.0563 | 22.0563 | 22.0563 | 22.0563 | 19.9304 | 18.336 | 16.4758 | 16.4758 | 15.4128 | 14.6156 | 16.7415 | 17.8045 | 18.6017 | 19.9304 | 20.9933 | 21.2591 | 20.9933 | 21.2591 | 19.3023
20 | LMTD of Condenser | ºC |  |  |  | 3.5937 | 3.9649 | 4.1518 | 4.1822 | 4.5869 | 4.769 | 4.4759 | 4.2521 | 4.0001 | 3.5231 | 3.0786 | 3.0447 | 3.2013 | 3.3143 | 3.7871 | 3.6767 | 3.8587 | 4.0001 | 4.0699 | 3.9568 | 4.1046 | 4.1046 | 3.8953
21 | LMTD of Evaporator | ºC |  |  |  | 2.1711 | 2.3236 | 2.1491 | 2.3881 | 2.6951 | 2.6951 | 2.6951 | 2.4734 | 2.5141 | 2.3759 | 2.2116 | 1.7889 | 1.9255 | 2.0437 | 2.2353 | 2.1271 | 2.3991 | 2.5141 | 2.6051 | 2.6277 | 2.3881 | 2.6277 | 2.3625
Performance Sheet Chiller
Date :- 11/2/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 2.3; Hours 8: 2.2 | 2.25
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.3; Hours 8: 0.3 | 0.3
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 13; Hours 8: 13 | 13
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 5.6; Hours 8: 5.5 | 5.55
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 18.2; Hours 8: 18.1 | 18.15
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 23.1; Hours 8: 22.9 | 23
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 8: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2376.1243; Hours 8: 2408.2341 | 4784.3585
15 | Power Consumption of Chiller | KWH |  | Hours 7: 750; Hours 8: 750 | 1500
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.31564; Hours 8: 0.31143 | 0.31354
17 | Average iKW/TR |  |  | Hours 7: 0.31354 | 0.31354
18 | COP of chiller |  |  | Hours 7: 11.1393; Hours 8: 11.2898 | 11.2145
19 | EER of Chiller |  |  | Hours 7: 38.0183; Hours 8: 38.5321 | 38.2752
20 | LMTD of Condenser | ºC |  | Hours 7: 4.2938; Hours 8: 4.147 | 4.2204
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.2803; Hours 8: 2.302 | 2.2911

## 12-02-2019 (hidden)
Performance Sheet Chiller
Date :- 12/2/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 20: 2; Hours 21: 1.7; Hours 22: 1.7; Hours 23: 1.7; Hours 0: 1.6; Hours 1: 1.9; Hours 2: 2; Hours 3: 2; Hours 4: 2.1; Hours 5: 2; Hours 6: 2.1 | 1.8909
2 | Small temperature difference of evaporator | ºC |  | Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.7; Hours 23: 0.4; Hours 0: 0.8; Hours 1: 1.1; Hours 2: 1.1; Hours 3: 1.2; Hours 4: 1.3; Hours 5: 1.2; Hours 6: 1.4 | 0.98182
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 20: 16.2; Hours 21: 15.4; Hours 22: 14.1; Hours 23: 13.5; Hours 0: 12.7; Hours 1: 11.8; Hours 2: 12.9; Hours 3: 13.3; Hours 4: 13.5; Hours 5: 13.7; Hours 6: 13.8 | 13.7182
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 20: 8.5; Hours 21: 8.1; Hours 22: 7.8; Hours 23: 6.9; Hours 0: 6; Hours 1: 5.6; Hours 2: 5.6; Hours 3: 5.8; Hours 4: 5.8; Hours 5: 6.2; Hours 6: 6.3 | 6.6
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 20: 22; Hours 21: 24.8; Hours 22: 24.3; Hours 23: 24.5; Hours 0: 24.7; Hours 1: 22; Hours 2: 21.5; Hours 3: 21.6; Hours 4: 21.6; Hours 5: 22.1; Hours 6: 22.3 | 22.8545
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 20: 22.5; Hours 21: 30.3; Hours 22: 29.1; Hours 23: 29.4; Hours 0: 29.8; Hours 1: 26.8; Hours 2: 27; Hours 3: 27.4; Hours 4: 27.5; Hours 5: 27.9; Hours 6: 28.1 | 27.8
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3; Hours 0: 4.3; Hours 1: 4.3; Hours 2: 4.3; Hours 3: 4.3; Hours 4: 4.3; Hours 5: 4.3; Hours 6: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8; Hours 5: 3.8; Hours 6: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8; Hours 5: 3.8; Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3; Hours 3: 3; Hours 4: 3; Hours 5: 3; Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5; Hours 3: 0.5; Hours 4: 0.5; Hours 5: 0.5; Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8; Hours 3: 0.8; Hours 4: 0.8; Hours 5: 0.8; Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971; Hours 3: 971; Hours 4: 971; Hours 5: 971; Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 20: 2472.4537; Hours 21: 2344.0146; Hours 22: 2022.9167; Hours 23: 2119.246; Hours 0: 2151.3558; Hours 1: 1990.8069; Hours 2: 2344.0146; Hours 3: 2408.2341; Hours 4: 2472.4537; Hours 5: 2408.2341; Hours 6: 2408.2341 | 25141.9643
15 | Power Consumption of Chiller | KWH |  | Hours 20: 1680; Hours 21: 1600; Hours 22: 1600; Hours 23: 1650; Hours 0: 1630; Hours 1: 1650; Hours 2: 1640; Hours 3: 1640; Hours 4: 1630; Hours 5: 1650; Hours 6: 1630 | 18000
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 20: 0.67949; Hours 21: 0.68259; Hours 22: 0.79094; Hours 23: 0.77858; Hours 0: 0.75766; Hours 1: 0.82881; Hours 2: 0.69965; Hours 3: 0.681; Hours 4: 0.65926; Hours 5: 0.68515; Hours 6: 0.67684 | 0.72
17 | Average iKW/TR |  |  | Hours 7: 0.72 | 0.72
18 | COP of chiller |  |  | Hours 20: 5.1745; Hours 21: 5.151; Hours 22: 4.4454; Hours 23: 4.5159; Hours 0: 4.6406; Hours 1: 4.2422; Hours 2: 5.0253; Hours 3: 5.163; Hours 4: 5.3332; Hours 5: 5.1317; Hours 6: 5.1947 | 4.9107
19 | EER of Chiller |  |  | Hours 20: 17.6605; Hours 21: 17.5803; Hours 22: 15.172; Hours 23: 15.4128; Hours 0: 15.8383; Hours 1: 14.4787; Hours 2: 17.1515; Hours 3: 17.6214; Hours 4: 18.2023; Hours 5: 17.5146; Hours 6: 17.7295 | 16.7602
20 | LMTD of Condenser | ºC |  | Hours 20: 2.2407; Hours 21: 3.8103; Hours 22: 3.579; Hours 23: 3.6124; Hours 0: 3.5612; Hours 1: 3.8088; Hours 2: 4.1611; Hours 3: 4.2616; Hours 4: 4.4112; Hours 5: 4.2616; Hours 6: 4.3776 | 3.826
21 | LMTD of Evaporator | ºC |  | Hours 20: 3.2583; Hours 21: 3.1533; Hours 22: 2.7361; Hours 23: 2.3059; Hours 0: 2.9937; Hours 1: 3.276; Hours 2: 3.5909; Hours 3: 3.786; Hours 4: 3.9796; Hours 5: 3.786; Hours 6: 4.055 | 3.3564
Performance Sheet Chiller
Date :- 12/2/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 2.6; Hours 8: 2.6; Hours 9: 2.6; Hours 10: 2.5; Hours 11: 2.5; Hours 12: 2.5; Hours 13: 1.9; Hours 14: 1; Hours 19: 2.7; Hours 20: 2.3; Hours 21: 1.9; Hours 22: 2.1; Hours 23: 2.3 | 2.2692
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.4; Hours 8: 0.4; Hours 9: 0.3; Hours 10: 0.3; Hours 11: 0.3; Hours 12: 0.4; Hours 13: 0.3; Hours 14: 1.2; Hours 19: 0.4; Hours 20: 0.3; Hours 21: 0.3; Hours 22: 0.3; Hours 23: 0.4 | 0.40769
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 13.7; Hours 8: 13.6; Hours 9: 13.8; Hours 10: 14.2; Hours 11: 14.2; Hours 12: 14.3; Hours 13: 13.8; Hours 14: 13.7; Hours 19: 14.3; Hours 20: 16.2; Hours 21: 15.6; Hours 22: 14.1; Hours 23: 13.6 | 14.2385
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 5.7; Hours 8: 5.7; Hours 9: 5.8; Hours 10: 6.1; Hours 11: 6.2; Hours 12: 6.4; Hours 13: 6; Hours 14: 7.8; Hours 19: 7.9; Hours 20: 7.7; Hours 21: 8.1; Hours 22: 7.8; Hours 23: 7 | 6.7846
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 20.8; Hours 8: 20.3; Hours 9: 20.5; Hours 10: 20.6; Hours 11: 20.6; Hours 12: 21.2; Hours 13: 21.5; Hours 14: 23.6; Hours 19: 21.8; Hours 20: 21.6; Hours 21: 25; Hours 22: 24.6; Hours 23: 24.7 | 22.0615
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 25.9; Hours 8: 25.4; Hours 9: 25.5; Hours 10: 25.6; Hours 11: 25.5; Hours 12: 26.2; Hours 13: 26.5; Hours 14: 27.1; Hours 19: 22.3; Hours 20: 27.1; Hours 21: 29.8; Hours 22: 28.7; Hours 23: 29 | 26.5077
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 8: 4.3; Hours 9: 4.3; Hours 10: 4.3; Hours 11: 4.3; Hours 12: 4.3; Hours 13: 4.3; Hours 14: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2568.7831; Hours 8: 2536.6733; Hours 9: 2568.7831; Hours 10: 2600.8929; Hours 11: 2568.7831; Hours 12: 2536.6733; Hours 13: 2504.5635; Hours 14: 1894.4775; Hours 19: 2055.0265; Hours 20: 2729.332; Hours 21: 2408.2341; Hours 22: 2022.9167; Hours 23: 2119.246 | 31114.3849
15 | Power Consumption of Chiller | KWH |  | Hours 7: 1400; Hours 8: 1360; Hours 9: 1410; Hours 10: 1360; Hours 11: 1400; Hours 12: 1400; Hours 13: 1060; Hours 14: 1030; Hours 19: 1250; Hours 20: 1350; Hours 21: 1200; Hours 22: 1150; Hours 23: 1330 | 16700
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.54501; Hours 8: 0.53614; Hours 9: 0.5489; Hours 10: 0.5229; Hours 11: 0.54501; Hours 12: 0.5519; Hours 13: 0.42323; Hours 14: 0.54369; Hours 19: 0.60826; Hours 20: 0.49463; Hours 21: 0.49829; Hours 22: 0.56849; Hours 23: 0.62758 | 0.53954
17 | Average iKW/TR |  |  | Hours 7: 0.53954 | 0.53954
18 | COP of chiller |  |  | Hours 7: 6.4513; Hours 8: 6.558; Hours 9: 6.4056; Hours 10: 6.7241; Hours 11: 6.4513; Hours 12: 6.3707; Hours 13: 8.3076; Hours 14: 6.467; Hours 19: 5.7804; Hours 20: 7.1084; Hours 21: 7.0561; Hours 22: 6.1848; Hours 23: 5.6025 | 6.5744
19 | EER of Chiller |  |  | Hours 7: 22.0183; Hours 8: 22.3826; Hours 9: 21.8622; Hours 10: 22.9493; Hours 11: 22.0183; Hours 12: 21.7431; Hours 13: 28.3538; Hours 14: 22.0718; Hours 19: 19.7284; Hours 20: 24.2609; Hours 21: 24.0826; Hours 22: 21.1089; Hours 23: 19.1212 | 22.4386
20 | LMTD of Condenser | ºC |  | Hours 7: 4.6974; Hours 8: 4.6974; Hours 9: 4.6614; Hours 10: 4.5512; Hours 11: 4.5153; Hours 12: 4.5512; Hours 13: 3.877; Hours 14: 2.327; Hours 19: 2.9429; Hours 20: 4.5037; Hours 21: 3.8088; Hours 22: 3.7871; Hours 23: 4.0791 | 4.0769
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.6277; Hours 8: 2.6051; Hours 9: 2.4095; Hours 10: 2.4308; Hours 11: 2.4095; Hours 12: 2.6051; Hours 13: 2.3666; Hours 14: 3.3188; Hours 19: 2.2589; Hours 20: 2.5157; Hours 21: 2.302; Hours 22: 2.0381; Hours 23: 2.3059 | 2.4764
Performance Sheet Chiller
Date :- 12/2/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 13: 0.8; Hours 14: 0.7; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8 | 0.78
2 | Small temperature difference of evaporator | ºC |  | Hours 13: 0.9; Hours 14: 0.3; Hours 15: 0.3; Hours 16: 0.3; Hours 17: 0.4 | 0.44
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 13: 23.5; Hours 14: 12.8; Hours 15: 11.8; Hours 16: 12.2; Hours 17: 13 | 14.66
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 13: 16; Hours 14: 5.4; Hours 15: 5.3; Hours 16: 5.8; Hours 17: 5.6 | 7.62
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 13: 25.2; Hours 14: 27.7; Hours 15: 28.6; Hours 16: 23.8; Hours 17: 22.5 | 25.56
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 13: 25.5; Hours 14: 32.8; Hours 15: 32.8; Hours 16: 28.3; Hours 17: 27.4 | 29.36
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 13: 2408.2341; Hours 14: 2376.1243; Hours 15: 2087.1362; Hours 16: 2055.0265; Hours 17: 2376.1243 | 11302.6455
15 | Power Consumption of Chiller | KWH |  | Hours 13: 1420; Hours 14: 1420; Hours 15: 1420; Hours 16: 1420; Hours 17: 1420 | 7100
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 13: 0.58964; Hours 14: 0.59761; Hours 15: 0.68036; Hours 16: 0.69099; Hours 17: 0.59761 | 0.63124
17 | Average iKW/TR |  |  | Hours 7: 0.63124 | 0.63124
18 | COP of chiller |  |  | Hours 13: 5.9629; Hours 14: 5.8834; Hours 15: 5.1679; Hours 16: 5.0884; Hours 17: 5.8834 | 5.5972
19 | EER of Chiller |  |  | Hours 13: 20.3515; Hours 14: 20.0801; Hours 15: 17.6379; Hours 16: 17.3666; Hours 17: 20.0801 | 19.1032
20 | LMTD of Condenser | ºC |  | Hours 13: 0.94205; Hours 14: 2.4119; Hours 15: 2.2918; Hours 16: 2.3799; Hours 17: 2.4954 | 2.1042
21 | LMTD of Evaporator | ºC |  | Hours 13: 3.3578; Hours 14: 2.2803; Hours 15: 2.0827; Hours 16: 2.0605; Hours 17: 2.4912 | 2.4545

## 13-02-2019 (hidden)
Performance Sheet Chiller
Date :- 13/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.1 | 2.2 | 2.3 | 2.1 | 2.2 | 1.8 | 1.7 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.4 | 1.7 | 1.7 | [9 empty] | 1.8133
2 | Small temperature difference of evaporator | ºC |  | 1.4 | 1.6 | 1.6 | 1.6 | 1.5 | 1.1 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | [9 empty] | 0.9
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.9 | 14 | 14.3 | 14.4 | 14.6 | 14.8 | 14.6 | 13.8 | 14.6 | 14.3 | 14.3 | 14.3 | 14.2 | 14 | 13.7 | [9 empty] | 14.2533
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.1 | 6.6 | 6.6 | 6.6 | 7.1 | 8 | 7.9 | 8.2 | 8.1 | 8 | 8 | 7.8 | 8 | 6.7 | [9 empty] | 7.3333
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.2 | 20.8 | 20.3 | 20.6 | 21.1 | 21.4 | 24.2 | 25.1 | 27.3 | 26.8 | 26.1 | 26 | 26 | 25.2 | 25.3 | [9 empty] | 23.8267
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.1 | 26.8 | 26.4 | 26.8 | 27.2 | 27.5 | 29.3 | 29.7 | 32.1 | 31.5 | 31 | 30.7 | 30.8 | 29.8 | 30.6 | [9 empty] | 29.1533
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [9 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [9 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [9 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [9 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [9 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2536.6733 | 2472.4537 | 2504.5635 | 2568.7831 | 2472.4537 | 2119.246 | 1894.4775 | 2055.0265 | 1990.8069 | 2022.9167 | 2022.9167 | 2055.0265 | 1926.5873 | 2247.6852 | [9 empty] | 33329.9603
15 | Power Consumption of Chiller | KWH |  | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | [9 empty] | 20700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.56549 | 0.54402 | 0.55815 | 0.55099 | 0.53722 | 0.55815 | 0.65117 | 0.72843 | 0.67152 | 0.69319 | 0.68218 | 0.68218 | 0.67152 | 0.71629 | 0.61396 | [9 empty] | 0.6283
17 | Average iKW/TR |  |  | Hours 7: 0.6283 | 0.6283
18 | COP of chiller |  |  | 6.2176 | 6.463 | 6.2994 | 6.3812 | 6.5448 | 6.2994 | 5.3995 | 4.8268 | 5.2359 | 5.0722 | 5.154 | 5.154 | 5.2359 | 4.9086 | 5.7267 | [9 empty] | 5.6613
19 | EER of Chiller |  |  | 21.2206 | 22.0582 | 21.4998 | 21.779 | 22.3374 | 21.4998 | 18.4284 | 16.4739 | 17.87 | 17.3115 | 17.5907 | 17.5907 | 17.87 | 16.7531 | 19.5453 | [9 empty] | 19.3219
20 | LMTD of Condenser | ºC |  | 4.4112 | 4.5604 | 4.7093 | 4.5113 | 4.5941 | 4.1242 | 3.6789 | 3.396 | 3.4625 | 3.4293 | 3.4955 | 3.4293 | 3.2256 | 3.5117 | 3.7448 | [9 empty] | 3.8856
21 | LMTD of Evaporator | ºC |  | 4.0844 | 4.435 | 4.375 | 4.405 | 4.3341 | 3.7029 | 2.3059 | 2.1401 | 2.4384 | 2.5538 | 2.5795 | 2.5795 | 2.6051 | 2.5022 | 2.3991 | [9 empty] | 3.1627
Performance Sheet Chiller
Date :- 13/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [6 empty] | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.6 | 0.8 | 0.9 | 0.8 | 0.9 | 0.8 | 0.9 | 0.9 | 0.8 | 0.76842
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.8 | 0.7 | 0.7 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.4 | 0.4 | 0.4 | 0.2 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.42105
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 17.6 | 14.8 | 14.7 | 14.8 | 14.6 | 14.5 | 14.5 | 14.4 | 14.2 | 13.9 | 13.3 | 12.8 | 13.6 | 13.8 | 14.2 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3632
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 14.8 | 8.1 | 8.1 | 8 | 8 | 8 | 7.8 | 8 | 7.6 | 6.5 | 6 | 5.5 | 5.7 | 5.7 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 7.2
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 21.6 | 24.5 | 27.3 | 27.5 | 27 | 26.5 | 26.2 | 26.3 | 25.5 | 25.6 | 25.9 | 24.8 | 23.1 | 22.2 | 22 | 22.7 | 21.8 | 21.8 | 22.3 | 24.4526
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 21.2 | 28.9 | 31.6 | 32.1 | 31.4 | 30.8 | 30.6 | 30.6 | 29.7 | 30.7 | 31 | 29.8 | 28.2 | 27.7 | 27.7 | 28.3 | 27.6 | 27.5 | 28 | 29.1263
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 899.0741 | 2151.3558 | 2119.246 | 2183.4656 | 2119.246 | 2087.1362 | 2151.3558 | 2055.0265 | 2119.246 | 2376.1243 | 2344.0146 | 2344.0146 | 2536.6733 | 2600.8929 | 2697.2222 | 2729.332 | 2729.332 | 2729.332 | 2729.332 | 43701.422
15 | Power Consumption of Chiller | KWH | [6 empty] | 1208.7 | 669.7 | 1424.3 | 1378.1 | 1393.5 | 1393.5 | 1316.5 | 1316.5 | 1439.7 | 1485.9 | 1439.7 | 1578.3 | 1562.9 | 1470.5 | 1655.3 | 1609.1 | 1455.1 | 1470.5 | 1532.2 | 26800
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 1.3444 | 0.31129 | 0.67208 | 0.63115 | 0.65755 | 0.66766 | 0.61194 | 0.64062 | 0.67935 | 0.62535 | 0.6142 | 0.67333 | 0.61612 | 0.56538 | 0.61371 | 0.58956 | 0.53313 | 0.53878 | 0.56138 | 0.63931
17 | Average iKW/TR |  |  | Hours 7: 0.63931 | 0.63931
18 | COP of chiller | [7 empty] | 2.6153 | 11.2949 | 5.2315 | 5.5708 | 5.3472 | 5.2661 | 5.7457 | 5.4884 | 5.1756 | 5.6225 | 5.7245 | 5.2218 | 5.7067 | 6.2188 | 5.7291 | 5.9638 | 6.595 | 6.5259 | 6.2631 | 5.8582
19 | EER of Chiller | [7 empty] | 8.9261 | 38.5494 | 17.8552 | 19.013 | 18.2499 | 17.9733 | 19.61 | 18.7319 | 17.6642 | 19.1895 | 19.5377 | 17.822 | 19.4768 | 21.2248 | 19.5535 | 20.3544 | 22.5086 | 22.2729 | 21.376 | 19.9942
20 | LMTD of Condenser | ºC | [6 empty] | 0.57708 | 2.2156 | 2.1871 | 2.2723 | 2.2156 | 2.1871 | 2.2156 | 2.1871 | 2.2918 | 2.4119 | 2.2654 | 2.524 | 2.6883 | 2.6651 | 2.8608 | 2.693 | 2.8892 | 2.8608 | 2.7208 | 2.3647
21 | LMTD of Evaporator | ºC | [6 empty] | 1.8616 | 2.8412 | 2.815 | 2.5363 | 2.1049 | 2.0827 | 2.1271 | 1.8304 | 2.1049 | 2.4912 | 2.4683 | 2.4683 | 2.1344 | 2.6502 | 2.7175 | 2.9408 | 2.7399 | 2.7399 | 2.7399 | 2.4418

## 14-02-2019 (hidden)
Chiller Operation
Performance Sheet Chiller
Date :- 14/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [11 empty] | 2.4 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2 | 2.1 | 2.1 | 2.2 | 2.1 | 2.2 | 2.1 | 2.2 | 2.1429
2 | Small temperature difference of evaporator | ºC | [11 empty] | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.33571
3 | Entering Chilled Water Temp. (tchwe) | ºC | [11 empty] | 15.5 | 15.6 | 14.8 | 14.6 | 14.3 | 13.7 | 13.1 | 12.2 | 12.5 | 13.3 | 13.8 | 14.2 | 14.5 | 14.6 | 14.05
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [11 empty] | 10 | 8.2 | 8 | 7.5 | 7 | 6.6 | 6 | 5.6 | 5.4 | 5.7 | 6.1 | 6.3 | 6.5 | 6.5 | 6.8143
5 | Entering Condenser Water Temp. (tcwe) | ºC | [11 empty] | 20.6 | 24.8 | 25.8 | 25.9 | 26.1 | 26 | 25.5 | 25.1 | 22.2 | 22.1 | 22.5 | 22.7 | 22.8 | 22.8 | 23.9214
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [11 empty] | 25.2 | 29.6 | 30.3 | 30.4 | 30.7 | 30.6 | 30.1 | 29.3 | 26.5 | 27 | 27.3 | 27.8 | 27.7 | 27.9 | 28.6
7 | Chilled water inlet pressure | (Kg/Cm2) | [11 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [11 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [11 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [11 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [11 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [11 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [11 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [11 empty] | 1766.0384 | 2376.1243 | 2183.4656 | 2279.795 | 2344.0146 | 2279.795 | 2279.795 | 2119.246 | 2279.795 | 2440.3439 | 2472.4537 | 2536.6733 | 2568.7831 | 2600.8929 | 32527.2156
15 | Power Consumption of Chiller | KWH | [11 empty] | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1450 | 19000
16 | Specific power consumption of Chiller | (iKW/TR) | [11 empty] | 0.76442 | 0.56815 | 0.61828 | 0.59216 | 0.57593 | 0.59216 | 0.59216 | 0.63702 | 0.59216 | 0.5532 | 0.54602 | 0.53219 | 0.52554 | 0.5575 | 0.58906
17 | Average iKW/TR |  |  | 0.58906 | [23 empty] | 0.58906
18 | COP of chiller | [12 empty] | 4.5995 | 6.1885 | 5.6867 | 5.9376 | 6.1049 | 5.9376 | 5.9376 | 5.5195 | 5.9376 | 6.3557 | 6.4394 | 6.6066 | 6.6903 | 6.3067 | 6.0177
19 | EER of Chiller | [12 empty] | 15.6983 | 21.1213 | 19.4088 | 20.265 | 20.8359 | 20.265 | 20.265 | 18.8379 | 20.265 | 21.6921 | 21.9776 | 22.5484 | 22.8338 | 21.5248 | 20.5385
20 | LMTD of Condenser | ºC | [11 empty] | 4.2973 | 4.035 | 3.9297 | 3.9297 | 4.0763 | 3.9649 | 3.8528 | 3.823 | 3.8587 | 4.1822 | 4.035 | 4.2521 | 4.0699 | 4.2521 | 4.0399
21 | LMTD of Evaporator | ºC | [11 empty] | 2.0437 | 2.4912 | 2.1491 | 2.215 | 2.2586 | 2.215 | 2.215 | 2.1049 | 2.215 | 2.5369 | 2.5597 | 2.3881 | 2.4095 | 2.6502 | 2.318
Chiller Operation
Performance Sheet Chiller
Date :- 14/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C | [27 empty] | Average
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.8 | 0.9 | 0.7 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.81176
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.4 | 0.1 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [7 empty] | 0.35294
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.2 | 14.1 | 14.6 | 14.8 | 14.8 | 14.6 | 14.3 | 14.3 | 14.3 | 14.3 | 14.4 | 15.7 | 15 | 14.6 | 14.3 | 13.8 | 13.2 | [7 empty] | 14.4294
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.7 | 5.7 | 6.1 | 6.4 | 6.5 | 6.5 | 6.3 | 6.4 | 6.3 | 6.2 | 6.4 | 8.2 | 7.8 | 7.5 | 6.7 | 6 | 5.8 | [7 empty] | 6.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.7 | 21.7 | 21.8 | 22.7 | 22.8 | 23.6 | 24.1 | 24.5 | 23.9 | 23.8 | 23.8 | 24.9 | 25.9 | 25.9 | 26.1 | 26 | 25.6 | [7 empty] | 24.0471
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.4 | 27.4 | 27.5 | 28.3 | 28.3 | 29 | 29.4 | 29.7 | 29.2 | 29.3 | 29.1 | 30 | 30.7 | 30.8 | 31.5 | 31.4 | 30.6 | [7 empty] | 29.3882
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2729.332 | 2697.2222 | 2729.332 | 2697.2222 | 2665.1124 | 2600.8929 | 2568.7831 | 2536.6733 | 2568.7831 | 2600.8929 | 2568.7831 | 2408.2341 | 2311.9048 | 2279.795 | 2440.3439 | 2504.5635 | 2376.1243 | [7 empty] | 43283.9947
15 | Power Consumption of Chiller | KWH |  | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.96 | [7 empty] | 21300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.45906 | 0.46453 | 0.45906 | 0.46453 | 0.47013 | 0.48173 | 0.48776 | 0.49393 | 0.48776 | 0.48173 | 0.48776 | 0.52027 | 0.54195 | 0.54958 | 0.51343 | 0.50026 | 0.52731 | [7 empty] | 0.49358
17 | Average iKW/TR |  |  | 0.49358 | [23 empty] | 0.49358
18 | COP of chiller |  |  | 7.6591 | 7.5689 | 7.6591 | 7.5689 | 7.4788 | 7.2986 | 7.2085 | 7.1184 | 7.2085 | 7.2986 | 7.2085 | 6.758 | 6.4877 | 6.3976 | 6.8481 | 7.0283 | 6.6678 | [7 empty] | 7.1449
19 | EER of Chiller |  |  | 26.1403 | 25.8328 | 26.1403 | 25.8328 | 25.5253 | 24.9102 | 24.6027 | 24.2951 | 24.6027 | 24.9102 | 24.6027 | 23.065 | 22.1424 | 21.8349 | 23.3725 | 23.9876 | 22.7571 | [7 empty] | 24.3856
20 | LMTD of Condenser | ºC |  | 2.7208 | 2.7208 | 2.7208 | 2.693 | 2.6651 | 2.6371 | 2.7462 | 2.5808 | 2.7462 | 2.5215 | 2.7462 | 2.5524 | 2.4667 | 2.4954 | 2.6371 | 2.6371 | 2.524 | [7 empty] | 2.636
21 | LMTD of Evaporator | ºC |  | 2.7399 | 2.7175 | 2.7399 | 2.4946 | 2.4734 | 2.8472 | 2.8236 | 2.8 | 2.6277 | 1.8381 | 2.6277 | 2.302 | 2.2368 | 2.215 | 2.3236 | 2.3666 | 2.2803 | [7 empty] | 2.4973

## 15-02-2019 (hidden)
Performance Sheet Chiller
Date :- 15/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  |  |  | 1.8 | 1.6 | 1.4 | 1.4 | 1.4 | 1.4 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.6 | 1.4 | 1.6 | 1.8 | 1.8 | 1.6 | 1.8 | 1.6 | 1.6 | 1.8 | 1.8 | 1.5818
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.8 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.5 | 0.4 | 0.4 | 6 | 0.6 | 0.5 | 0.7 | 0.9 | 1.5 | 1.4 | 1.1 | 1.2 | 1.4 | 1.4 | 1.4 | 1.4 | 1.1136
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 14.3 | 14.6 | 13.6 | 13 | 12.8 | 12.9 | 13 | 13.1 | 13.4 | 13.5 | 13.5 | 13.3 | 13 | 12.4 | 13.2 | 13.6 | 13.7 | 13.6 | 13.5 | 13.4 | 13.3 | 13.2 | 13.3591
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 9 | 7.3 | 6.8 | 6.9 | 7 | 7 | 7 | 6.8 | 7 | 7.1 | 7 | 7 | 5.9 | 5.5 | 5.7 | 5.8 | 5.8 | 5.8 | 5.8 | 5.5 | 5.6 | 5.7 | 6.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 21.1 | 24.3 | 25.1 | 24.3 | 24.5 | 24.5 | 25.1 | 25.3 | 26.1 | 26 | 25.6 | 25 | 25.1 | 23.3 | 22.1 | 21.5 | 21 | 20.8 | 20.1 | 20.2 | 21.1 | 21.5 | 23.3455
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 26.7 | 29.9 | 30.1 | 29 | 29 | 29 | 29.7 | 30.1 | 31.1 | 31 | 30.5 | 29.8 | 30.5 | 28.6 | 27.9 | 27.5 | 27.1 | 26.8 | 26.2 | 26.3 | 27 | 27.3 | 28.6864
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 1701.8188 | 2344.0146 | 2183.4656 | 1958.6971 | 1862.3677 | 1894.4775 | 1926.5873 | 2022.9167 | 2055.0265 | 2055.0265 | 2087.1362 | 2022.9167 | 2279.795 | 2215.5754 | 2408.2341 | 2504.5635 | 2536.6733 | 2504.5635 | 2472.4537 | 2536.6733 | 2472.4537 | 2408.2341 | 48453.6706
15 | Power Consumption of Chiller | KWH |  |  |  | 1530 | 1530 | 1484 | 1484 | 1484 | 1530 | 1530 | 1530 | 1530 | 1484 | 1484 | 1550 | 1550 | 1550 | 1550 | 1580 | 1580 | 1580 | 1580 | 1550 | 1550 | 1580 | 33800
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.89904 | 0.65273 | 0.67965 | 0.75765 | 0.79684 | 0.80761 | 0.79415 | 0.75633 | 0.74452 | 0.72213 | 0.71102 | 0.76622 | 0.67989 | 0.69959 | 0.64363 | 0.63085 | 0.62286 | 0.63085 | 0.63904 | 0.61104 | 0.62691 | 0.65608 | 0.70585
17 | Average iKW/TR |  |  | 0.70585 | [23 empty] | 0.70585
18 | COP of chiller |  |  |  |  | 3.9108 | 5.3866 | 5.1732 | 4.6407 | 4.4125 | 4.3536 | 4.4274 | 4.6487 | 4.7225 | 4.8689 | 4.945 | 4.5888 | 5.1715 | 5.0258 | 5.4628 | 5.5734 | 5.6449 | 5.5734 | 5.502 | 5.7542 | 5.6085 | 5.3591 | 5.0343
19 | EER of Chiller |  |  |  |  | 13.3477 | 18.3846 | 17.6562 | 15.8387 | 15.0597 | 14.8588 | 15.1106 | 15.8662 | 16.118 | 16.6176 | 16.8773 | 15.6614 | 17.6502 | 17.153 | 18.6446 | 19.0222 | 19.266 | 19.0222 | 18.7783 | 19.6389 | 19.1417 | 18.2906 | 17.182
20 | LMTD of Condenser | ºC |  |  |  | 3.9613 | 3.7232 | 3.2899 | 3.1933 | 3.1283 | 3.1283 | 3.2791 | 3.3448 | 3.4099 | 3.4099 | 3.2578 | 3.4625 | 3.4167 | 3.6264 | 4.0268 | 4.0918 | 3.8823 | 4.0918 | 3.8823 | 3.8823 | 4.0594 | 4.0268 | 3.617
21 | LMTD of Evaporator | ºC |  |  |  | 2.609 | 2.832 | 2.7067 | 2.528 | 2.2891 | 2.4763 | 2.3392 | 2.2353 | 2.2589 | 8.8162 | 2.6306 | 2.4137 | 2.9451 | 3.1952 | 4.1858 | 4.1429 | 3.7585 | 3.8712 | 4.1137 | 4.1721 | 4.1137 | 4.055 | 3.3949
Performance Sheet Chiller
Date :- 15/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | [24 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 2.3 | 2.4 | 2.1 | 1.9 | 1.8 | 1.7 | 1.7 | 1.7 | 1.7 | 1.9 | 1.8 | 1.7 | 1.8 | 1.9 | [10 empty] | 1.8857
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.4 | [10 empty] | 0.32857
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.7 | 14.7 | 15.3 | 14.2 | 13.7 | 13.1 | 13 | 13 | 13.2 | 13.3 | 13.6 | 13.7 | 13.6 | 13.5 | [10 empty] | 13.7571
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.8 | 6.6 | 7 | 7.1 | 7 | 6.9 | 7 | 7.1 | 7.1 | 7.1 | 7 | 7 | 6.8 | 7 | [10 empty] | 6.9643
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.8 | 22.8 | 22.1 | 25.2 | 25.2 | 24.6 | 24.7 | 24.8 | 25.3 | 25.5 | 26.2 | 26.3 | 25.8 | 25.2 | [10 empty] | 24.75
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28 | 27.8 | 27.3 | 29.8 | 29.5 | 28.5 | 28.6 | 28.7 | 29.3 | 29.5 | 30.5 | 30.5 | 30.2 | 29.4 | [10 empty] | 29.1143
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [10 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [10 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [10 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [10 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [10 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [10 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [10 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2600.8929 | 2665.1124 | 2279.795 | 2151.3558 | 1990.8069 | 1926.5873 | 1894.4775 | 1958.6971 | 1990.8069 | 2119.246 | 2151.3558 | 2183.4656 | 2087.1362 | [10 empty] | 30536.4087
15 | Power Consumption of Chiller | KWH |  | 1340 | 1260 | 1300 | 1240 | 1260 | 1240 | 1240 | 1240 | 1240 | 1300 | 1260 | 1260 | 1260 | 1260 | [10 empty] | 17700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.52825 | 0.48445 | 0.48778 | 0.54391 | 0.58568 | 0.62286 | 0.64363 | 0.65453 | 0.63307 | 0.653 | 0.59455 | 0.58568 | 0.57706 | 0.6037 | [10 empty] | 0.58558
17 | Average iKW/TR |  |  | 0.58558 | [23 empty] | 0.58558
18 | COP of chiller |  |  | 6.6559 | 7.2577 | 7.2081 | 6.4643 | 6.0033 | 5.6449 | 5.4628 | 5.3718 | 5.5539 | 5.3844 | 5.9137 | 6.0033 | 6.0929 | 5.8241 | [10 empty] | 6.0601
19 | EER of Chiller |  |  | 22.7167 | 24.7706 | 24.6013 | 22.0627 | 20.4893 | 19.266 | 18.6446 | 18.3338 | 18.9553 | 18.3768 | 20.1835 | 20.4893 | 20.7951 | 19.8777 | [10 empty] | 20.683
20 | LMTD of Condenser | ºC |  | 4.3993 | 4.4405 | 4.1736 | 3.74 | 3.5231 | 3.2714 | 3.2714 | 3.2714 | 3.3062 | 3.5301 | 3.5231 | 3.3753 | 3.5577 | 3.6007 | [10 empty] | 3.6417
21 | LMTD of Evaporator | ºC |  | 2.6051 | 2.6502 | 2.6951 | 2.215 | 2.1271 | 1.7889 | 1.9708 | 1.9481 | 1.9933 | 2.0158 | 2.1049 | 2.3293 | 2.1491 | 2.2825 | [10 empty] | 2.2054

## 16-02-2019 (hidden)
Performance Sheet Chiller
Date :- 16/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.6 | 1.4 | 1.6 | 1.6 | 1.6 | 1.7 | 0.9 | 0.9 | 1.4 | 1.4 | [8 empty] | 1.5562
2 | Small temperature difference of evaporator | ºC |  | 1.5 | 1.7 | 1.6 | 1.7 | 1.6 | 1.6 | 1.2 | 0.9 | 0.8 | 0.9 | 1.1 | 1.4 | 0.3 | 0.3 | 0.7 | 0.6 | [8 empty] | 1.1188
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.1 | 13.5 | 13.6 | 13.6 | 13.1 | 12.6 | 12 | 12 | 12.1 | 12.3 | 14 | 14.6 | 15.1 | 13.5 | 13.3 | [8 empty] | 13.2188
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.5 | 5.8 | 5.8 | 5.8 | 5.6 | 5.5 | 5.3 | 5.5 | 5.6 | 5.5 | 6.4 | 6.8 | 7.9 | 7.1 | 7 | [8 empty] | 6.0375
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.5 | 20.4 | 20.7 | 20 | 20 | 20 | 20 | 20.7 | 22 | 22.1 | 22.1 | 22.6 | 21.9 | 23.7 | 24 | 24 | [8 empty] | 21.5437
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.3 | 26.3 | 26.7 | 26.1 | 26 | 26 | 25.5 | 25.8 | 27 | 27.1 | 27.3 | 28.3 | 28 | 29.2 | 29 | 28.9 | [8 empty] | 27.0938
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2440.3439 | 2472.4537 | 2504.5635 | 2504.5635 | 2408.2341 | 2279.795 | 2151.3558 | 2087.1362 | 2087.1362 | 2183.4656 | 2440.3439 | 2504.5635 | 2311.9048 | 2055.0265 | 2022.9167 | [8 empty] | 36894.1468
15 | Power Consumption of Chiller | KWH |  | 1345 | 1400 | 1375 | 1345 | 1345 | 1345 | 1320 | 1320 | 1295 | 1340 | 1390 | 1345 | 1345 | 1300 | 1345 | 1345 | [8 empty] | 21500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.55115 | 0.57369 | 0.55613 | 0.53702 | 0.53702 | 0.5585 | 0.579 | 0.61357 | 0.62047 | 0.64203 | 0.6366 | 0.55115 | 0.53702 | 0.56231 | 0.65449 | 0.66488 | [8 empty] | 0.58594
17 | Average iKW/TR |  |  | 0.58594 | [23 empty] | 0.58594
18 | COP of chiller |  |  | 6.3794 | 6.1287 | 6.3223 | 6.5472 | 6.5472 | 6.2954 | 6.0725 | 5.7304 | 5.6667 | 5.4764 | 5.5231 | 6.3794 | 6.5472 | 6.2528 | 5.3721 | 5.2882 | [8 empty] | 6.0331
19 | EER of Chiller |  |  | 21.7728 | 20.9174 | 21.578 | 22.3457 | 22.3457 | 21.4863 | 20.7256 | 19.558 | 19.3404 | 18.6909 | 18.8502 | 21.7728 | 22.3457 | 21.3409 | 18.335 | 18.0485 | [8 empty] | 20.5909
20 | LMTD of Condenser | ºC |  | 4.0268 | 4.0594 | 4.0918 | 4.1242 | 4.0918 | 4.0918 | 3.691 | 3.3218 | 3.5284 | 3.5284 | 3.5938 | 3.8753 | 2.9738 | 2.8037 | 3.2899 | 3.2578 | [8 empty] | 3.6469
21 | LMTD of Evaporator | ºC |  | 4.2156 | 4.4722 | 4.375 | 4.5331 | 4.405 | 4.3146 | 3.6713 | 3.1404 | 2.9398 | 3.0852 | 3.4491 | 4.0844 | 2.3666 | 2.2368 | 2.7625 | 2.5795 | [8 empty] | 3.5394
Performance Sheet Chiller
Date :- 16/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [13 empty] | 0.9 | 0.9 | 0.8 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 0.86667
2 | Small temperature difference of evaporator | ºC | [13 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.34167
3 | Entering Chilled Water Temp. (tchwe) | ºC | [13 empty] | 15.2 | 15.3 | 14 | 13.6 | 12.8 | 12.5 | 13.1 | 13.2 | 13.3 | 13.3 | 13.2 | 13.2 | 13.5583
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [13 empty] | 8 | 7.8 | 7.8 | 7 | 5.8 | 5.4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.4 | 5.5 | 6.225
5 | Entering Condenser Water Temp. (tcwe) | ºC | [13 empty] | 22 | 23.8 | 24.3 | 24.2 | 24.3 | 20.8 | 19.2 | 20 | 19.8 | 19.6 | 19.2 | 19.3 | 21.375
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [13 empty] | 21.3 | 29 | 28.5 | 28.7 | 29.1 | 25.6 | 24.2 | 25.1 | 25.1 | 24.8 | 24.4 | 24.5 | 25.8583
7 | Chilled water inlet pressure | (Kg/Cm2) | [13 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [13 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [13 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [13 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [13 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [13 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [13 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [13 empty] | 2311.9048 | 2408.2341 | 1990.8069 | 2119.246 | 2247.6852 | 2279.795 | 2440.3439 | 2472.4537 | 2504.5635 | 2504.5635 | 2504.5635 | 2472.4537 | 28256.6138
15 | Power Consumption of Chiller | KWH | [13 empty] | 1315 | 1315 | 1325 | 1320 | 1315 | 1315 | 1315 | 1320 | 1315 | 1315 | 1315 | 1315 | 15800
16 | Specific power consumption of Chiller | (iKW/TR) | [13 empty] | 0.5688 | 0.54604 | 0.66556 | 0.62286 | 0.58505 | 0.57681 | 0.53886 | 0.53388 | 0.52504 | 0.52504 | 0.52504 | 0.53186 | 0.56207
17 | Average iKW/TR |  |  | 0.56207 | [23 empty] | 0.56207
18 | COP of chiller | [14 empty] | 6.1815 | 6.4391 | 5.2828 | 5.6449 | 6.0098 | 6.0956 | 6.5249 | 6.5857 | 6.6966 | 6.6966 | 6.6966 | 6.6108 | 6.2887
19 | EER of Chiller | [14 empty] | 21.0974 | 21.9765 | 18.0301 | 19.266 | 20.5114 | 20.8044 | 22.2695 | 22.4771 | 22.8555 | 22.8555 | 22.8555 | 22.5625 | 21.4635
20 | LMTD of Condenser | ºC | [13 empty] | 0.4654 | 2.7173 | 2.2918 | 2.244 | 2.3285 | 2.6005 | 2.6591 | 2.6883 | 2.7462 | 2.7173 | 2.7173 | 2.85 | 2.4188
21 | LMTD of Evaporator | ºC | [13 empty] | 2.2368 | 2.302 | 2.0158 | 2.1049 | 2.1931 | 2.215 | 2.5369 | 2.5597 | 2.5824 | 2.3666 | 2.5824 | 2.5597 | 2.3546

## 17-02-2019 (hidden)
Performance Sheet Chiller
Date :- 17/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [11 empty] | 1.4 | 1.4 | 1.1 | 1.1 | 1.1 | 1.5 | 1.6 | 1.6 | 1.5 | 1.5 | 1.6 | 1.5 | 1.6 | 1.6 | 1.4357
2 | Small temperature difference of evaporator | ºC | [11 empty] | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 1.1 | 1.2 | 1.2 | 1.3 | 1.3 | 1.4 | 1.3 | 1.4 | 1.0857
3 | Entering Chilled Water Temp. (tchwe) | ºC | [11 empty] | 15 | 15 | 13.8 | 13.3 | 13.3 | 12.2 | 12.7 | 13.3 | 13.6 | 13.8 | 13.8 | 13.7 | 13.7 | 13.8 | 13.6429
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [11 empty] | 8 | 7.9 | 7.8 | 7.1 | 6.1 | 5.4 | 5.7 | 5.7 | 6.2 | 6.2 | 6.1 | 6.1 | 6 | 6.1 | 6.4571
5 | Entering Condenser Water Temp. (tcwe) | ºC | [11 empty] | 19.9 | 24.2 | 24.2 | 24 | 25.2 | 23.7 | 22.6 | 22.4 | 21.9 | 21.4 | 21.7 | 21.7 | 21.8 | 21.3 | 22.5714
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [11 empty] | 25 | 29.6 | 28.8 | 28.8 | 30.6 | 29 | 28 | 28.3 | 27.7 | 27.3 | 27.7 | 27.7 | 27.8 | 27.3 | 28.1143
7 | Chilled water inlet pressure | (Kg/Cm2) | [11 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [11 empty] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) | [11 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [11 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [11 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [11 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [11 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [11 empty] | 2247.6852 | 2279.795 | 1926.5873 | 1990.8069 | 2311.9048 | 2183.4656 | 2247.6852 | 2215.5754 | 2215.5754 | 2215.5754 | 2215.5754 | 2215.5754 | 2215.5754 | 2215.5754 | 30696.9577
15 | Power Consumption of Chiller | KWH | [11 empty] | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.3 | 22300
16 | Specific power consumption of Chiller | (iKW/TR) | [11 empty] | 0.70868 | 0.6987 | 0.8268 | 0.80013 | 0.689 | 0.72953 | 0.70868 | 0.40622 | 0.40622 | 0.40622 | 0.40622 | 0.40622 | 0.40622 | 0.40622 | 0.57179
17 | Average iKW/TR |  |  | 0.57179 | [23 empty] | 0.57179
18 | COP of chiller | [12 empty] | 4.9613 | 5.0322 | 4.2525 | 4.3943 | 5.1031 | 4.8196 | 4.9613 | 8.6555 | 8.6555 | 8.6555 | 8.6555 | 8.6555 | 8.6555 | 8.6555 | 6.7223
19 | EER of Chiller | [12 empty] | 16.9329 | 17.1748 | 14.5139 | 14.9977 | 17.4167 | 16.4491 | 16.9329 | 29.5413 | 29.5413 | 29.5413 | 29.5413 | 29.5413 | 29.5413 | 29.5413 | 22.9434
20 | LMTD of Condenser | ºC | [11 empty] | 3.3218 | 3.4167 | 2.7961 | 2.8578 | 3.0397 | 3.5065 | 3.6588 | 4.0408 | 4.0408 | 4.0408 | 4.0408 | 4.0408 | 4.0408 | 4.0408 | 3.6345
21 | LMTD of Evaporator | ºC | [11 empty] | 3.2225 | 3.1004 | 2.8037 | 2.8584 | 3.1269 | 3.1678 | 3.506 | 2.3759 | 2.3759 | 2.3759 | 2.3759 | 2.3759 | 2.3759 | 2.3759 | 2.7441
Performance Sheet Chiller
Date :- 17/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1 | 1 | 0.9 | 0.9 | 1 | 1.1 | 0.9 | 0.9 | 1 | 1 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | [9 empty] | 0.90667
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | [9 empty] | 0.34667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.1 | 13.4 | 13.5 | 13.6 | 13.9 | 14.1 | 14.3 | 14.7 | 15 | 15.4 | 15.3 | 14.1 | 13.7 | 13.6 | [9 empty] | 14.0533
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.7 | 5.6 | 5.6 | 5.6 | 5.7 | 5.7 | 5.7 | 6 | 6.1 | 7.7 | 7.8 | 7.8 | 8 | 6.2 | [9 empty] | 6.32
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 19.2 | 19.2 | 19.8 | 19.4 | 19.6 | 20.5 | 21.3 | 22.1 | 22.1 | 22.2 | 23.1 | 24.3 | 24.5 | 24.1 | 25.3 | [9 empty] | 21.78
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 24.2 | 24.2 | 24.9 | 24.7 | 24.9 | 26 | 26.8 | 27.9 | 28.1 | 28.2 | 28.2 | 29.3 | 28.6 | 28 | 30.4 | [9 empty] | 26.96
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [9 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | [9 empty] | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [9 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [9 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [9 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [9 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2376.1243 | 2504.5635 | 2536.6733 | 2568.7831 | 2633.0026 | 2697.2222 | 2761.4418 | 2793.5516 | 2857.7712 | 2472.4537 | 2408.2341 | 2022.9167 | 1830.2579 | 2376.1243 | [9 empty] | 37247.3545
15 | Power Consumption of Chiller | KWH |  | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1270 | 1270 | 1300 | 1320 | 1210 | 1210 | 1200 | 1260 | 1240 | [9 empty] | 18600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.5066 | 0.51344 | 0.48711 | 0.48094 | 0.47493 | 0.46335 | 0.47085 | 0.4599 | 0.46536 | 0.4619 | 0.48939 | 0.50244 | 0.5932 | 0.68843 | 0.52186 | [9 empty] | 0.50531
17 | Average iKW/TR |  |  | 0.50531 | [23 empty] | 0.50531
18 | COP of chiller |  |  | 6.9405 | 6.8479 | 7.2181 | 7.3106 | 7.4031 | 7.5882 | 7.4673 | 7.6451 | 7.5555 | 7.6121 | 7.1844 | 6.9978 | 5.9271 | 5.1073 | 6.7375 | [9 empty] | 7.0362
19 | EER of Chiller |  |  | 23.6878 | 23.3719 | 24.6353 | 24.9511 | 25.2669 | 25.8986 | 25.4858 | 26.0926 | 25.7869 | 25.98 | 24.5204 | 23.8835 | 20.2293 | 17.4312 | 22.995 | [9 empty] | 24.0144
20 | LMTD of Condenser | ºC |  | 2.7906 | 2.7906 | 2.6883 | 2.7462 | 2.8796 | 3.0696 | 2.8037 | 2.8892 | 3.0834 | 3.0834 | 2.6883 | 2.6591 | 2.1295 | 2.0715 | 2.4119 | [9 empty] | 2.719
21 | LMTD of Evaporator | ºC |  | 2.5141 | 2.4912 | 2.5824 | 2.6051 | 2.6277 | 2.6727 | 2.7175 | 2.7622 | 2.7844 | 2.8287 | 2.3451 | 2.302 | 1.8097 | 1.6842 | 2.0343 | [9 empty] | 2.4508

## 18-02-2019 (hidden)
Performance Sheet Chiller
Date :- 18/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.7 | 1.7 | 1.6 | 1.7 | 1.7 | 1.7 | 1.6 | 1.6 | 1.5 | 1.4 | 1.4 | 1.2 | 1.2 | 1.6 | 1.8 | 1.6 | 1.6 | 1.6 | 1.7 | 1.6 | 1.6 | 1.4 | 1.5 | 1 | 1.5417
2 | Small temperature difference of evaporator | ºC |  | 1.5 | 1.6 | 1.7 | 1.7 | 1.7 | 1.6 | 1.5 | 1.5 | 1.5 | 0.8 | 1.1 | 1.1 | 1.2 | 1 | 0.7 | 1.2 | 1.4 | 1.6 | 1.4 | 1.3 | 1.4 | 1.3 | 1.4 | 1.3 | 1.3542
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.7 | 13.5 | 13.7 | 13.7 | 13.7 | 14 | 14.2 | 14.5 | 14.9 | 15.3 | 14.7 | 13.8 | 13.6 | 13.5 | 13 | 12.2 | 13.2 | 13.7 | 13.7 | 13.8 | 13.8 | 13.8 | 13.7 | 13.7 | 13.8083
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6 | 5.7 | 5.9 | 5.9 | 5.9 | 6.3 | 6.5 | 6.7 | 7.2 | 7.6 | 8 | 8 | 8.1 | 7.2 | 5.8 | 5.5 | 5.8 | 6.2 | 6.1 | 6.1 | 6.2 | 6.2 | 6.1 | 6.1 | 6.4625
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.8 | 20.5 | 20.8 | 20.3 | 20.1 | 20.4 | 20.6 | 22.2 | 22.6 | 22.9 | 24.6 | 22.6 | 22.5 | 22.1 | 22.4 | 22.4 | 21.6 | 21.4 | 20.7 | 21.3 | 21 | 20.8 | 21.2 | 21 | 21.5333
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.8 | 26.6 | 26.8 | 26.4 | 26.2 | 26.5 | 26.7 | 28.2 | 28.5 | 28.9 | 29.8 | 27.3 | 26.8 | 27 | 28 | 27.7 | 27.4 | 27.3 | 26.7 | 27.2 | 27 | 26.8 | 27.2 | 27 | 27.2833
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2472.4537 | 2504.5635 | 2504.5635 | 2504.5635 | 2504.5635 | 2472.4537 | 2472.4537 | 2504.5635 | 2472.4537 | 2472.4537 | 2151.3558 | 1862.3677 | 1766.0384 | 2022.9167 | 2311.9048 | 2151.3558 | 2376.1243 | 2408.2341 | 2440.3439 | 2472.4537 | 2440.3439 | 2440.3439 | 2440.3439 | 2440.3439 | 56609.5569
15 | Power Consumption of Chiller | KWH |  | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1400 | 1400 | 1200 | 1300 | 1400 | 1600 | 1400 | 1300 | 1600 | 1500 | 1400 | 1500 | 1600 | 1500 | 1500 | 25000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.68758 | 0.67876 | 0.67876 | 0.67876 | 0.67876 | 0.68758 | 0.68758 | 0.67876 | 0.68758 | 0.56624 | 0.65075 | 0.64434 | 0.73611 | 0.69207 | 0.69207 | 0.65075 | 0.54711 | 0.66439 | 0.61467 | 0.56624 | 0.61467 | 0.65565 | 0.61467 | 0.61467 | 0.65285
17 | Average iKW/TR |  |  | 0.65285 | [23 empty] | 0.65285
18 | COP of chiller |  |  | 5.1136 | 5.18 | 5.18 | 5.18 | 5.18 | 5.1136 | 5.1136 | 5.18 | 5.1136 | 6.2094 | 5.403 | 5.4567 | 4.7765 | 5.0804 | 5.0804 | 5.403 | 6.4265 | 5.2921 | 5.7202 | 6.2094 | 5.7202 | 5.3627 | 5.7202 | 5.7202 | 5.414
19 | EER of Chiller |  |  | 17.4528 | 17.6794 | 17.6794 | 17.6794 | 17.6794 | 17.4528 | 17.4528 | 17.6794 | 17.4528 | 21.1927 | 18.4404 | 18.6238 | 16.302 | 17.3394 | 17.3394 | 18.4404 | 21.9337 | 18.0619 | 19.5229 | 21.1927 | 19.5229 | 18.3027 | 19.5229 | 19.5229 | 18.4779
20 | LMTD of Condenser | ºC |  | 3.972 | 4.004 | 3.8507 | 4.004 | 4.004 | 4.004 | 3.8823 | 3.8507 | 3.6967 | 3.6036 | 3.3535 | 2.9511 | 2.8244 | 3.4955 | 3.9613 | 3.6264 | 3.7872 | 3.819 | 3.972 | 3.819 | 3.8507 | 3.6036 | 3.728 | 3.0834 | 3.6978
21 | LMTD of Evaporator | ºC |  | 4.2454 | 4.405 | 4.5331 | 4.5331 | 4.5331 | 4.375 | 4.2454 | 4.275 | 4.2454 | 3.2583 | 3.4204 | 3.1587 | 3.1981 | 3.1692 | 2.9709 | 3.5552 | 4.0255 | 4.3146 | 4.0844 | 3.9796 | 4.0844 | 3.9507 | 4.0844 | 3.9507 | 3.9415
Performance Sheet Chiller
Date :- 18/02/2019
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [10 empty] | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | [10 empty] | 0.72
2 | Small temperature difference of evaporator | ºC | [10 empty] | 0.2 | 0.1 | 0.1 | 0.2 | 0.3 | [10 empty] | 0.18
3 | Entering Chilled Water Temp. (tchwe) | ºC | [10 empty] | 15.3 | 14.7 | 13.7 | 13.6 | 13.5 | [10 empty] | 14.16
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [10 empty] | 12.6 | 7.2 | 8 | 8 | 6.9 | [10 empty] | 8.54
5 | Entering Condenser Water Temp. (tcwe) | ºC | [10 empty] | 23 | 24.8 | 22.7 | 22.5 | 22.2 | [10 empty] | 23.04
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [10 empty] | 24.6 | 29.6 | 26.6 | 26.1 | 26.1 | [10 empty] | 26.6
7 | Chilled water inlet pressure | (Kg/Cm2) | [10 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [10 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [10 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [10 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [10 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [10 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [10 empty] | 3 | 3 | 3 | 3 | 3 | [10 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [10 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [10 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [10 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [10 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [10 empty] | 971 | 971 | 971 | 971 | 971 | [10 empty] | 971
14 | TR Genrated by Chiller | TR | [10 empty] | 866.9643 | 2408.2341 | 1830.2579 | 1798.1481 | 2119.246 | [10 empty] | 9022.8505
15 | Power Consumption of Chiller | KWH | [10 empty] | 1400 | 1200 | 1200 | 1400 | 1600 | [10 empty] | 6800
16 | Specific power consumption of Chiller | (iKW/TR) | [10 empty] | 1.6148 | 0.49829 | 0.65565 | 0.77858 | 0.75499 | [10 empty] | 0.86047
17 | Average iKW/TR |  |  | 0.86047 | [23 empty] | 0.86047
18 | COP of chiller | [11 empty] | 2.1773 | 7.0561 | 5.3627 | 4.5159 | 7.0561 | [10 empty] | 5.2336
19 | EER of Chiller | [11 empty] | 7.4312 | 24.0826 | 18.3027 | 15.4128 | 24.0826 | [10 empty] | 17.8624
20 | LMTD of Condenser | ºC | [10 empty] | 1.2314 | 2.1846 | 2.2025 | 2.1117 | 2.2025 | [10 empty] | 1.9866
21 | LMTD of Evaporator | ºC | [10 empty] | 1.0097 | 1.7318 | 1.4038 | 1.6631 | 2.1049 | [10 empty] | 1.5827

## 19-02-2019 (hidden)
Performance Sheet Chiller
Date :- 19/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.7 | 1.7 | 1.8 | 1.7 | 1.7 | 1.6 | 1.4 | 1.5 | 1.5 | 1.5 | 1.7 | 1.6 | 1.5 | 1.4 | 1.3 | 1.4 | 1.6 | 1.6 | 1.5 | 1.6 | 1.6 | 1.7 | 1.7 | 1.5875
2 | Small temperature difference of evaporator | ºC |  | 1.8 | 1.8 | 1.7 | 1.8 | 1.7 | 1.4 | 1 | 0.8 | 0.8 | 0.8 | 1.1 | 1.4 | 1.1 | 0.8 | 0.4 | 0.3 | 0.9 | 1.2 | 1.2 | 1 | 1.1 | 1.2 | 1 | 1.1 | 1.1417
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.6 | 13.5 | 13.7 | 13.8 | 13.7 | 13.7 | 12.9 | 12.3 | 12.1 | 12.2 | 12.9 | 14.4 | 15 | 14.9 | 13.7 | 13.1 | 12.4 | 12.2 | 13.1 | 13.3 | 13.6 | 13.7 | 13.8 | 13.8 | 13.3917
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.9 | 5.8 | 6 | 6 | 6.1 | 6.2 | 5.5 | 5.4 | 5.4 | 5.5 | 5.8 | 6.7 | 7.2 | 7.8 | 6.4 | 6.1 | 5.8 | 5.6 | 5.6 | 5.9 | 6.1 | 6.1 | 6.3 | 6.3 | 6.0625
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.6 | 20.2 | 20.2 | 20 | 19.9 | 19.8 | 20.4 | 20.9 | 22.8 | 23.6 | 23.4 | 22.6 | 21.7 | 24.2 | 25 | 25.1 | 24.8 | 22.2 | 21.6 | 22.1 | 22 | 21.9 | 21.9 | 22.1 | 22.0417
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.6 | 26.1 | 26.3 | 26 | 25.8 | 25.8 | 26.1 | 26.3 | 27.9 | 28.7 | 29 | 28.6 | 27.9 | 29.6 | 30.5 | 30.3 | 29.7 | 27.3 | 27.5 | 27.9 | 27.8 | 27.8 | 27.9 | 27.9 | 27.7208
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2472.4537 | 2472.4537 | 2472.4537 | 2504.5635 | 2440.3439 | 2408.2341 | 2376.1243 | 2215.5754 | 2151.3558 | 2151.3558 | 2279.795 | 2472.4537 | 2504.5635 | 2279.795 | 2344.0146 | 2247.6852 | 2119.246 | 2119.246 | 2408.2341 | 2376.1243 | 2408.2341 | 2440.3439 | 2408.2341 | 2408.2341 | 56481.1177
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1450 | 1500 | 1500 | 1450 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 35900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.60668 | 0.60668 | 0.60668 | 0.59891 | 0.61467 | 0.62286 | 0.63128 | 0.67703 | 0.69723 | 0.69723 | 0.65795 | 0.60668 | 0.59891 | 0.63602 | 0.63993 | 0.66735 | 0.68421 | 0.7078 | 0.62286 | 0.63128 | 0.62286 | 0.61467 | 0.62286 | 0.62286 | 0.63731
17 | Average iKW/TR |  |  | 0.63731 | [23 empty] | 0.63731
18 | COP of chiller |  |  | 5.7954 | 5.7954 | 5.7954 | 5.8707 | 5.7202 | 5.6449 | 5.5696 | 5.1933 | 5.0428 | 5.0428 | 5.3438 | 5.7954 | 5.8707 | 5.5281 | 5.4944 | 5.2686 | 5.1388 | 4.9675 | 5.6449 | 5.5696 | 5.6449 | 5.7202 | 5.6449 | 5.6449 | 5.5311
19 | EER of Chiller |  |  | 19.7798 | 19.7798 | 19.7798 | 20.0367 | 19.5229 | 19.266 | 19.0092 | 17.7248 | 17.211 | 17.211 | 18.2385 | 19.7798 | 20.0367 | 18.8674 | 18.7523 | 17.9816 | 17.5387 | 16.9541 | 19.266 | 19.0092 | 19.266 | 19.5229 | 19.266 | 19.266 | 18.8778
20 | LMTD of Condenser | ºC |  | 4.0918 | 3.9398 | 4.004 | 4.0918 | 3.9398 | 3.972 | 3.7553 | 3.4167 | 3.4422 | 3.4422 | 3.6021 | 3.972 | 3.9138 | 3.5385 | 3.4482 | 3.2309 | 3.2578 | 3.5612 | 3.819 | 3.6653 | 3.7872 | 3.819 | 3.972 | 3.9076 | 3.7329
21 | LMTD of Evaporator | ºC |  | 4.6288 | 4.6288 | 4.5027 | 4.6596 | 4.4722 | 4.055 | 3.4771 | 3.0472 | 2.9937 | 2.9937 | 3.5344 | 4.1137 | 3.7307 | 3.1004 | 2.4683 | 2.1931 | 3.1128 | 3.526 | 3.786 | 3.4771 | 3.6471 | 3.8144 | 3.5046 | 3.6471 | 3.6298
Performance Sheet Chiller
Date :- 19/02/2019
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [13 empty] | 0.8 | 0.7 | 0.7 | 0.7 | [8 empty] | 0.725
2 | Small temperature difference of evaporator | ºC | [13 empty] | 0.1 | 0.1 | 0.2 | 0.1 | [8 empty] | 0.125
3 | Entering Chilled Water Temp. (tchwe) | ºC | [13 empty] | 14.9 | 14.9 | 13.7 | 13.1 | [8 empty] | 14.15
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [13 empty] | 9 | 7.8 | 6.1 | 6 | [8 empty] | 7.225
5 | Entering Condenser Water Temp. (tcwe) | ºC | [13 empty] | 24.2 | 24.8 | 25.2 | 24.8 | [8 empty] | 24.75
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [13 empty] | 28.7 | 29.3 | 30 | 29 | [8 empty] | 29.25
7 | Chilled water inlet pressure | (Kg/Cm2) | [13 empty] | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [13 empty] | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [13 empty] | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [13 empty] | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [13 empty] | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [13 empty] | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [13 empty] | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR | [13 empty] | 1894.4775 | 2279.795 | 2440.3439 | 2279.795 | [8 empty] | 8894.4114
15 | Power Consumption of Chiller | KWH | [13 empty] | 1375 | 1375 | 1375 | 1375 | [8 empty] | 5500
16 | Specific power consumption of Chiller | (iKW/TR) | [13 empty] | 0.72579 | 0.60312 | 0.56345 | 0.60312 | [8 empty] | 0.62387
17 | Average iKW/TR |  |  | 0.62387 | [23 empty] | 0.62387
18 | COP of chiller | [14 empty] | 4.8444 | 5.8296 | 6.2402 | 5.8296 | [8 empty] | 5.686
19 | EER of Chiller | [14 empty] | 16.5338 | 19.8966 | 21.2977 | 19.8966 | [8 empty] | 19.4062
20 | LMTD of Condenser | ºC | [13 empty] | 2.3799 | 2.244 | 2.3285 | 2.1584 | [8 empty] | 2.2777
21 | LMTD of Evaporator | ºC | [13 empty] | 1.441 | 1.6602 | 2.0745 | 1.6602 | [8 empty] | 1.709

## 20-02-2019 (hidden)
Performance Sheet Chiller
Date :- 20/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.7 | 1.8 | 1.8 | 1.8 | 1.9 | 1.7 | 1.6 | 1.6 | 1.6 | 1.5 | 1.6 | 1.6 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | [7 empty] | 1.6235
2 | Small temperature difference of evaporator | ºC |  | 1.3 | 1.4 | 1.3 | 1.4 | 1.1 | 0.5 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | [7 empty] | 0.65294
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.8 | 14 | 14.3 | 14.5 | 14.7 | 15.1 | 15 | 14.1 | 13.8 | 13.8 | 13.8 | 13.9 | 14 | 13.8 | 13.8 | 13.7 | 13.5 | [7 empty] | 14.0941
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.3 | 6.6 | 6.8 | 7.1 | 7.5 | 7.8 | 7.2 | 7 | 7.1 | 7 | 7.1 | 7 | 7 | 7 | 6.7 | 6.5 | [7 empty] | 6.9412
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.1 | 21.7 | 21.6 | 22.4 | 22.9 | 24.1 | 27.1 | 26.6 | 26.7 | 26.5 | 26.6 | 26.5 | 26.5 | 26.5 | 26.6 | 26.5 | 26.6 | [7 empty] | 25.1471
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.9 | 27.7 | 27.6 | 28.4 | 28.8 | 29.9 | 32.5 | 31.7 | 31.8 | 31.5 | 31.8 | 31.6 | 31.7 | 31.7 | 31.7 | 31.7 | 31.8 | [7 empty] | 30.5765
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2472.4537 | 2472.4537 | 2472.4537 | 2440.3439 | 2440.3439 | 2311.9048 | 2215.5754 | 2183.4656 | 2151.3558 | 2183.4656 | 2183.4656 | 2247.6852 | 2183.4656 | 2183.4656 | 2247.6852 | 2247.6852 | [7 empty] | 39045.5026
15 | Power Consumption of Chiller | KWH |  | 1400 | 1380 | 1380 | 1400 | 1390 | 1400 | 1390 | 1390 | 1380 | 1380 | 1380 | 1380 | 1400 | 1380 | 1380 | 1390 | 1400 | [7 empty] | 23600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58134 | 0.55815 | 0.55815 | 0.56624 | 0.56959 | 0.57369 | 0.60124 | 0.62738 | 0.63202 | 0.64146 | 0.63202 | 0.63202 | 0.62286 | 0.63202 | 0.63202 | 0.61841 | 0.62286 | [7 empty] | 0.60597
17 | Average iKW/TR |  |  | 0.60597 | [23 empty] | 0.60597
18 | COP of chiller |  |  | 6.0481 | 6.2994 | 6.2994 | 6.2094 | 6.1728 | 6.1287 | 5.848 | 5.6043 | 5.5631 | 5.4813 | 5.5631 | 5.5631 | 5.6449 | 5.5631 | 5.5631 | 5.6855 | 5.6449 | [7 empty] | 5.8166
19 | EER of Chiller |  |  | 20.6422 | 21.4998 | 21.4998 | 21.1927 | 21.0679 | 20.9174 | 19.9591 | 19.1274 | 18.9868 | 18.7076 | 18.9868 | 18.9868 | 19.266 | 18.9868 | 18.9868 | 19.4047 | 19.266 | [7 empty] | 19.852
20 | LMTD of Condenser | ºC |  | 3.9076 | 4.0918 | 4.0918 | 4.0918 | 4.1777 | 3.9076 | 3.6588 | 3.5612 | 3.5612 | 3.4099 | 3.5938 | 3.5612 | 3.4744 | 3.4744 | 3.4422 | 3.4744 | 3.3535 | [7 empty] | 3.6961
21 | LMTD of Evaporator | ºC |  | 3.9218 | 4.1137 | 3.9796 | 4.1137 | 3.675 | 2.7289 | 2.2368 | 2.3759 | 2.3526 | 2.3293 | 2.3526 | 2.1491 | 2.1931 | 2.3526 | 2.3526 | 2.3991 | 2.3991 | [7 empty] | 2.825
Performance Sheet Chiller
Date :- 20/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [6 empty] | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 1 | 1 | 1 | 0.9 | 0.8 | 0.9 | 0.8 | 0.9 | 0.87368
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.3 | 0.3 | 0.4 | 0.3 | 0.2 | 0.3 | 0.2 | 0.2 | 0.3 | 0.27895
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 17.7 | 15.3 | 14.3 | 14.1 | 14 | 14.1 | 14.1 | 14.1 | 14 | 14 | 13.8 | 13.7 | 12.8 | 13.1 | 14 | 14.6 | 14.7 | 14.8 | 15 | 14.3263
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 8.5 | 7.2 | 6.9 | 7 | 7 | 7 | 7 | 7.1 | 7 | 7.1 | 6.5 | 6 | 5.3 | 5.6 | 5.7 | 5.9 | 6.1 | 6.1 | 6.2 | 6.5895
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 23.7 | 27.5 | 26.9 | 27 | 26.7 | 27 | 26.8 | 26.7 | 26.8 | 26.9 | 26.7 | 26.9 | 26.8 | 26 | 25.2 | 25.2 | 24.9 | 24.9 | 24.8 | 26.1789
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 23.2 | 33.1 | 31.9 | 31.8 | 31.5 | 31.7 | 31.6 | 31.6 | 31.6 | 31.6 | 31.7 | 32.2 | 32 | 31.2 | 30.9 | 31.1 | 30.8 | 30.8 | 30.8 | 31.1105
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 2954.1005 | 2600.8929 | 2376.1243 | 2279.795 | 2247.6852 | 2279.795 | 2279.795 | 2247.6852 | 2247.6852 | 2215.5754 | 2344.0146 | 2472.4537 | 2408.2341 | 2408.2341 | 2665.1124 | 2793.5516 | 2761.4418 | 2793.5516 | 2825.6614 | 47201.3889
15 | Power Consumption of Chiller | KWH | [6 empty] | 1620 | 1550 | 1540 | 1550 | 1540 | 1520 | 1520 | 1520 | 1520 | 1510 | 1530 | 1530 | 1520 | 1550 | 1580 | 1640 | 1600 | 1560 | 1600 | 29500
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.54839 | 0.59595 | 0.64811 | 0.67989 | 0.68515 | 0.66673 | 0.66673 | 0.67625 | 0.67625 | 0.68154 | 0.65273 | 0.61882 | 0.63117 | 0.64363 | 0.59285 | 0.58707 | 0.57941 | 0.55843 | 0.56624 | 0.62923
17 | Average iKW/TR |  |  | 0.62923 | [23 empty] | 0.62923
18 | COP of chiller | [7 empty] | 6.4115 | 5.8998 | 5.425 | 5.1715 | 5.1317 | 5.2735 | 5.2735 | 5.1993 | 5.1993 | 5.1589 | 5.3866 | 5.6818 | 5.5706 | 5.4628 | 5.9307 | 5.9891 | 6.0683 | 6.2962 | 6.2094 | 5.6179
19 | EER of Chiller | [7 empty] | 21.8824 | 20.1361 | 18.5154 | 17.6502 | 17.5146 | 17.9985 | 17.9985 | 17.745 | 17.745 | 17.6074 | 18.3846 | 19.392 | 19.0125 | 18.6446 | 20.2415 | 20.4408 | 20.711 | 21.4891 | 21.1927 | 19.1738
20 | LMTD of Condenser | ºC | [6 empty] | 0.61658 | 2.693 | 2.524 | 2.4667 | 2.6005 | 2.5709 | 2.4667 | 2.4954 | 2.4667 | 2.5709 | 2.6591 | 2.8796 | 2.85 | 2.85 | 2.8608 | 2.7761 | 2.9175 | 2.7761 | 2.9457 | 2.5782
21 | LMTD of Evaporator | ºC | [6 empty] | 2.6626 | 2.4308 | 2.2803 | 2.215 | 2.1931 | 2.215 | 2.215 | 2.1931 | 1.9534 | 1.933 | 2.2586 | 2.3451 | 2.5141 | 2.302 | 2.2136 | 2.5579 | 2.2726 | 2.2922 | 2.5789 | 2.2961

## 21-02-2019 (hidden)
Date :- 21/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 1.6 | 1.6 | 1.2 | 1.2 | 1.2 | 1.5 | 1.6 | 1.7 | 1.7 | 1.6 | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | [7 empty] | 1.4733
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.7 | 0.7 | 0.3 | 0.3 | 0.3 | 0.6 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.5 | 0.7 | 0.6 | 0.4 | [7 empty] | 0.62
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 15.3 | 14.9 | 12.7 | 12.6 | 12.5 | 13.6 | 14.2 | 14.6 | 15.2 | 16.1 | 15.2 | 14.6 | 14.2 | 13.7 | 13.3 | [7 empty] | 14.18
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 8.5 | 8 | 7 | 7 | 7.1 | 7.2 | 7.1 | 7.1 | 7.7 | 8.6 | 7.7 | 7.3 | 7 | 6.3 | 6.1 | [7 empty] | 7.3133
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 21.2 | 25 | 24.7 | 25.2 | 25.2 | 25.2 | 25.4 | 25.4 | 25.3 | 26 | 26 | 26.1 | 26.2 | 24.9 | 26 | [7 empty] | 25.1867
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 26.6 | 30.3 | 29 | 29.3 | 29.3 | 30 | 30.8 | 31.2 | 31.1 | 31.8 | 31.6 | 31.7 | 31.6 | 30.5 | 31.4 | [7 empty] | 30.4133
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2183.4656 | 2215.5754 | 1830.2579 | 1798.1481 | 1733.9286 | 2055.0265 | 2279.795 | 2408.2341 | 2408.2341 | 2408.2341 | 2408.2341 | 2344.0146 | 2311.9048 | 2376.1243 | 2311.9048 | [7 empty] | 33073.082
15 | Power Consumption of Chiller | KWH |  |  |  | 1450 | 1410 | 1410 | 1410 | 1450 | 1470 | 1510 | 1500 | 1480 | 1530 | 1480 | 1470 | 1470 | 1490 | 1470 | [7 empty] | 22000
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.66408 | 0.6364 | 0.77038 | 0.78414 | 0.83625 | 0.71532 | 0.66234 | 0.62286 | 0.61456 | 0.63532 | 0.61456 | 0.62713 | 0.63584 | 0.62707 | 0.63584 | [7 empty] | 0.67214
17 | Average iKW/TR |  |  | Hours 7: 0.67214 | 0.67214
18 | COP of chiller |  |  |  |  | 5.2945 | 5.5248 | 4.564 | 4.4839 | 4.2045 | 4.9153 | 5.3084 | 5.6449 | 5.7212 | 5.5342 | 5.7212 | 5.6065 | 5.5297 | 5.607 | 5.5297 | [7 empty] | 5.2793
19 | EER of Chiller |  |  |  |  | 18.0702 | 18.8561 | 15.5768 | 15.3035 | 14.3499 | 16.7759 | 18.1177 | 19.266 | 19.5264 | 18.8883 | 19.5264 | 19.135 | 18.8729 | 19.1367 | 18.8729 | [7 empty] | 18.0183
20 | LMTD of Condenser | ºC |  |  |  | 3.6588 | 3.6264 | 2.8244 | 2.7602 | 2.7602 | 3.3448 | 3.6588 | 3.9076 | 3.9076 | 3.7872 | 3.6021 | 3.6021 | 3.4167 | 3.4795 | 3.4167 | [7 empty] | 3.4502
21 | LMTD of Evaporator | ºC |  |  |  | 2.8673 | 2.8933 | 1.9027 | 1.8799 | 1.834 | 2.6051 | 2.9451 | 3.206 | 3.3578 | 3.3578 | 3.3578 | 2.6572 | 2.9709 | 2.8568 | 2.4453 | [7 empty] | 2.7425
Date :- 21/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | [5 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1.1 | 1 | 1.1 | 1.2 | 1.2 | 1 | 0.96842
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.3 | 0.3 | 0.2 | [5 empty] | 0.5 | 0.5 | 0.5 | 0.4 | 0.5 | 0.5 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.5 | 0.5 | 0.42632
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15 | 15.2 | 15.5 | 15.1 | 12.9 | [5 empty] | 15.3 | 16.3 | 15.5 | 14.8 | 14.5 | 14 | 13.5 | 13 | 12.8 | 13.7 | 14.3 | 14.7 | 14.9 | 15.1 | 14.5316
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.3 | 6.6 | 7.8 | 7 | [5 empty] | 8.6 | 7.8 | 7.2 | 6.9 | 7 | 6.3 | 6 | 5.8 | 5.6 | 5.7 | 5.9 | 6.1 | 6.4 | 6.5 | 6.6211
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.6 | 24 | 24 | 25.3 | 24.9 | [5 empty] | 25.7 | 26.3 | 26.2 | 26.4 | 26.5 | 25.2 | 26.2 | 26.1 | 24.8 | 24.3 | 24.5 | 24.5 | 24.5 | 24.3 | 25.1737
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.7 | 30.1 | 30.2 | 30.1 | 28.8 | [5 empty] | 24.9 | 32.1 | 32 | 31.8 | 31.6 | 30.4 | 31.5 | 31.1 | 29.7 | 30 | 30.4 | 30.3 | 30.5 | 30.3 | 30.3421
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [5 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | [5 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | [5 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2793.5516 | 2857.7712 | 2857.7712 | 2344.0146 | 1894.4775 | [5 empty] | 2151.3558 | 2729.332 | 2665.1124 | 2536.6733 | 2408.2341 | 2472.4537 | 2408.2341 | 2311.9048 | 2311.9048 | 2568.7831 | 2697.2222 | 2761.4418 | 2729.332 | 2761.4418 | 48261.0119
15 | Power Consumption of Chiller | KWH |  | 1480 | 1530 | 1340 | 1310 | 1310 | [5 empty] | 1480 | 1500 | 1400 | 1420 | 1360 | 1400 | 1400 | 1400 | 1430 | 1430 | 1450 | 1500 | 1530 | 1530 | 27200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.52979 | 0.53538 | 0.4689 | 0.55887 | 0.69148 | [5 empty] | 0.68794 | 0.54959 | 0.52531 | 0.55979 | 0.56473 | 0.56624 | 0.58134 | 0.60556 | 0.61854 | 0.55668 | 0.53759 | 0.54319 | 0.56058 | 0.55406 | 0.56819
17 | Average iKW/TR |  |  | Hours 7: 0.56819 | 0.56819
18 | COP of chiller |  |  | 6.6366 | 6.5673 | 7.4985 | 6.2913 | 5.0847 | [5 empty] | 5.1109 | 6.3976 | 6.6932 | 6.2809 | 6.226 | 6.2094 | 6.0481 | 5.8062 | 5.6844 | 6.316 | 6.5403 | 6.4728 | 6.2721 | 6.3459 | 6.2359
19 | EER of Chiller |  |  | 22.6506 | 22.4141 | 25.5922 | 21.4721 | 17.3541 | [5 empty] | 17.4436 | 21.8349 | 22.844 | 21.4369 | 21.2493 | 21.1927 | 20.6422 | 19.8165 | 19.4008 | 21.5564 | 22.322 | 22.0917 | 21.4067 | 21.6586 | 21.2831
20 | LMTD of Condenser | ºC |  | 2.9738 | 2.9738 | 3.0018 | 2.6005 | 2.3298 | [5 empty] | 0.3641 | 2.8892 | 2.8892 | 2.7751 | 2.6883 | 2.7173 | 2.7462 | 2.7906 | 2.8884 | 2.9967 | 3.1882 | 3.2887 | 3.3487 | 3.0834 | 2.7649
21 | LMTD of Evaporator | ºC |  | 2.7844 | 2.8287 | 2.5999 | 2.2586 | 1.7263 | [5 empty] | 2.512 | 2.9408 | 2.8941 | 2.6051 | 2.7051 | 2.7527 | 2.302 | 2.4453 | 2.6332 | 2.8236 | 2.7175 | 2.9641 | 2.9408 | 2.9641 | 2.6525

## 22-02-2019 (hidden)
Date :- 22/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 1.9 | 1.8 | 1.8 | 1.8 | 1.8 | 1.7 | 1.6 | 1 | 1 | 1.7 | 1.6 | 1.7 | 1.8 | 1.7 | 1.7 | 1.7 | 1.8 | 2 | 1.9 | 1.8 | 2.1 | 2 | 1.9 | 2.2
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.5 | 0.3 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.38636
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 15.1 | 15.2 | 14 | 13.6 | 13.4 | 13.6 | 14 | 14.1 | 14.4 | 14.4 | 14.2 | 14.1 | 14 | 13.9 | 13.5 | 12.5 | 12.7 | 14 | 14.5 | 14.7 | 15.1 | 15.2 | 14.1
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 10.6 | 7.6 | 7 | 6.9 | 7 | 7.1 | 7.1 | 7.2 | 7.3 | 7.3 | 7.2 | 7.1 | 7.1 | 6.8 | 6.2 | 5.6 | 5.6 | 6.2 | 6.5 | 6.7 | 6.8 | 7.1 | 7
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 20.2 | 25.6 | 25.5 | 25.7 | 26 | 27.1 | 27.5 | 27.1 | 26.8 | 26.3 | 26 | 25.5 | 25.7 | 26.2 | 25.7 | 25.3 | 24.2 | 23.6 | 23.7 | 23.6 | 23.5 | 23.3 | 25.1864
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 25.3 | 30.4 | 30 | 30 | 30.1 | 31.3 | 31.8 | 31.6 | 31.4 | 31 | 30.5 | 30 | 30.1 | 30.7 | 30.3 | 29.7 | 28.8 | 28.5 | 28.8 | 28.7 | 28.7 | 28.7 | 29.8364
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 1444.9405 | 2440.3439 | 2247.6852 | 2151.3558 | 2055.0265 | 2087.1362 | 2215.5754 | 2215.5754 | 2279.795 | 2279.795 | 2247.6852 | 2247.6852 | 2215.5754 | 2279.795 | 2344.0146 | 2215.5754 | 2279.795 | 2504.5635 | 2568.7831 | 2568.7831 | 2665.1124 | 2600.8929 | 50155.4894
15 | Power Consumption of Chiller | KWH |  |  |  | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1500 | 1500 | 1500 | 1500 | 33600
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 1.0381 | 0.61467 | 0.66735 | 0.69723 | 0.72992 | 0.71869 | 0.67703 | 0.67703 | 0.65795 | 0.65795 | 0.66735 | 0.66735 | 0.72216 | 0.70182 | 0.68259 | 0.72216 | 0.70182 | 0.63883 | 0.58393 | 0.58393 | 0.56283 | 0.57673 | 0.67943
17 | Average iKW/TR |  |  | Hours 7: 0.67943 | 0.67943
18 | COP of chiller |  |  |  |  | 3.3869 | 5.7202 | 5.2686 | 5.0428 | 4.817 | 4.8922 | 5.1933 | 5.1933 | 5.3438 | 5.3438 | 5.2686 | 5.2686 | 4.8687 | 5.0098 | 5.151 | 4.8687 | 5.0098 | 5.5038 | 6.0212 | 6.0212 | 6.247 | 6.0965 | 5.2517
19 | EER of Chiller |  |  |  |  | 11.5596 | 19.5229 | 17.9816 | 17.211 | 16.4404 | 16.6972 | 17.7248 | 17.7248 | 18.2385 | 18.2385 | 17.9816 | 17.9816 | 16.617 | 17.0986 | 17.5803 | 16.617 | 17.0986 | 18.7844 | 20.5504 | 20.5504 | 21.3211 | 20.8073 | 17.924
20 | LMTD of Condenser | ºC |  |  |  | 3.9109 | 3.6943 | 3.5921 | 3.5231 | 3.4536 | 3.3753 | 3.2951 | 2.6397 | 2.6701 | 3.5454 | 3.3625 | 3.4778 | 3.5577 | 3.4778 | 3.5117 | 3.4438 | 3.6263 | 3.9568 | 3.9109 | 3.7954 | 4.1736 | 4.1274 | 3.551
21 | LMTD of Evaporator | ºC |  |  |  | 1.796 | 2.5369 | 2.3991 | 2.1271 | 2.0605 | 2.0827 | 2.3759 | 2.5607 | 2.6091 | 2.6091 | 2.1931 | 2.3991 | 2.1711 | 2.4222 | 2.4683 | 2.3759 | 2.4222 | 2.5824 | 2.4095 | 2.6277 | 2.6951 | 2.6502 | 2.3897
Date :- 22/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.1 | 1 | 0.9 | 0.9 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 0.9 | 0.8 | 1 | 0.9 | [7 empty] | 0.93529
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | [7 empty] | 0.40588
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.2 | 15.2 | 15.6 | 15.2 | 14 | 13.6 | 13.5 | 13.6 | 14 | 14.1 | 14.4 | 14.4 | 14.3 | 14.2 | 14 | 14 | 13.5 | [7 empty] | 14.2824
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.5 | 6.7 | 6.9 | 7.1 | 6.8 | 7 | 6.8 | 7 | 7 | 7.1 | 7 | 7.1 | 7 | 7 | 7 | 6.1 | 5.7 | [7 empty] | 6.8118
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.2 | 24.3 | 24.2 | 25.7 | 25.6 | 25.8 | 26 | 27.1 | 27.5 | 27.2 | 26.8 | 26.5 | 26 | 25.5 | 25.7 | 26.2 | 25.7 | [7 empty] | 25.8824
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.2 | 30.3 | 30.2 | 31.5 | 30.6 | 30.3 | 30.5 | 31.7 | 32.3 | 32 | 32 | 31.6 | 31.2 | 30.5 | 30.6 | 31.8 | 31.2 | [7 empty] | 31.0882
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2793.5516 | 2729.332 | 2793.5516 | 2600.8929 | 2311.9048 | 2119.246 | 2151.3558 | 2119.246 | 2247.6852 | 2247.6852 | 2376.1243 | 2344.0146 | 2344.0146 | 2311.9048 | 2247.6852 | 2536.6733 | 2504.5635 | [7 empty] | 40779.4312
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1300 | 1300 | 1200 | 1200 | 1200 | 1200 | 1200 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | [7 empty] | 21600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.46536 | 0.47631 | 0.46536 | 0.49983 | 0.51905 | 0.56624 | 0.55779 | 0.56624 | 0.53388 | 0.57837 | 0.54711 | 0.5546 | 0.5546 | 0.56231 | 0.57837 | 0.51248 | 0.51905 | [7 empty] | 0.53276
17 | Average iKW/TR |  |  | Hours 7: 0.53276 | 0.53276
18 | COP of chiller |  |  | 7.5555 | 7.3818 | 7.5555 | 7.0344 | 6.7739 | 6.2094 | 6.3035 | 6.2094 | 6.5857 | 6.0791 | 6.4265 | 6.3397 | 6.3397 | 6.2528 | 6.0791 | 6.8607 | 6.7739 | [7 empty] | 6.633
19 | EER of Chiller |  |  | 25.7869 | 25.1941 | 25.7869 | 24.0085 | 23.1193 | 21.1927 | 21.5138 | 21.1927 | 22.4771 | 20.748 | 21.9337 | 21.6373 | 21.6373 | 21.3409 | 20.748 | 23.4157 | 23.1193 | [7 empty] | 22.6383
20 | LMTD of Condenser | ºC |  | 3.2175 | 3.0834 | 2.9457 | 2.8892 | 2.7906 | 2.5115 | 2.5115 | 2.5413 | 2.6005 | 2.6005 | 2.7173 | 2.8203 | 2.85 | 2.6591 | 2.4954 | 2.9676 | 2.8037 | [7 empty] | 2.765
21 | LMTD of Evaporator | ºC |  | 3.1742 | 3.126 | 2.9873 | 2.6502 | 2.2368 | 2.1049 | 2.1271 | 2.3059 | 2.3991 | 2.3991 | 2.2803 | 2.4683 | 2.4683 | 2.4453 | 2.3991 | 2.6051 | 2.5824 | [7 empty] | 2.5153

## 23-02-2019 (hidden)
Date :- 23/01/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.1; Hours 8: 1.1; Hours 9: 1.9; Hours 10: 1.7; Hours 16: 1.9; Hours 17: 1.9; Hours 18: 1.8; Hours 19: 1.7; Hours 20: 1.9; Hours 21: 1.9; Hours 22: 1.7; Hours 23: 1.8 | 1.7
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.4; Hours 10: 0.3; Hours 16: 0.4; Hours 17: 0.4; Hours 18: 0.4; Hours 19: 0.5; Hours 20: 0.3; Hours 21: 0.4; Hours 22: 0.4; Hours 23: 0.4 | 0.40833
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 15.3; Hours 8: 15.5; Hours 9: 16; Hours 10: 15.6; Hours 16: 15.7222; Hours 17: 15.7222; Hours 18: 15.7222; Hours 19: 15.4444; Hours 20: 15; Hours 21: 14.5; Hours 22: 14.1667; Hours 23: 13.7222 | 15.2
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 7; Hours 8: 7.1; Hours 9: 7.6; Hours 10: 8; Hours 16: 7.8889; Hours 17: 7.8889; Hours 18: 7.8889; Hours 19: 7.7222; Hours 20: 7.5; Hours 21: 7; Hours 22: 6.6667; Hours 23: 6.4444 | 7.3917
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 23.6; Hours 8: 23.1; Hours 9: 23.3; Hours 10: 26.2; Hours 16: 25.6667; Hours 17: 25.6667; Hours 18: 25.6667; Hours 19: 26.1111; Hours 20: 26; Hours 21: 24.9444; Hours 22: 24.8333; Hours 23: 24.7778 | 24.9889
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 28.8; Hours 8: 28.4; Hours 9: 28.7; Hours 10: 31.1; Hours 16: 30.6111; Hours 17: 30.6111; Hours 18: 30.6111; Hours 19: 31; Hours 20: 30.7778; Hours 21: 29.8889; Hours 22: 29.5; Hours 23: 29.4444 | 29.9537
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 8: 4.3; Hours 9: 4.3; Hours 10: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 10: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 10: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2665.1124; Hours 8: 2697.2222; Hours 9: 2697.2222; Hours 10: 2440.3439; Hours 16: 2515.266; Hours 17: 2515.266; Hours 18: 2515.266; Hours 19: 2479.5875; Hours 20: 2408.2341; Hours 21: 2408.2341; Hours 22: 2408.2351; Hours 23: 2336.8785 | 30086.8682
15 | Power Consumption of Chiller | KWH |  | 1600 | 1500 | 1400 | 1200 |  | 0 | 0 | 0 | 0 | 1100 | 1400 | 1600 | 1500 | 1500 | 1400 | 1500 | 800 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16500
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.60035; Hours 8: 0.55613; Hours 9: 0.51905; Hours 10: 0.49173; Hours 16: 0.43733; Hours 17: 0.5566; Hours 18: 0.63612; Hours 19: 0.60494; Hours 20: 0.62286; Hours 21: 0.58134; Hours 22: 0.62286; Hours 23: 0.34234 | 0.54764
17 | Average iKW/TR |  |  | Hours 7: 0.54764 | 0.54764
18 | COP of chiller |  |  | Hours 7: 5.8566; Hours 8: 6.3223; Hours 9: 6.7739; Hours 10: 7.1502; Hours 16: 8.0397; Hours 17: 6.3169; Hours 18: 5.5273; Hours 19: 5.8122; Hours 20: 5.6449; Hours 21: 6.0481; Hours 22: 5.6449; Hours 23: 10.2706 | 6.6173
19 | EER of Chiller |  |  | Hours 7: 19.9885; Hours 8: 21.578; Hours 9: 23.1193; Hours 10: 24.4037; Hours 16: 27.4395; Hours 17: 21.5596; Hours 18: 18.8647; Hours 19: 19.8369; Hours 20: 19.266; Hours 21: 20.6422; Hours 22: 19.2661; Hours 23: 35.0535 | 22.5848
20 | LMTD of Condenser | ºC |  | Hours 7: 2.9795; Hours 8: 3.0097; Hours 9: 4.0118; Hours 10: 3.6124; Hours 16: 3.8581; Hours 17: 3.8581; Hours 18: 3.7431; Hours 19: 3.6087; Hours 20: 3.8011; Hours 21: 3.8581; Hours 22: 3.5342; Hours 23: 3.649 | 3.627
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.8941; Hours 8: 2.9175; Hours 9: 2.7175; Hours 10: 2.3236; Hours 16: 2.59; Hours 17: 2.59; Hours 18: 2.59; Hours 19: 2.7579; Hours 20: 2.302; Hours 21: 2.5141; Hours 22: 2.5141; Hours 23: 2.4632 | 2.5978
Date :- 23/01/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  | 1.9 | 1.9 | 1.8 | 1.4 | 1.8 | 1.8 | 1.7 | 1.7 | 1.9 | 1.8 | 1.7 | 1.7 | 1.8 | 1.7 | 1.8 | 1.7 | 1.9 | 1.9 | 1.8 | 1.7 | 1.8 | 2 | 2.1 | 1.7957
2 | Small temperature difference of evaporator | ºC |  |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.3 | 0.4 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.4 | 0.39565
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  | 15.6 | 15.6 | 15.6 | 14.5 | 13 | 12.3 | 12.8 | 13.5 | 14 | 14.3 | 15.5 | 15.5 | 14.9 | 14.4 | 14.1 | 13.7 | 12.5 | 12.2 | 12.3 | 13.6 | 13.8 | 14.1 | 14.1 | 13.9957
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  | 7.6 | 7.6 | 7.6 | 7 | 7 | 5.5 | 5.6 | 5.8 | 6.2 | 6.3 | 7.9 | 7.7 | 7.3 | 7.1 | 6.6 | 6.5 | 5.4 | 5.3 | 5.3 | 5.6 | 5.5 | 5.5 | 5.6 | 6.413
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  | 26 | 26 | 26 | 25.1 | 24.7 | 23.3 | 23.7 | 25 | 24.9 | 24.5 | 25.2 | 25.9 | 26 | 24.8 | 24.6 | 24.5 | 23.5 | 23.5 | 21.9 | 21 | 20.6 | 20.2 | 20 | 23.9522
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  | 31.6 | 31.6 | 31.6 | 30.2 | 29 | 28.2 | 28.6 | 30.3 | 30.4 | 30 | 30.8 | 31.5 | 31.1 | 30.1 | 30 | 29.8 | 28.5 | 28.3 | 26.7 | 26.2 | 26 | 26 | 25.6 | 29.2217
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  | 2568.7831 | 2568.7831 | 2568.7831 | 2408.2341 | 1926.5873 | 2183.4656 | 2311.9048 | 2472.4537 | 2504.5635 | 2568.7831 | 2440.3439 | 2504.5635 | 2440.3439 | 2344.0146 | 2408.2341 | 2311.9048 | 2279.795 | 2215.5754 | 2247.6852 | 2568.7831 | 2665.1124 | 2761.4418 | 2729.332 | 55999.4709
15 | Power Consumption of Chiller | KWH |  |  | 1500 | 1500 | 1300 | 1200 | 1500 | 1400 | 1500 | 1600 | 1500 | 1300 | 1600 | 1400 | 1400 | 1400 | 1400 | 1300 | 1200 | 1400 | 1500 | 1500 | 1300 | 1500 | 1500 | 32700
16 | Specific power consumption of Chiller | (iKW/TR) |  |  | 0.58393 | 0.58393 | 0.50608 | 0.49829 | 0.77858 | 0.64118 | 0.64882 | 0.64713 | 0.59891 | 0.50608 | 0.65565 | 0.55898 | 0.57369 | 0.59727 | 0.58134 | 0.56231 | 0.52636 | 0.63189 | 0.66735 | 0.58393 | 0.48778 | 0.54319 | 0.54959 | 0.58749
17 | Average iKW/TR |  |  | Hours 7: 0.58749 | 0.58749
18 | COP of chiller |  |  |  | 6.0212 | 6.0212 | 6.9476 | 7.0561 | 4.5159 | 5.4836 | 5.4191 | 5.4332 | 5.8707 | 6.9476 | 5.3627 | 6.29 | 6.1287 | 5.8868 | 6.0481 | 6.2528 | 6.6798 | 5.5643 | 5.2686 | 6.0212 | 7.2081 | 6.4728 | 6.3976 | 6.0564
19 | EER of Chiller |  |  |  | 20.5504 | 20.5504 | 23.7121 | 24.0826 | 15.4128 | 18.7156 | 18.4954 | 18.5436 | 20.0367 | 23.7121 | 18.3027 | 21.4679 | 20.9174 | 20.0917 | 20.6422 | 21.3409 | 22.7982 | 18.9908 | 17.9816 | 20.5504 | 24.6013 | 22.0917 | 21.8349 | 20.6706
20 | LMTD of Condenser | ºC |  |  | 4.0785 | 4.0785 | 3.9613 | 3.3218 | 3.5231 | 3.7282 | 3.6124 | 3.7448 | 4.0452 | 3.9283 | 3.8429 | 3.8429 | 3.7954 | 3.7448 | 3.8953 | 3.7448 | 3.877 | 3.8088 | 3.6943 | 3.7119 | 3.8953 | 4.2616 | 4.3101 | 3.8455
21 | LMTD of Evaporator | ºC |  |  | 2.6277 | 2.6277 | 2.6277 | 2.302 | 2.164 | 2.3526 | 2.4453 | 2.5597 | 2.5824 | 2.6277 | 2.5369 | 2.5824 | 2.7289 | 2.2586 | 2.5141 | 2.4453 | 2.6091 | 2.1711 | 2.3991 | 2.8236 | 2.4734 | 2.7622 | 2.7399 | 2.5201

## 24-02-2019 (hidden)
Date :- 24/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [6 empty] | 1.1 | 0.9 | 0.9 | 1 | 1 | 0.9 | 0.9 | 0.9 | 1.1 | 1.8 | 0.9 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1 | 1.1 | 1.1 | 1.0526
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.7 | 0.6 | 0.6 | 0.6 | 0.4 | 0.5 | 0.6 | 0.4 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.7 | 0.8 | 0.8 | 0.64737
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 15.8 | 15.7778 | 14.6667 | 14.4444 | 14.3889 | 14.2778 | 14.2778 | 14.1667 | 14.2778 | 13.9444 | 13.5556 | 12.5556 | 12.4444 | 13.3333 | 13.6111 | 13.8889 | 14 | 14.1111 | 14.1111 | 14.086
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 9 | 8.2778 | 8 | 8 | 8.1111 | 8.1111 | 8 | 8.1111 | 8.1111 | 6.1111 | 5.8889 | 5.7222 | 5.6111 | 5.6111 | 5.6111 | 5.6111 | 5.6111 | 5.6111 | 5.6111 | 6.8801
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 22.9444 | 24.3889 | 23.9444 | 24.5556 | 23.4444 | 23.1111 | 22.8889 | 22.8333 | 23.6111 | 22.9444 | 22.6111 | 22.1667 | 20.9444 | 19.9444 | 19.9444 | 20.5 | 21.4444 | 22.4444 | 21.3333 | 22.4211
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 25.8889 | 29.4444 | 28.5 | 28.9444 | 27.6111 | 27.2778 | 27.0556 | 27 | 27.7778 | 28.2778 | 28 | 27 | 25.6111 | 25.2778 | 25.5 | 26.2778 | 27.2778 | 28.3333 | 27.2222 | 27.2778
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 2183.4656 | 2408.2344 | 2140.6533 | 2069.2957 | 2015.7816 | 1980.1044 | 2015.7816 | 1944.4272 | 1980.1044 | 2515.2654 | 2461.7522 | 2194.1704 | 2194.171 | 2479.5885 | 2568.7831 | 2657.9776 | 2693.6548 | 2729.332 | 2729.332 | 43961.875
15 | Power Consumption of Chiller | KWH | [6 empty] | 1310 | 1310 | 1300 | 1300 | 1280 | 1280 | 1280 | 1290 | 1320 | 1370 | 1310 | 1310 | 1320 | 1320 | 1370 | 1360 | 1390 | 1390 | 1390 | 25200
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.59996 | 0.54397 | 0.60729 | 0.62823 | 0.63499 | 0.64643 | 0.63499 | 0.66343 | 0.66663 | 0.54467 | 0.53214 | 0.59704 | 0.60159 | 0.53235 | 0.53333 | 0.51167 | 0.51603 | 0.50928 | 0.50928 | 0.57965
17 | Average iKW/TR |  |  | Hours 7: 0.57965 | 0.57965
18 | COP of chiller | [7 empty] | 5.8604 | 6.4636 | 5.7896 | 5.5966 | 5.5371 | 5.4391 | 5.5371 | 5.2997 | 5.2743 | 6.4552 | 6.6073 | 5.8891 | 5.8445 | 6.6047 | 6.5926 | 6.8717 | 6.8136 | 6.9038 | 6.9038 | 6.1202
19 | EER of Chiller | [7 empty] | 20.0014 | 22.0604 | 19.7601 | 19.1014 | 18.8981 | 18.5636 | 18.8981 | 18.0879 | 18.0011 | 22.0317 | 22.5506 | 20.0995 | 19.9472 | 22.5419 | 22.5005 | 23.453 | 23.2548 | 23.5628 | 23.5628 | 20.8882
20 | LMTD of Condenser | ºC | [6 empty] | 2.2614 | 2.6753 | 2.5281 | 2.6057 | 2.5372 | 2.4112 | 2.4112 | 2.4112 | 2.6606 | 3.8732 | 2.7719 | 2.868 | 2.8167 | 3.0197 | 3.0862 | 3.0192 | 3.0353 | 3.1849 | 3.1849 | 2.8085
21 | LMTD of Evaporator | ºC | [6 empty] | 2.8673 | 2.8816 | 2.673 | 2.6164 | 2.2301 | 2.3807 | 2.5738 | 2.1773 | 2.7007 | 2.9638 | 2.9228 | 2.876 | 2.876 | 3.1043 | 3.3363 | 3.4079 | 3.2721 | 3.4649 | 3.4649 | 2.8837
Date :- 25/12/2018
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.3 | 2.2 | 2.2 | 2.1 | 2 | 1.9 | 1.8 | 1.4 | 1.8 | 1.8 | 1.4 | 1.5 | 1.6 | 1.8 | 1.8 | 1.7 | [8 empty] | 1.8313
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.1 | 0.2 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.2 | [8 empty] | 0.33125
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.1 | 14.1 | 14.2 | 14.6 | 14.7 | 15.2 | 15.6 | 14.6 | 14.1 | 14.2 | 14.1 | 14.2 | 14.2 | 14.1 | 14.2 | 13.3 | [8 empty] | 14.3437
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.6 | 5.6 | 5.8 | 6.1 | 6.3 | 8 | 8 | 8 | 7.8 | 8 | 8 | 8 | 8.2 | 7.1 | 6 | [8 empty] | 7.0062
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.6 | 21.5 | 20.9 | 20.8 | 21.2 | 21.6 | 23.8 | 23.7 | 24.2 | 23.3 | 22.9 | 22.7 | 22.7 | 23.4 | 23.1 | 22.2 | [8 empty] | 22.4125
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.7 | 27.1 | 26.7 | 26.7 | 27.2 | 27.5 | 29.2 | 28.3 | 28.7 | 27.6 | 27.1 | 26.9 | 26.8 | 27.3 | 28.1 | 27.6 | [8 empty] | 27.4688
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2729.332 | 2729.332 | 2761.4418 | 2825.6614 | 2761.4418 | 2857.7712 | 2440.3439 | 2119.246 | 1958.6971 | 2055.0265 | 1958.6971 | 1990.8069 | 1990.8069 | 1894.4775 | 2279.795 | 2344.0146 | [8 empty] | 37696.8915
15 | Power Consumption of Chiller | KWH |  | 1250 | 1290 | 1300 | 1270 | 1300 | 1210 | 1200 | 1180 | 1140 | 1140 | 1140 | 1140 | 1140 | 1200 | 1230 | 1170 | [8 empty] | 19300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.45799 | 0.47264 | 0.47077 | 0.44945 | 0.47077 | 0.42341 | 0.49173 | 0.5568 | 0.58202 | 0.55474 | 0.58202 | 0.57263 | 0.57263 | 0.63342 | 0.53952 | 0.49914 | [8 empty] | 0.52061
17 | Average iKW/TR |  |  | Hours 7: 0.52061 | 0.52061
18 | COP of chiller |  |  | 7.6771 | 7.439 | 7.4686 | 7.8229 | 7.4686 | 8.3041 | 7.1502 | 6.3146 | 6.041 | 6.3381 | 6.041 | 6.1401 | 6.1401 | 5.5508 | 6.5169 | 7.0441 | [8 empty] | 6.8411
19 | EER of Chiller |  |  | 26.2018 | 25.3894 | 25.4905 | 26.6994 | 25.4905 | 28.3418 | 24.4037 | 21.5518 | 20.618 | 21.6321 | 20.618 | 20.9561 | 20.9561 | 18.9449 | 22.2421 | 24.0414 | [8 empty] | 23.3486
20 | LMTD of Condenser | ºC |  | 4.7093 | 4.4245 | 4.4927 | 4.4112 | 4.3281 | 4.1777 | 3.8953 | 3.1609 | 3.5921 | 3.5231 | 3.0297 | 3.1461 | 3.2272 | 3.3834 | 3.7618 | 3.7776 | [8 empty] | 3.815
21 | LMTD of Evaporator | ºC |  | 2.7399 | 2.7399 | 2.9641 | 3.0104 | 2.7622 | 2.8287 | 2.3236 | 1.5697 | 1.7681 | 2.0605 | 1.9933 | 2.0158 | 2.2116 | 1.9481 | 2.215 | 2.0142 | [8 empty] | 2.3228

## 25-02-2019 (hidden)
Date :- 25/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [9 empty] | 1.7 | 1.6 | 1.4 | 1.4 | 1.6 | 1.7 | 1.5 | 1.5 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.8 | 1.9 | 1.8 | 1.7125
2 | Small temperature difference of evaporator | ºC | [9 empty] | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.41875
3 | Entering Chilled Water Temp. (tchwe) | ºC | [9 empty] | 13.2222 | 15.7222 | 15 | 14.7222 | 14.3889 | 14.1667 | 13.7778 | 13.2222 | 12.5556 | 11.9444 | 13.0556 | 13.5556 | 14 | 14.2778 | 14.5556 | 14.7222 | 13.9306
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [9 empty] | 9 | 8.5556 | 7.9444 | 7.9444 | 8.1667 | 7.3889 | 7 | 6.1111 | 5.7222 | 5.5 | 5.5 | 5.7222 | 5.9444 | 6.1667 | 6.3333 | 6.5 | 6.8438
5 | Entering Condenser Water Temp. (tcwe) | ºC | [9 empty] | 19.7778 | 23.9444 | 25.3889 | 24.2222 | 24.1111 | 22.9444 | 23.1111 | 24.5556 | 25.2222 | 23.2778 | 21.8889 | 23.0556 | 23.4444 | 23.8333 | 24.5 | 24.1667 | 23.5903
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [9 empty] | 25.5556 | 28.5556 | 29.7778 | 28.4444 | 28.0556 | 27.1667 | 27.3889 | 29.0556 | 29.5556 | 27.4444 | 26.6667 | 28.1667 | 28.6667 | 29.0556 | 29.7222 | 29.5 | 28.2986
7 | Chilled water inlet pressure | (Kg/Cm2) | [9 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [9 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [9 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [9 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [9 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [9 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [9 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [9 empty] | 1355.7459 | 2301.2006 | 2265.5241 | 2176.3295 | 1997.9426 | 2176.3311 | 2176.3308 | 2283.362 | 2194.1704 | 2069.2957 | 2426.074 | 2515.2683 | 2586.6217 | 2604.4615 | 2640.1394 | 2640.1374 | 36408.9352
15 | Power Consumption of Chiller | KWH | [9 empty] | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 23600
16 | Specific power consumption of Chiller | (iKW/TR) | [9 empty] | 1.088 | 0.64097 | 0.65106 | 0.67775 | 0.73826 | 0.67775 | 0.67775 | 0.64598 | 0.67224 | 0.7128 | 0.60798 | 0.58642 | 0.57024 | 0.56634 | 0.55868 | 0.55868 | 0.66443
17 | Average iKW/TR |  |  | Hours 7: 0.66443 | 0.66443
18 | COP of chiller |  |  | Hours 15: 3.2317; Hours 16: 5.4854; Hours 17: 5.4004; Hours 18: 5.1878; Hours 19: 4.7626; Hours 20: 5.1878 | 4.8759
19 | EER of Chiller |  |  | Hours 15: 11.0299; Hours 16: 18.7218; Hours 17: 18.4315; Hours 18: 17.7059; Hours 19: 16.2546; Hours 20: 17.7059 | 16.6416
20 | LMTD of Condenser | ºC |  | Hours 15: 3.9005; Hours 16: 3.3997; Hours 17: 3.0919; Hours 18: 3.037; Hours 19: 3.1739; Hours 20: 3.383 | 3.331
21 | LMTD of Evaporator | ºC |  | Hours 15: 1.7254; Hours 16: 2.4376; Hours 17: 2.2053; Hours 18: 2.3475; Hours 19: 2.2169; Hours 20: 2.5309 | 2.2439
Date :- 25/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.2 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.9 | 0.9 | 0.9 | 0.9 | 1.1 | 1.1 | 0.9 | [8 empty] | 1.0875
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.4 | 0.4 | 0.6 | 0.4 | 0.3 | [8 empty] | 0.64375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14 | 13.8889 | 14.1111 | 14.2222 | 14.2222 | 14.5556 | 14.7778 | 15.1111 | 15.4444 | 15.7778 | 15 | 14.8333 | 14.3889 | 14.2778 | 13.8333 | 13.2778 | [8 empty] | 14.4826
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.5 | 5.6111 | 5.5556 | 5.5556 | 5.6667 | 5.7778 | 6.2222 | 6.5556 | 7.7222 | 8.0556 | 7.8889 | 7.8889 | 8.2222 | 7.0556 | 5.9444 | [8 empty] | 6.5451
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.7778 | 19.7778 | 19.4444 | 20.7222 | 20.8333 | 20.3889 | 20.5 | 22.4444 | 23.2778 | 24.1111 | 25.3889 | 24.2222 | 24.2222 | 23.3333 | 23.2222 | 24.8333 | [8 empty] | 22.3438
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.7778 | 25.5556 | 25.4444 | 26.6667 | 26.7778 | 26.5556 | 26.7778 | 28.6667 | 29.5 | 29.7222 | 30.3333 | 29 | 28.6667 | 27.4444 | 27.8333 | 30 | [8 empty] | 27.8576
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2729.3317 | 2693.6545 | 2729.332 | 2782.8475 | 2782.8475 | 2854.2047 | 2889.8813 | 2854.2028 | 2854.2022 | 2586.6223 | 2229.8466 | 2229.8453 | 2087.1366 | 1944.4269 | 2176.3289 | 2354.7183 | [8 empty] | 40779.429
15 | Power Consumption of Chiller | KWH |  | 1240 | 1280 | 1240 | 1240 | 1240 | 1320 | 1250 | 1330 | 1240 | 1150 | 1150 | 1050 | 1050 | 1100 | 1210 | 1210 | [8 empty] | 19300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.45432 | 0.47519 | 0.45432 | 0.44559 | 0.44559 | 0.46248 | 0.43254 | 0.46598 | 0.43445 | 0.4446 | 0.51573 | 0.47088 | 0.50308 | 0.56572 | 0.55598 | 0.51386 | [8 empty] | 0.47752
17 | Average iKW/TR |  |  | Hours 7: 0.47752 | 0.47752
18 | COP of chiller |  |  | 7.739 | 7.3991 | 7.739 | 7.8907 | 7.8907 | 7.6026 | 8.1287 | 7.5454 | 8.093 | 7.9083 | 6.8175 | 7.4668 | 6.9889 | 6.2151 | 6.3239 | 6.8423 | [8 empty] | 7.4119
19 | EER of Chiller |  |  | 26.4131 | 25.2532 | 26.4131 | 26.931 | 26.931 | 25.9475 | 27.7431 | 25.7524 | 27.6216 | 26.9911 | 23.2682 | 25.4842 | 23.8532 | 21.2121 | 21.5836 | 23.3528 | [8 empty] | 25.297
20 | LMTD of Condenser | ºC |  | 3.3487 | 3.2821 | 3.2175 | 3.3321 | 3.3321 | 3.3983 | 3.4312 | 3.4148 | 3.4148 | 2.8355 | 2.6429 | 2.5939 | 2.4949 | 2.643 | 2.7995 | 2.7077 | [8 empty] | 3.0555
21 | LMTD of Evaporator | ºC |  | 3.6231 | 3.5939 | 3.4649 | 3.5075 | 3.5075 | 3.3962 | 3.4236 | 3.3962 | 3.3962 | 3.0182 | 2.7431 | 2.3862 | 2.2825 | 2.5166 | 2.3475 | 2.2658 | [8 empty] | 3.0543

## 26-02-2019 (hidden)
Performance Sheet Chiller
Date :- 26/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.8 | 2 | 1.6 | 1.7 | [8 empty] | 1.7 | 1.7 | 1.6 | 1.6 | 1.4 | [7 empty] | 1.6778
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.6 | 0.4 | 0.4 | [8 empty] | 0.4 | 0.3 | 0.6 | 0.6 | 0.6 | [7 empty] | 0.48889
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.8889 | 14.8889 | 15.5 | 15.0556 | [8 empty] | 13.6111 | 15.5556 | 14.4444 | 13.9444 | 13.2222 | [7 empty] | 14.5679
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.4444 | 6.5556 | 7 | 7.8889 | [8 empty] | 8.5 | 8 | 6.3889 | 6.2778 | 5.7778 | [7 empty] | 6.9815
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.0556 | 24 | 24.1111 | 25.3333 | [8 empty] | 18.0556 | 24.6667 | 25.1667 | 25.2222 | 25.2778 | [7 empty] | 23.9877
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.3889 | 29.5556 | 29.6111 | 29.7778 | [8 empty] | 24.5 | 29.2778 | 30.0556 | 29.9444 | 30.0556 | [7 empty] | 29.1296
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | [8 empty] | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | [8 empty] | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2711.4937 | 2675.8162 | 2729.332 | 2301.2029 | [8 empty] | 1641.1666 | 2426.074 | 2586.6204 | 2461.7489 | 2390.3942 | [7 empty] | 21923.849
15 | Power Consumption of Chiller | KWH |  | 1460 | 1360 | 1270 | 1450 | [8 empty] | 1270 | 1270 | 1300 | 1360 | 1360 | [7 empty] | 12100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53845 | 0.50826 | 0.46532 | 0.63011 | [8 empty] | 0.77384 | 0.52348 | 0.50259 | 0.55245 | 0.56894 | [7 empty] | 0.5626
17 | Average iKW/TR |  |  | 0.5626 | [23 empty] | 0.5626
18 | COP of chiller |  |  | 6.5299 | 6.9178 | 7.5562 | 5.58 | [8 empty] | 4.5436 | 6.7166 | 6.9958 | 6.3643 | 6.1799 | [7 empty] | 6.376
19 | EER of Chiller |  |  | 22.2865 | 23.6104 | 25.7892 | 19.0446 | [8 empty] | 15.5072 | 22.9237 | 23.8767 | 21.7215 | 21.0919 | [7 empty] | 21.7613
20 | LMTD of Condenser | ºC |  | 3.8732 | 4.1798 | 3.691 | 3.4589 | [8 empty] | 4.1134 | 3.5154 | 3.4918 | 3.4367 | 3.2185 | [7 empty] | 3.6643
21 | LMTD of Evaporator | ºC |  | 2.9278 | 3.0857 | 2.7399 | 2.4376 | [8 empty] | 1.9485 | 2.314 | 3.0182 | 2.9228 | 2.8679 | [7 empty] | 2.6958
Performance Sheet Chiller
Date :- 26/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  |  |  | 1 | 1.1 | 1 | 1.1 | 1 | 1.1 | 1.2 | 1.1 | 1 | 1.3 | 1 | 1 | 1.1 | 1.1 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0818
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.6 | 0.5 | 0.4 | 0.5 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.3 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.5
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 15.6111 | 15.1111 | 13.8889 | 12.2222 | 12.4444 | 12.5556 | 12.8889 | 12.9444 | 13.0556 | 14.6111 | 15.5 | 15.5 | 14.5 | 14.0556 | 13.3333 | 12.6667 | 12.9444 | 14.1111 | 14.5556 | 14.7778 | 14.8889 | 14.7778 | 13.952
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 8.9 | 7.8333 | 5.8889 | 5.3333 | 5.5556 | 5.4444 | 5.5556 | 5.5 | 5.6111 | 5.8333 | 6.5 | 7.8889 | 6.2222 | 6 | 5.5556 | 5.3333 | 5.7778 | 5.7778 | 5.7778 | 5.7778 | 5.8889 | 5.7778 | 6.0788
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 24.1111 | 25.3333 | 25.2222 | 23.3333 | 22.0556 | 21.3889 | 20.6667 | 21.4444 | 22.1111 | 24 | 24.2222 | 24.7222 | 25.1667 | 25.1667 | 25.3889 | 25 | 23.7778 | 24 | 24.3889 | 23.9444 | 23.6111 | 23.6111 | 23.7576
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 23.4444 | 30.5 | 30.8889 | 28 | 26.7222 | 26.1667 | 25.6667 | 26.5556 | 27.2222 | 30.1667 | 30.4444 | 29.9444 | 30.7778 | 30.7778 | 30.7778 | 30.1111 | 28.6667 | 29.6667 | 30.4444 | 30.1111 | 29.7778 | 29.7778 | 28.9369
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2154.9232 | 2336.8788 | 2568.7837 | 2212.007 | 2212.0093 | 2283.3643 | 2354.718 | 2390.3936 | 2390.3971 | 2818.5256 | 2889.881 | 2443.9116 | 2657.9767 | 2586.6233 | 2497.4268 | 2354.719 | 2301.1997 | 2675.8149 | 2818.5269 | 2889.8813 | 2889.8816 | 2889.8813 | 55617.7247
15 | Power Consumption of Chiller | KWH |  |  |  | 1510 | 1570 | 1430 | 1410 | 1430 | 1440 | 1450 | 1460 | 1570 | 1600 | 1500 | 1550 | 1540 | 1530 | 1500 | 1450 | 1570 | 1590 | 1600 | 1600 | 1600 | 1600 | 33500
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.70072 | 0.67184 | 0.55668 | 0.63743 | 0.64647 | 0.63065 | 0.61578 | 0.61078 | 0.65679 | 0.56767 | 0.51905 | 0.63423 | 0.57939 | 0.5915 | 0.60062 | 0.61578 | 0.68225 | 0.59421 | 0.56767 | 0.55366 | 0.55366 | 0.55366 | 0.60639
17 | Average iKW/TR |  |  | 0.60639 | [23 empty] | 0.60639
18 | COP of chiller |  |  |  |  | 5.0177 | 5.2334 | 6.316 | 5.5159 | 5.4388 | 5.5752 | 5.7098 | 5.7566 | 5.3533 | 6.1937 | 6.7739 | 5.5437 | 6.0685 | 5.9442 | 5.854 | 5.7098 | 5.1535 | 5.9171 | 6.1937 | 6.3505 | 6.3505 | 6.3505 | 5.8327
19 | EER of Chiller |  |  |  |  | 17.1254 | 17.8617 | 21.5564 | 18.8258 | 18.5625 | 19.0282 | 19.4875 | 19.6472 | 18.2707 | 21.1391 | 23.1193 | 18.9208 | 20.7117 | 20.2874 | 19.9796 | 19.4875 | 17.5889 | 20.195 | 21.1391 | 21.6743 | 21.6743 | 21.6743 | 19.9071
20 | LMTD of Condenser | ºC |  |  |  | 0.60682 | 2.9695 | 2.987 | 2.8167 | 2.6903 | 2.8509 | 3.0446 | 2.9526 | 2.8236 | 3.5277 | 3.147 | 2.8566 | 3.1027 | 3.1027 | 2.9058 | 2.9526 | 2.885 | 3.1192 | 3.2338 | 3.2663 | 3.2663 | 3.2663 | 2.9261
21 | LMTD of Evaporator | ºC |  |  |  | 2.6842 | 2.6518 | 2.6277 | 2.558 | 2.8904 | 2.7849 | 2.8403 | 2.8679 | 2.8679 | 2.5743 | 3.2461 | 2.5395 | 2.6902 | 2.6402 | 2.5774 | 2.4759 | 2.4376 | 2.7026 | 3.0053 | 3.0566 | 3.2461 | 3.2461 | 2.7823

## 27-02-19 (hidden)
Performance Sheet Chiller
Date :- 27/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [6 empty] | 1.7 | 1.5 | 1.3 | 1.4 | 1.3 | 1.4 | 1.4 | 1.5 | 1.4 | 1.6 | 1.4 | 1.4 | 1.5 | 1.6 | 1.6 | 1.7 | 1.8 | 1.7 | 1.8 | 1.5263
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.5 | 0.4 | 0.5 | 0.39474
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 13.7222 | 14.3333 | 13.8889 | 13.7222 | 13.7222 | 13.8333 | 13.8889 | 13.8889 | 13.7778 | 13.7778 | 13.6667 | 13.1111 | 12.5556 | 12.7778 | 13.8889 | 14.4444 | 14.6667 | 14.8333 | 15.0556 | 13.8713
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 8 | 6.9444 | 6.9444 | 7 | 7.1111 | 7.1111 | 7 | 7.1111 | 7 | 7 | 6.1667 | 5.6111 | 5.6111 | 5.6111 | 5.8333 | 6.0556 | 6.5 | 6.4444 | 6.5556 | 6.6111
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 20 | 24.3889 | 24.2222 | 24.3889 | 24.6667 | 24.3333 | 24.5 | 24.9444 | 24.9444 | 24.9444 | 25.2778 | 25.4444 | 25.2222 | 23.5556 | 23.4444 | 23.4444 | 23.7222 | 23.4444 | 23 | 24.0994
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 24.5 | 29.0556 | 28.4444 | 28.5556 | 28.7778 | 28.5556 | 28.8889 | 29.3333 | 29.3333 | 29.1111 | 30 | 30.2222 | 29.5 | 28.2222 | 28.6111 | 28.8333 | 29 | 28.7778 | 28.2778 | 28.7368
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 1837.3927 | 2372.5553 | 2229.8466 | 2158.4906 | 2122.8131 | 2158.4903 | 2212.008 | 2176.3305 | 2176.3308 | 2176.3308 | 2408.2354 | 2408.2341 | 2229.8482 | 2301.2026 | 2586.6223 | 2693.6526 | 2622.3005 | 2693.6535 | 2729.3336 | 44293.6716
15 | Power Consumption of Chiller | KWH | [6 empty] | 1520 | 1520 | 1520 | 1490 | 1510 | 1470 | 1490 | 1500 | 1500 | 1500 | 1580 | 1500 | 1500 | 1530 | 1530 | 1600 | 1510 | 1500 | 1530 | 28800
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.82726 | 0.64066 | 0.68166 | 0.6903 | 0.71132 | 0.68103 | 0.6736 | 0.68923 | 0.68923 | 0.68923 | 0.65608 | 0.62286 | 0.67269 | 0.66487 | 0.5915 | 0.59399 | 0.57583 | 0.55686 | 0.56058 | 0.65625
17 | Average iKW/TR |  |  | Hours 7: 0.65625 | 0.65625
18 | COP of chiller | [7 empty] | 4.2502 | 5.4881 | 5.158 | 5.0935 | 4.9429 | 5.1628 | 5.2197 | 5.1013 | 5.1013 | 5.1013 | 5.3591 | 5.6449 | 5.2268 | 5.2883 | 5.9442 | 5.9193 | 6.106 | 6.3139 | 6.2721 | 5.4049
19 | EER of Chiller | [7 empty] | 14.5059 | 18.7309 | 17.6042 | 17.384 | 16.8702 | 17.6205 | 17.815 | 17.4108 | 17.4108 | 17.4108 | 18.2906 | 19.266 | 17.8389 | 18.0488 | 20.2874 | 20.2026 | 20.8397 | 21.5494 | 21.4067 | 18.447
20 | LMTD of Condenser | ºC | [6 empty] | 3.4778 | 3.301 | 2.9191 | 3.0186 | 2.8828 | 3.037 | 3.0919 | 3.2092 | 3.0919 | 3.2499 | 3.2005 | 3.2185 | 3.1721 | 3.4182 | 3.583 | 3.774 | 3.8547 | 3.7558 | 3.8547 | 3.3216
21 | LMTD of Evaporator | ºC | [6 empty] | 2.0974 | 2.4887 | 2.1809 | 2.132 | 2.1074 | 2.132 | 2.3733 | 2.3475 | 2.3475 | 2.3475 | 2.5141 | 2.5141 | 2.3862 | 2.4376 | 2.8367 | 2.715 | 2.8629 | 2.715 | 2.9408 | 2.4461
Performance Sheet Chiller
Date :- 27/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.1 | 1.2 | 1.1 | 1.1 | 0.9 | 1.1 | 1 | 1 | 0.9 | 1 | 0.9 | 0.9 | 0.9 | 1.1 | 1 | 1 | 0.9 | [7 empty] | 1.0059
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | [7 empty] | 0.48824
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.7778 | 14.6667 | 15.1111 | 15.1111 | 15.6111 | 15.5 | 14.8889 | 14 | 13.7778 | 13.7778 | 13.8889 | 14 | 13.8889 | 13.7778 | 13.8889 | 13.6667 | 13.2222 | [7 empty] | 14.3268
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.7778 | 5.6667 | 6 | 6.1111 | 6.3333 | 7.1667 | 7 | 7 | 7.1111 | 7.1111 | 7.1111 | 7 | 7 | 6.8889 | 7.1111 | 6 | 5.4444 | [7 empty] | 6.5784
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.6111 | 22.8333 | 22.8333 | 23.6111 | 23.6111 | 24.7222 | 24.5 | 24.2778 | 24.4444 | 24.6667 | 24.3333 | 24.5556 | 25.0556 | 24.9444 | 25.0556 | 25.3333 | 25.4444 | [7 empty] | 24.3431
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.7222 | 29.0556 | 29.2222 | 29.8889 | 29.8333 | 30.3889 | 29.9444 | 29 | 28.8889 | 29.2778 | 29.0556 | 29.2778 | 29.7778 | 29.6667 | 29.6667 | 30.6111 | 30.8333 | [7 empty] | 29.6536
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2889.8813 | 2889.8819 | 2925.5581 | 2889.8806 | 2979.0742 | 2675.8153 | 2533.1059 | 2247.6852 | 2140.6533 | 2140.6533 | 2176.3305 | 2247.6852 | 2212.008 | 2212.008 | 2176.3305 | 2461.7515 | 2497.4274 | [7 empty] | 42295.7302
15 | Power Consumption of Chiller | KWH |  | 1300 | 1340 | 1340 | 1340 | 1250 | 1220 | 1200 | 1190 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1220 | 1200 | [7 empty] | 21000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.44985 | 0.46369 | 0.45803 | 0.46369 | 0.41959 | 0.45594 | 0.47373 | 0.52943 | 0.56058 | 0.56058 | 0.55139 | 0.53388 | 0.54249 | 0.54249 | 0.55139 | 0.49558 | 0.48049 | [7 empty] | 0.50193
17 | Average iKW/TR |  |  | Hours 7: 0.50193 | 0.50193
18 | COP of chiller |  |  | 7.816 | 7.5827 | 7.6763 | 7.5827 | 8.3795 | 7.7116 | 7.422 | 6.6411 | 6.2721 | 6.2721 | 6.3766 | 6.5857 | 6.4812 | 6.4812 | 6.3766 | 7.0947 | 7.3175 | [7 empty] | 7.0629
19 | EER of Chiller |  |  | 26.6761 | 25.8798 | 26.1993 | 25.8798 | 28.5994 | 26.3197 | 25.3313 | 22.6659 | 21.4067 | 21.4067 | 21.7635 | 22.4771 | 22.1203 | 22.1203 | 21.7635 | 24.2142 | 24.9745 | [7 empty] | 24.1058
20 | LMTD of Condenser | ºC |  | 3.25 | 3.4148 | 3.3308 | 3.2986 | 3.008 | 3.1192 | 2.9221 | 2.7071 | 2.4949 | 2.6735 | 2.5775 | 2.5775 | 2.5775 | 2.8338 | 2.6735 | 2.873 | 2.7719 | [7 empty] | 2.8885
21 | LMTD of Evaporator | ºC |  | 3.2461 | 3.2461 | 3.2726 | 3.2461 | 3.1204 | 2.9019 | 2.7974 | 2.3991 | 2.3215 | 2.5038 | 2.7011 | 2.3991 | 2.3733 | 2.558 | 2.3475 | 2.5521 | 2.5774 | [7 empty] | 2.739
Performance Sheet Chiller
Date :- 27/02/2019
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 11: 1.2 | 1.2
2 | Small temperature difference of evaporator | ºC |  | Hours 11: 0.5 | 0.5
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 11: 15.2778 | 15.2778
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 11: 8 | 8
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 11: 23.7222 | 23.7222
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 11: 22.7778 | 22.7778
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 11: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 11: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 11: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 11: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 11: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 11: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 11: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 11: 2336.8798 | 2336.8798
15 | Power Consumption of Chiller | KWH |  | Hours 11: 1200 | 1200
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 11: 0.51351 | 0.51351
17 | Average iKW/TR |  |  | Hours 7: 0.51351 | 0.51351
18 | COP of chiller |  |  | Hours 11: 6.8471 | 6.8471
19 | EER of Chiller |  |  | Hours 11: 23.369 | 23.369
20 | LMTD of Condenser | ºC |  | Hours 11: 0.61065 | 0.61065
21 | LMTD of Evaporator | ºC |  | Hours 11: 2.6518 | 2.6518

## 28-02-2019 (hidden)
Performance Sheet Chiller
Date :- 28/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.6; Hours 8: 1.7; Hours 9: 1.6; Hours 10: 1.8; Hours 11: 1.8; Hours 12: 1.7; Hours 13: 1.6; Hours 14: 1.6; Hours 15: 1.6; Hours 16: 1.6; Hours 17: 1.6; Hours 18: 1.6; Hours 19: 1.5; Hours 20: 1.4 | 1.6214
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.4; Hours 8: 0.4; Hours 9: 0.6; Hours 10: 0.7; Hours 11: 0.7; Hours 12: 0.6; Hours 13: 0.5; Hours 14: 0.4; Hours 15: 0.4; Hours 16: 0.5; Hours 17: 0.4; Hours 18: 0.4; Hours 19: 0.5; Hours 20: 0.4 | 0.49286
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 15.0556; Hours 8: 15.1111; Hours 9: 15.2222; Hours 10: 15.6667; Hours 11: 15.8333; Hours 12: 15.3333; Hours 13: 14.8333; Hours 14: 14.2222; Hours 15: 13.7778; Hours 16: 13.6111; Hours 17: 13.5556; Hours 18: 14.5556; Hours 19: 15.2778; Hours 20: 15.6667 | 14.8373
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 6.5556; Hours 8: 6.6667; Hours 9: 6.7222; Hours 10: 7.0556; Hours 11: 7.2778; Hours 12: 6.8333; Hours 13: 6.3889; Hours 14: 5.9444; Hours 15: 5.6111; Hours 16: 5.6111; Hours 17: 5.5; Hours 18: 6.0556; Hours 19: 6.3889; Hours 20: 7.3333 | 6.4246
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 23; Hours 8: 23.3333; Hours 9: 23.4444; Hours 10: 23.2222; Hours 11: 22.7778; Hours 12: 22.6667; Hours 13: 22.2222; Hours 14: 21.9444; Hours 15: 21.6667; Hours 16: 22.6111; Hours 17: 22.2222; Hours 18: 21.7778; Hours 19: 20.6111; Hours 20: 23.6111 | 22.5079
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 28.2778; Hours 8: 28.6111; Hours 9: 28.7778; Hours 10: 28.7778; Hours 11: 28.2778; Hours 12: 28.0556; Hours 13: 27.5556; Hours 14: 27.2778; Hours 15: 26.8889; Hours 16: 27.7222; Hours 17: 27.5; Hours 18: 27.2778; Hours 19: 26.3333; Hours 20: 28.6111 | 27.8532
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4; Hours 8: 4; Hours 9: 4; Hours 10: 4; Hours 11: 4; Hours 12: 4; Hours 13: 4; Hours 14: 4; Hours 15: 4; Hours 16: 4; Hours 17: 4; Hours 18: 4; Hours 19: 4; Hours 20: 4 | 4
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.5; Hours 8: 3.5; Hours 9: 3.5; Hours 10: 3.5; Hours 11: 3.5; Hours 12: 3.5; Hours 13: 3.5; Hours 14: 3.5; Hours 15: 3.5; Hours 16: 3.5; Hours 17: 3.5; Hours 18: 3.5; Hours 19: 3.5; Hours 20: 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2729.3336; Hours 8: 2711.4928; Hours 9: 2729.3317; Hours 10: 2765.0105; Hours 11: 2747.17; Hours 12: 2729.331; Hours 13: 2711.4921; Hours 14: 2657.976; Hours 15: 2622.3005; Hours 16: 2568.7831; Hours 17: 2586.6229; Hours 18: 2729.333; Hours 19: 2854.2041; Hours 20: 2675.8166 | 37818.1978
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1600 | 1500 | 1500 | 1600 | 1400 | 1600 | 1500 | 1400 | 1600 | 1600 | 1300 | 1500 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.54958; Hours 8: 0.59008; Hours 9: 0.58622; Hours 10: 0.54249; Hours 11: 0.54602; Hours 12: 0.58622; Hours 13: 0.51632; Hours 14: 0.60196; Hours 15: 0.57202; Hours 16: 0.54501; Hours 17: 0.61857; Hours 18: 0.58622; Hours 19: 0.45547; Hours 20: 0.56058 | 0.5612
17 | Average iKW/TR |  |  | Hours 7: 0.5612 | 0.5612
18 | COP of chiller |  |  | Hours 7: 6.3976; Hours 8: 5.9585; Hours 9: 5.9977; Hours 10: 6.4812; Hours 11: 6.4394; Hours 12: 5.9977; Hours 13: 6.8097; Hours 14: 5.8409; Hours 15: 6.1467; Hours 16: 6.4513; Hours 17: 5.6841; Hours 18: 5.9977; Hours 19: 7.7195; Hours 20: 6.2721 | 6.2996
19 | EER of Chiller |  |  | Hours 7: 21.8349; Hours 8: 20.3364; Hours 9: 20.4702; Hours 10: 22.1203; Hours 11: 21.9776; Hours 12: 20.4702; Hours 13: 23.2416; Hours 14: 19.935; Hours 15: 20.9786; Hours 16: 22.0183; Hours 17: 19.3998; Hours 18: 20.4702; Hours 19: 26.3467; Hours 20: 21.4067 | 21.5005
20 | LMTD of Condenser | ºC |  | Hours 7: 3.6192; Hours 8: 3.7375; Hours 9: 3.6372; Hours 10: 3.9466; Hours 11: 3.9283; Hours 12: 3.774; Hours 13: 3.6372; Hours 14: 3.6372; Hours 15: 3.6011; Hours 16: 3.5648; Hours 17: 3.6192; Hours 18: 3.691; Hours 19: 3.6408; Hours 20: 3.2899 | 1.22
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.7399; Hours 8: 2.7275; Hours 9: 3.126; Hours 10: 3.3275; Hours 11: 3.3137; Hours 12: 3.126; Hours 13: 2.9278; Hours 14: 2.6902; Hours 15: 2.6652; Hours 16: 2.8236; Hours 17: 2.6402; Hours 18: 2.7399; Hours 19: 3.031; Hours 20: 2.7026 | 2.8986
Performance Sheet Chiller
Date :- 28/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 18: 1.2; Hours 19: 1.2; Hours 20: 0.9; Hours 21: 1.1; Hours 22: 0.9; Hours 23: 1.1; Hours 0: 1.1; Hours 1: 1.1; Hours 2: 0.9; Hours 3: 1; Hours 4: 1.1; Hours 5: 1.1; Hours 6: 1.1 | 1.0615
2 | Small temperature difference of evaporator | ºC |  | Hours 18: 0.6; Hours 19: 0.6; Hours 20: 0.6; Hours 21: 0.4; Hours 22: 0.4; Hours 23: 0.7; Hours 0: 0.6; Hours 1: 0.7; Hours 2: 0.6; Hours 3: 0.7; Hours 4: 0.7; Hours 5: 0.7; Hours 6: 0.7 | 0.61538
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 18: 15.9444; Hours 19: 15.9444; Hours 20: 15.9444; Hours 21: 14.3889; Hours 22: 13.3889; Hours 23: 12.6111; Hours 0: 13.2778; Hours 1: 13.3889; Hours 2: 13.5556; Hours 3: 13.5556; Hours 4: 13.5556; Hours 5: 13.3889; Hours 6: 13.2778 | 14.0171
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 18: 7.2778; Hours 19: 7.2778; Hours 20: 7.2778; Hours 21: 6.9444; Hours 22: 5.8333; Hours 23: 5.3333; Hours 0: 5.6667; Hours 1: 5.6667; Hours 2: 5.6667; Hours 3: 5.5556; Hours 4: 5.4444; Hours 5: 5.4444; Hours 6: 5.5 | 6.0684
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 18: 23; Hours 19: 23; Hours 20: 23; Hours 21: 24.6111; Hours 22: 24.6111; Hours 23: 23.5; Hours 0: 20.1111; Hours 1: 20.1667; Hours 2: 19.7778; Hours 3: 19.6667; Hours 4: 19.7778; Hours 5: 19.8889; Hours 6: 20.3333 | 21.6496
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 18: 29.1111; Hours 19: 29.1111; Hours 20: 29.1111; Hours 21: 29.8889; Hours 22: 29.8333; Hours 23: 28.3333; Hours 0: 25.3889; Hours 1: 25.3889; Hours 2: 25.1667; Hours 3: 25.0556; Hours 4: 25.2222; Hours 5: 25.2222; Hours 6: 25.5 | 27.1026
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 18: 4; Hours 19: 4; Hours 20: 4; Hours 21: 4; Hours 22: 4; Hours 23: 4; Hours 0: 4; Hours 1: 4; Hours 2: 4; Hours 3: 4; Hours 4: 4; Hours 5: 4; Hours 6: 4 | 4
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 18: 3.5; Hours 19: 3.5; Hours 20: 3.5; Hours 21: 3.5; Hours 22: 3.5; Hours 23: 3.5; Hours 0: 3.5; Hours 1: 3.5; Hours 2: 3.5; Hours 3: 3.5; Hours 4: 3.5; Hours 5: 3.5; Hours 6: 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8; Hours 5: 3.8; Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3; Hours 3: 3; Hours 4: 3; Hours 5: 3; Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5; Hours 3: 0.5; Hours 4: 0.5; Hours 5: 0.5; Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8; Hours 3: 0.8; Hours 4: 0.8; Hours 5: 0.8; Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971; Hours 3: 971; Hours 4: 971; Hours 5: 971; Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 18: 2782.8504; Hours 19: 2782.8504; Hours 20: 2782.8504; Hours 21: 2390.3955; Hours 22: 2426.0734; Hours 23: 2336.8788; Hours 0: 2443.9123; Hours 1: 2479.5895; Hours 2: 2533.1068; Hours 3: 2568.7844; Hours 4: 2604.4622; Hours 5: 2550.9448; Hours 6: 2497.4284 | 33180.1271
15 | Power Consumption of Chiller | KWH |  | Hours 18: 1200; Hours 19: 1300; Hours 20: 1400; Hours 21: 1300; Hours 22: 1300; Hours 23: 1200; Hours 0: 1400; Hours 1: 1300; Hours 2: 1300; Hours 3: 1300; Hours 4: 1300; Hours 5: 1200; Hours 6: 1200 | 16700
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 18: 0.43121; Hours 19: 0.46715; Hours 20: 0.50308; Hours 21: 0.54384; Hours 22: 0.53585; Hours 23: 0.51351; Hours 0: 0.57285; Hours 1: 0.52428; Hours 2: 0.5132; Hours 3: 0.50608; Hours 4: 0.49914; Hours 5: 0.47041; Hours 6: 0.48049 | 0.5047
17 | Average iKW/TR |  |  | Hours 7: 0.5047 | 0.5047
18 | COP of chiller |  |  | Hours 18: 8.1538; Hours 19: 7.5265; Hours 20: 6.9889; Hours 21: 6.4651; Hours 22: 6.5616; Hours 23: 6.8471; Hours 0: 6.1377; Hours 1: 6.7063; Hours 2: 6.8511; Hours 3: 6.9476; Hours 4: 7.0441; Hours 5: 7.4743; Hours 6: 7.3175 | 7.0017
19 | EER of Chiller |  |  | Hours 18: 27.8288; Hours 19: 25.6881; Hours 20: 23.8532; Hours 21: 22.0654; Hours 22: 22.3947; Hours 23: 23.369; Hours 0: 20.948; Hours 1: 22.8887; Hours 2: 23.3827; Hours 3: 23.7121; Hours 4: 24.0414; Hours 5: 25.5097; Hours 6: 24.9745 | 23.8966
20 | LMTD of Condenser | ºC |  | Hours 18: 3.3818; Hours 19: 3.3818; Hours 20: 2.9769; Hours 21: 3.003; Hours 22: 2.7238; Hours 23: 2.868; Hours 0: 3.003; Hours 1: 2.9862; Hours 2: 2.7719; Hours 3: 2.9058; Hours 4: 3.053; Hours 5: 3.0197; Hours 6: 2.9695 | 3.0034
21 | LMTD of Evaporator | ºC |  | Hours 18: 3.1662; Hours 19: 3.1662; Hours 20: 3.1662; Hours 21: 2.5014; Hours 22: 2.5268; Hours 23: 2.9909; Hours 0: 2.9091; Hours 1: 3.1044; Hours 2: 2.9774; Hours 3: 3.1746; Hours 4: 3.2026; Hours 5: 3.1606; Hours 6: 3.1184 | 3.0127

## Summery
Date | Avg.RH Temp.(%) | Avg. DB Temperature (°C) | Avg. WB Temperature (°C) | Chilled Water Avg. Inlet Temperature (°C) | Chilled Water Avg. Outlet Temperature (°C) | Condenser Water Avg. Outlet Temperature (°C) | Condenser Water Avg. Inlet Temperature (°C) | Chiller No.1 | [18 empty] | Chiller No.2 | [18 empty] | Chiller No.3 | [18 empty] | Chiller No.4 | [18 empty] | Chiller No.5 | [18 empty] | Chiller No.6 | [18 empty] | Total TR Generated | Difference from previous day | Total Power Consumption (KWH) | Difference from previous day | Total Running Hrs. | Avg. FLA % | Avg iKW/tr
[8 empty] | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Avg. Entering Chilled water Temp. | Avg. Leaving Chilled water Temp. | Avg. Evaporator Delta "T" | Avg. Entering Condenser water Temp. | Avg. Leaving Condenser water Temp. | Avg. Condenser Delta "T" | Evaporator pressure (kpag) | Condenser pressure (kpag) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Avg. Entering Chilled water Temp. | Avg. Leaving Chilled water Temp. | Avg. Evaporator Delta "T" | Avg. Entering Condenser water Temp. | Avg. Leaving Condenser water Temp. | Avg. Condenser Delta "T" | Evaporator pressure (kpag) | Condenser pressure (kpag) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Avg. Entering Chilled water Temp. | Avg. Leaving Chilled water Temp. | Avg. Evaporator Delta "T" | Avg. Entering Condenser water Temp. | Avg. Leaving Condenser water Temp. | Avg. Condenser Delta "T" | Evaporator pressure (kpag) | Condenser pressure (kpag) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Avg. Entering Chilled water Temp. | Avg. Leaving Chilled water Temp. | Avg. Evaporator Delta "T" | Avg. Entering Condenser water Temp. | Avg. Leaving Condenser water Temp. | Avg. Condenser Delta "T" | Evaporator pressure (kpag) | Condenser pressure (kpag) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Avg. Entering Chilled water Temp. | Avg. Leaving Chilled water Temp. | Avg. Evaporator Delta "T" | Avg. Entering Condenser water Temp. | Avg. Leaving Condenser water Temp. | Avg. Condenser Delta "T" | Evaporator pressure (kpag) | Condenser pressure (kpag) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Avg. Entering Chilled water Temp. | Avg. Leaving Chilled water Temp. | Avg. Evaporator Delta "T" | Avg. Entering Condenser water Temp. | Avg. Leaving Condenser water Temp. | Avg. Condenser Delta "T" | Evaporator pressure (kpag) | Condenser pressure (kpag)
Date :- 28/03/2025 | 39.6125 | 30.5667 | 20.3458 | 14.1417 | 9.1917 | 31.2917 | 26.65 | 1 |  | 1800 | [5 empty] | 81 | [29 empty] | 24 | 61104.9272 | 35900 | 0.58906 | 5.9997 | 20.4771 | 2.262 | 2.8952 | 89.9 | 0.6875 | 0.55 | 14.1417 | 6.2125 | 7.9292 | 26.7708 | 31.4042 | 4.6333 | 256.5667 | 715.3292 | [38 empty] | 19 | 44664.7156 | 27500 | 0.61413 | 5.9062 | 20.1579 | 3.0811 | 2.6281 | 83.3 | 1.2105 | 0.48421 | 13.9158 | 6.5947 | 7.3211 | 27.7316 | 32.8105 | 5.0789 | 262.3632 | 760.0947 | 105769.6429 | -1316.5013 | 65200 | 700 | 44 | 84.7333 | 0.61643
2025-03-01 | 41.4 | 29.8875 | 20.1625 | 13.4333 | 8.6917 | 30.5542 | 26.1917 | 18 | 44247.2884 | 25500 | 0.57569 | 6.1561 | 21.0109 | 3.9229 | 3.3293 | 84.7 | 1.8167 | 0.86111 | 13.2444 | 5.5889 | 7.6556 | 26.6444 | 32.0722 | 5.4278 | 244.6444 | 759.8722 | [19 empty] | 24 | 58311.3757 | 34300 | 0.58984 | 5.995 | 20.4611 | 2.1731 | 2.7107 | 85.8 | 0.67917 | 0.49583 | 13.4375 | 5.8708 | 7.5667 | 26.3 | 30.6583 | 4.3583 | 252.8875 | 701.3458 | [21 empty] | 1200 | [35 empty] | 102558.664 | -3210.9788 | 61000 | -4200 | 42 | 85.25 | 0.59478
2025-03-02 | 36.0875 | 29.8667 | 19.05 | 13.5458 | 8.5333 | 30.15 | 25.6208 | [38 empty] | 24 | 59627.877 | 34800 | 0.58589 | 6.0378 | 20.6069 | 2.2611 | 2.7871 | 87.8 | 0.72083 | 0.51667 | 13.5333 | 5.7958 | 7.7375 | 25.7167 | 30.1833 | 4.4667 | 251.6875 | 690.1917 | [19 empty] | 18 | 41261.078 | 24900 | 0.59641 | 5.9188 | 20.2009 | 2.2129 | 3.2376 | 94.8 | 0.64118 | 0.81176 | 13.5647 | 6.0059 | 7.5588 | 27.2647 | 31.9588 | 4.6941 | 250.6765 | 726.5824 | [19 empty] | 100888.955 | -1669.709 | 59700 | -1300 | 42 | 91.3 | 0.59174
2025-03-03 | 38.3792 | 30.0125 | 19.6542 | 13.5708 | 8.5417 | 30.0125 | 24.9 | [38 empty] | 24 | 60494.8413 | 34400 | 0.57027 | 6.1994 | 21.1585 | 2.3237 | 2.8533 | 87.3 | 0.76667 | 0.5375 | 13.6125 | 5.7625 | 7.85 | 25.0333 | 29.5 | 4.4667 | 251.0583 | 674.6208 | [19 empty] | 6 | 15155.8201 | 9100 | 0.57392 | 6.1824 | 21.1007 | 2.3214 | 3.4048 | 93.5 | 0.66667 | 0.86667 | 13.75 | 5.8833 | 7.8667 | 26.4 | 31.35 | 4.95 | 246.6167 | 713.15 | 12 | 23921.7923 | 17800 | 0.5935 | 5.9414 | 20.2779 | 3.003 | 2.9026 | 82.6 | 1.17 | 0.62 | 13.28 | 5.83 | 7.45 | 25.59 | 30.58 | 4.99 | 250.88 | 709.47 | 99572.4537 | -1316.5013 | 61300 | 1600 | 42 | 87.8 | 0.61563
2025-03-04 | 36.275 | 30.0042 | 19.1375 | 13.4792 | 8.425 | 28.7292 | 24.2417 | [38 empty] | 19 | 44054.6296 | 25500 | 0.56568 | 6.2552 | 21.3492 | 2.2418 | 2.7616 | 85.9 | 0.75 | 0.51667 | 13.5611 | 5.9389 | 7.6222 | 25.1889 | 29.45 | 4.2611 | 253.3778 | 673.4667 | [38 empty] | 24 | 56416.8981 | 33100 | 0.58806 | 6.0228 | 20.5558 | 2.9131 | 2.899 | 84 | 1.1417 | 0.64167 | 13.4083 | 6.0875 | 7.3208 | 24.4833 | 29.3 | 4.8167 | 253.7292 | 679.9375 | 100471.5278 | 899.0741 | 58600 | -2700 | 43 | 84.95 | 0.58325
2025-03-05 | 28.9542 | 30.3125 | 17.7875 | 13.2917 | 8.4167 | 27.6208 | 22.9875 | 22 | 54104.9934 | 29700 | 0.53807 | 6.5687 | 22.4189 | 3.8391 | 3.6945 | 84.4 | 1.7591 | 1.1136 | 13.2818 | 5.6227 | 7.6591 | 22.8227 | 28.2 | 5.3773 | 241.4591 | 668.6591 | [38 empty] | 5 | 12362.2685 | 7200 | 0.52335 | 6.8343 | 23.3256 | 3.6353 | 3.0642 | 86.2 | 1.82 | 0.68 | 13.5 | 5.8 | 7.7 | 23.8 | 28.36 | 4.56 | 250.28 | 672.64 | [19 empty] | 12 | 26843.7831 | 15000 | 0.53193 | 7.8962 | 26.9497 | 2.9311 | 2.8269 | 75.8 | 1.1636 | 0.56364 | 13.2 | 5.6 | 7.6 | 24.2818 | 29.0636 | 4.7818 | 248.5273 | 673.8 | 93311.045 | -7160.4828 | 51900 | -6700 | 39 | 82.1333 | 0.5562
2025-03-06 | 27.5083 | 29.425 | 16.75 | 13.2375 | 8.4 | 26.5167 | 22.0333 | 24 | 59178.3399 | 30800 | 0.52221 | 6.7581 | 23.0654 | 3.9258 | 4.044 | 84.5 | 1.8375 | 1.3583 | 13.3833 | 5.7042 | 7.6792 | 21.6625 | 27.025 | 5.3625 | 241.1417 | 644.4833 | [76 empty] | 14 | 29701.5542 | 17900 | 0.55862 | 6.3209 | 21.5731 | 2.6819 | 2.5332 | 72.9 | 1.0846 | 0.46154 | 12.7385 | 5.6231 | 7.1154 | 23.6615 | 27.9615 | 4.3 | 250.5462 | 648.2 | 88879.8942 | -4431.1508 | 48700 | -3200 | 38 | 78.7 | 0.54793
2025-03-07 | 28.7208 | 29.875 | 17.3292 | 13.1917 | 8.3083 | 27.0375 | 22.5667 | 24 | 58279.2659 | 30900 | 0.53149 | 6.6385 | 22.6571 | 4.0805 | 3.8448 | 85.5 | 1.9792 | 1.2375 | 13.3333 | 5.7708 | 7.5625 | 22.2083 | 27.5417 | 5.3333 | 242.1958 | 657.3667 | [76 empty] | 14 | 32430.8862 | 18900 | 0.54958 | 6.436 | 21.966 | 2.7656 | 2.5834 | 77.4 | 1.1214 | 0.47857 | 12.8 | 5.5857 | 7.2143 | 23.7929 | 28.2143 | 4.4214 | 249.5929 | 652.5786 | 90710.1521 | 1830.2579 | 49800 | 1100 | 38 | 81.45 | 0.549
2025-03-08 | 45.2958 | 29.6708 | 20.3375 | 13.4875 | 8.2458 | 30.025 | 25.0333 | 24 | 58150.8267 | 31900 | 0.5494 | 6.4384 | 21.9744 | 3.9768 | 3.3086 | 85.6 | 1.9042 | 0.8825 | 13.5917 | 6.0458 | 7.5458 | 24.7417 | 30.025 | 5.2833 | 249.9375 | 715.2708 | [76 empty] | 20 | 47329.828 | 28400 | 0.57483 | 6.152 | 20.9969 | 2.8529 | 2.578 | 79.3 | 1.12 | 0.45 | 13.355 | 5.985 | 7.37 | 25.405 | 30.11 | 4.705 | 260.94 | 697.03 | 105480.6548 | 14770.5026 | 60300 | 10500 | 44 | 82.45 | 0.57167
2025-03-09 | 47.275 | 29.9625 | 21.2583 | 13.5333 | 8.0917 | 30.8833 | 25.9542 | 24 | 58054.4974 | 32500 | 0.56062 | 6.299 | 21.4986 | 4.01 | 3.2517 | 88.6 | 1.9417 | 0.84167 | 13.6 | 6.0667 | 7.5333 | 25.6292 | 30.8833 | 5.2542 | 251.8917 | 734.8208 | [76 empty] | 21 | 52371.0648 | 30700 | 0.58672 | 6.0215 | 20.5514 | 3.0337 | 2.747 | 79.6 | 1.1857 | 0.49048 | 13.5476 | 5.781 | 7.7667 | 26.2905 | 31.3143 | 5.0238 | 251.6238 | 725.0714 | 110425.5622 | 4944.9074 | 63200 | 2900 | 45 | 84.1 | 0.57233
2025-03-10 | 34.6083 | 31.975 | 20.1833 | 13.375 | 8.0917 | 30.0833 | 25.025 | 24 | 59403.1085 | 32700 | 0.55096 | 6.4142 | 21.8917 | 4.0172 | 3.1457 | 87.8 | 1.9083 | 0.7375 | 13.4667 | 5.7583 | 7.7083 | 24.6917 | 30.0833 | 5.3917 | 247.9042 | 716.5375 | [76 empty] | 19 | 46238.0952 | 26700 | 0.57838 | 6.1427 | 20.965 | 2.9848 | 2.6125 | 80.1 | 1.2053 | 0.44211 | 13.1842 | 5.6053 | 7.5789 | 25.5263 | 30.3158 | 4.7895 | 256.4842 | 702.2421 | 105641.2037 | -4784.3585 | 59400 | -3800 | 43 | 83.95 | 0.56228
2025-03-11 | 40.0458 | 31.825 | 21.2917 | 13.3708 | 7.725 | 29.8125 | 25.2708 | 24 | 57861.8386 | 32100 | 0.55581 | 6.3509 | 21.6757 | 2.5706 | 4.9163 | 85.7 | 2.0833 | 0.80833 | 13.4583 | 5.95 | 7.5083 | 24.9417 | 30.1708 | 5.2292 | 249.6875 | 720.0958 | [76 empty] | 24 | 58600.3638 | 33400 | 0.56971 | 6.1987 | 21.156 | 3.0184 | 2.7115 | 81.3 | 1.2458 | 0.49167 | 13.5708 | 5.9667 | 7.6042 | 25.525 | 30.2625 | 4.7375 | 254.1292 | 703.3667 | 116462.2024 | 10820.9987 | 65500 | 6100 | 48 | 83.5 | 0.56241
2025-03-12 | 42.2417 | 31.8958 | 21.7417 | 13.6 | 8.0167 | 30.1875 | 25.5292 | 24 | 58375.5952 | 31600 | 0.54207 | 6.5283 | 22.281 | 4.0925 | 3.0834 | 87 | 2.0833 | 0.72917 | 13.7125 | 6.1375 | 7.575 | 25.1333 | 30.1875 | 5.0542 | 258.8833 | 710.1 | [76 empty] | 24 | 59370.9987 | 34400 | 0.5799 | 6.085 | 20.7682 | 3.0613 | 2.7265 | 80.5 | 1.2792 | 0.4875 | 13.7542 | 6.05 | 7.7042 | 25.8708 | 30.6167 | 4.7458 | 255.2167 | 712.05 | 117746.5939 | 1284.3915 | 66000 | 500 | 48 | 83.75 | 0.56053
2025-03-13 | 62.1583 | 30.4208 | 24.2167 | 14.175 | 8.275 | 32.4708 | 27.4917 | 24 | 57733.3995 | 33700 | 0.58469 | 6.0488 | 20.6444 | 4.0563 | 3.0871 | 93.1 | 1.9708 | 0.7375 | 14.225 | 6.7333 | 7.4917 | 27.1792 | 32.4708 | 5.2917 | 260.6167 | 772.9417 | [38 empty] | 10 | 24242.8902 | 16500 | 0.6195 | 5.6913 | 19.4245 | 3.4184 | 2.6388 | 92.2 | 1.64 | 0.46 | 14.55 | 7 | 7.55 | 28.74 | 33.27 | 4.53 | 266.54 | 785.31 | [19 empty] | 17 | 42224.3717 | 23800 | 0.56261 | 10.4899 | 35.8021 | 3.2464 | 2.7127 | 80.7 | 1.3588 | 0.47647 | 14.2882 | 6.5529 | 7.7353 | 27.3765 | 32.4 | 5.0235 | 261.1941 | 755.1824 | 124200.6614 | 6454.0675 | 74000 | 8000 | 51 | 88.6667 | 0.59581
2025-03-14 | 54.9208 | 30.3542 | 22.8583 | 13.9 | 8.1 | 31.1 | 26.6542 | 6 | 14642.0635 | 7500 | 0.51508 | 8.0599 | 27.5083 | 4.1267 | 3.0148 | 92 | 2 | 0.66667 | 14.9667 | 7.3667 | 7.7833 | 27.1833 | 32.5833 | 5.5 | 268.7833 | 776.1167 | 5 | 11880.6217 | 7200 | 0.55227 | 6.6428 | 22.672 | 2.1197 | 2.6952 | 89.8 | 0.78 | 0.54 | 13.8667 | 6.5667 | 7.3 | 27.15 | 31.1667 | 4.0167 | 258.1 | 724.8667 | 17 | 38820.7341 | 24900 | 0.59276 | 5.9455 | 20.2918 | 2.2399 | 2.677 | 82.7 | 0.74375 | 0.48125 | 13.4187 | 5.8625 | 7.5562 | 26.325 | 30.6062 | 4.2812 | 252.6125 | 698.35 | 24 | 59114.1204 | 35100 | 0.59401 | 5.9359 | 20.2594 | 3.5301 | 2.788 | 90.7 | 1.725 | 0.525 | 14.15 | 6.4792 | 7.6708 | 26.7625 | 31.3333 | 4.5708 | 260.3125 | 739.5625 | [38 empty] | 124457.5397 | 256.8783 | 74700 | 700 | 52 | 88.8 | 0.6002
2025-03-15 | 47.7542 | 30.2458 | 21.5417 | 13.7 | 8 | 29.4 | 25 | [38 empty] | 24 | 60077.414 | 34000 | 0.56608 | 6.2299 | 21.2627 | 2.2802 | 2.8333 | 87 | 0.75 | 0.53333 | 13.6792 | 5.8833 | 7.7958 | 25.1125 | 29.5042 | 4.3917 | 252.6083 | 674.2208 | 24 | 60494.8413 | 34900 | 0.57715 | 6.115 | 20.8706 | 3.668 | 2.9622 | 87 | 1.8083 | 0.6 | 13.8667 | 6.0167 | 7.85 | 25.0667 | 29.7625 | 4.6958 | 253.575 | 704.6417 | [38 empty] | 120572.2553 | -3885.2844 | 68900 | -5800 | 48 | 87 | 0.57144
2025-03-16 | 53.2958 | 29.8583 | 22.3208 | 13.4458 | 7.7833 | 29.6542 | 25.2542 | 1 | 2408.2341 | 1800 | 0.53981 | 6.5133 | 22.2301 | 3.7954 | 2.5141 | 87 | 1.8 | 0.4 | 13.1 | 5.6 | 7.5 | 24.8 | 29.9 | 5.1 | 248.2 | 706.7 | [19 empty] | 24 | 59403.1085 | 34200 | 0.57578 | 6.121 | 20.8911 | 2.2702 | 2.7437 | 87.7 | 0.75417 | 0.49583 | 13.475 | 5.7667 | 7.7083 | 25.35 | 29.6875 | 4.3375 | 251.2625 | 679.6042 | 23 | 58022.3876 | 33400 | 0.57582 | 6.1898 | 21.1258 | 3.6993 | 2.9433 | 89.4 | 1.8304 | 0.58696 | 13.6435 | 5.787 | 7.8565 | 25.3348 | 30.0478 | 4.713 | 251.2304 | 711.6435 | [38 empty] | 119833.7302 | -738.5251 | 69400 | 500 | 48 | 88.0333 | 0.57914
2025-03-17 | 54.1 | 29.7 | 22.2 | 13.3 | 7.6 | 29.5 | 25.2 | 23 | 54522.4206 | 30700 | 0.54902 | 6.4231 | 21.9221 | 3.9933 | 3.0476 | 89.7 | 1.8773 | 0.67273 | 12.7 | 13.3 | 7.7182 | 21.8 | 21.8 | 5.4273 | 247.8273 | 718.6636 | [19 empty] | 24 | 58600.3638 | 33300 | 0.57331 | 6.1532 | 21.0009 | 2.2693 | 2.7323 | 87.9 | 0.77917 | 0.50417 | 13.3292 | 5.725 | 7.6042 | 25.3292 | 29.55 | 4.2208 | 251.2875 | 675.5125 | 1 | 2151.3558 | 1800 | 0.60427 | 5.8186 | 19.8588 | 3.1585 | 2.3293 | 85 | 1.6 | 0.4 | 14.9 | 6.3 | 6.7 | 21.8 | 27.2 | 3.9 | 252.3 | 641.9 | [38 empty] | 115274.1402 | -4559.5899 | 65800 | -3600 | 48 | 87.5333 | 0.57081
2025-03-18 | 55.2958 | 29.0333 | 21.8625 | 13.3 | 7.7 | 29.2208 | 24.8625 | 1 | 1958.6971 | 1500 | 0.61265 | 5.739 | 19.5871 | 3.5231 | 2.1879 | 77 | 1.8 | 0.4 | 12.7 | 6.6 | 6.1 | 24.6 | 28.9 | 4.3 | 263.4 | 675.7 | [19 empty] | 23 | 56994.8743 | 32100 | 0.56413 | 6.2981 | 21.4953 | 2.2051 | 2.7502 | 87.4 | 0.7087 | 0.5 | 13.3696 | 5.6522 | 7.7174 | 24.9826 | 29.3087 | 4.3261 | 249.913 | 670.0913 | 24 | 59531.5476 | 34300 | 0.57722 | 6.1198 | 20.8868 | 3.5712 | 2.7099 | 86 | 1.75 | 0.47917 | 13.4875 | 5.7625 | 7.725 | 24.975 | 29.5833 | 4.6083 | 250.9167 | 697.8375 | [38 empty] | 118485.119 | 3210.9788 | 67900 | 2100 | 48 | 83.4667 | 0.57307
2025-03-19 | 54.3792 | 29.0458 | 21.8458 | 13.4 | 7.3 | 29.3 | 24.8 | 24 | 58825.1323 | 31600 | 0.53775 | 6.5812 | 22.4616 | 3.6444 | 3.1565 | 86.3 | 1.625 | 0.76667 | 13.4958 | 5.8625 | 7.6333 | 24.4958 | 29.7625 | 5.2667 | 249.2167 | 700.425 | [38 empty] | 4 | 9857.705 | 5600 | 0.56856 | 6.2078 | 21.1874 | 3.3994 | 2.6951 | 80 | 1.625 | 0.475 | 13.35 | 5.675 | 7.675 | 24.275 | 28.8 | 4.525 | 249.575 | 679.825 | [19 empty] | 20 | 47137.1693 | 27900 | 0.56629 | 6.2295 | 21.2613 | 3.2251 | 2.7933 | 84.5 | 1.2895 | 0.52105 | 13.5789 | 5.8526 | 7.7263 | 24.8105 | 30.0368 | 5.2263 | 253.0737 | 699.2632 | 115820.0066 | -2665.1124 | 65100 | -2800 | 48 | 83.6 | 0.56208
2025-03-20 | 45.1417 | 30.0792 | 20.7125 | 13.2875 | 7.55 | 28.0917 | 23.8167 | 23 | 53270.1389 | 27800 | 0.52693 | 6.799 | 23.205 | 3.3463 | 3.2294 | 81 | 1.4478 | 0.89565 | 13.4174 | 6.2043 | 7.213 | 23.4348 | 28.4391 | 5.0043 | 251.9304 | 667.5 | [19 empty] | 1 | 2022.9167 | 1200 | 0.54377 | 6.466 | 22.0684 | 1.8577 | 2.4137 | 69 | 0.72 | 0.5 | 13.1 | 6.8 | 6.3 | 24.1 | 27.2 | 3.1 | 266.8 | 625.4 | [38 empty] | 24 | 57155.4233 | 31700 | 0.55548 | 6.3581 | 21.7001 | 3.179 | 2.685 | 81.5 | 1.3083 | 0.50417 | 13.4542 | 6.0375 | 7.4167 | 23.6458 | 28.65 | 5.0042 | 254.7583 | 667.8417 | 112448.4788 | -3371.5278 | 60700 | -4400 | 48 | 77.1667 | 0.5398
2025-03-21 | 50.2375 | 29.0083 | 20.7917 | 13.7417 | 8.1167 | 28.1292 | 23.8167 | [38 empty] | 24 | 58664.5833 | 32000 | 0.54605 | 6.486 | 22.1369 | 2.1202 | 2.6495 | 84.6 | 0.675 | 0.45833 | 13.7375 | 6.125 | 7.6125 | 23.9708 | 28.1625 | 4.1917 | 256.5667 | 643.6708 | [38 empty] | 21 | 48582.1098 | 27800 | 0.54627 | 6.487 | 22.14 | 3.2314 | 2.8579 | 82.1 | 1.31 | 0.58 | 13.775 | 6.21 | 7.565 | 23.42 | 28.585 | 5.165 | 256.405 | 667.035 | 107246.6931 | -5201.7857 | 59800 | -900 | 45 | 83.35 | 0.55759
2025-03-22 | 60.4625 | 29.0708 | 22.7583 | 14.025 | 8.1167 | 30.1125 | 25.5208 | [38 empty] | 24 | 61522.3545 | 35000 | 0.56843 | 6.208 | 21.1879 | 2.1914 | 2.8637 | 87.9 | 0.68333 | 0.525 | 14.0667 | 6.0833 | 7.9833 | 25.675 | 30.0792 | 4.4042 | 255.3333 | 686.0833 | [21 empty] | 1400 | [16 empty] | 24 | 58728.8029 | 33400 | 0.56846 | 6.2124 | 21.2028 | 3.2062 | 2.8081 | 88.5 | 1.2304 | 0.5 | 14.2391 | 6.287 | 7.9522 | 25.3348 | 30.7391 | 5.4043 | 257.9522 | 713.4826 | 120251.1574 | 13004.4643 | 69800 | 10000 | 48 | 88.2 | 0.58045
2025-03-23 | 64.3417 | 30.0083 | 24.3625 | 14.3083 | 8.1083 | 31.8625 | 27.15 | [19 empty] | 4 | 7192.5926 | 5800 | 0.54564 | 6.6004 | 22.5271 | 2.3174 | 3.1958 | 85.5 | 0.7 | 0.8 | 14.2 | 6.7333 | 7.4667 | 28.4333 | 33.2 | 4.7667 | 260.1667 | 756.1333 | 24 | 62004.0013 | 37100 | 0.59908 | 5.8842 | 20.0829 | 2.2588 | 2.9532 | 92.3 | 0.7 | 0.56667 | 14.3417 | 6.2958 | 8.0458 | 27.3042 | 31.8625 | 4.5583 | 257.4167 | 726.3708 | [19 empty] | 24 | 61811.3426 | 36700 | 0.59338 | 5.9452 | 20.2908 | 2.24 | 3.6584 | 97.1 | 0.5875 | 1.0125 | 14.5083 | 6.4875 | 8.0208 | 27.3208 | 32.4 | 5.0792 | 254.05 | 736.9083 | [19 empty] | 131007.9365 | 10756.7791 | 79600 | 9800 | 52 | 91.6333 | 0.6076
2025-03-24 | 61.0167 | 29.8083 | 23.7667 | 14.1333 | 7.9417 | 31.8792 | 27.1292 | [38 empty] | 24 | 60462.7315 | 35900 | 0.59414 | 5.9407 | 20.2756 | 2.1395 | 2.8453 | 92 | 0.6375 | 0.53333 | 14.1708 | 6.325 | 7.8458 | 27.2708 | 31.7208 | 4.45 | 258.3542 | 722.0583 | 3 | 7674.2394 | 5100 | 0.58614 | 6.0629 | 20.6926 | 3.5513 | 2.876 | 96.3 | 1.6667 | 0.53333 | 15.0667 | 7.1 | 7.9667 | 29.4 | 34.2333 | 4.8333 | 267.5333 | 807.4 | 24 | 62581.9775 | 37200 | 0.59449 | 5.9449 | 20.29 | 2.3196 | 3.7749 | 94.8 | 0.625 | 1.0708 | 14.35 | 6.2292 | 8.1208 | 27.2833 | 32.45 | 5.1667 | 250.3917 | 739.4875 | [19 empty] | 130718.9484 | -288.9881 | 78200 | -1400 | 51 | 94.3667 | 0.59823
2025-03-25 | 64.45 | 29.875 | 24.325 | 14.0792 | 7.8292 | 32.4375 | 27.8125 | [38 empty] | 24 | 59306.7791 | 35700 | 0.60275 | 5.8543 | 19.9806 | 2.1229 | 2.7832 | 89 | 0.6375 | 0.52083 | 14.1208 | 6.425 | 7.6958 | 27.9375 | 32.3375 | 4.4 | 259.6375 | 735.8375 | 6 | 12522.8175 | 10300 | 0.61496 | 5.7638 | 19.672 | 3.2291 | 2.6989 | 92.5 | 1.42 | 0.46 | 14.76 | 6.96 | 7.8 | 29.26 | 34 | 4.74 | 266.68 | 795.54 | 24 | 60526.9511 | 36600 | 0.605 | 5.8343 | 19.9126 | 2.237 | 3.4299 | 93.1 | 0.6 | 0.8875 | 14.2583 | 6.4042 | 7.8542 | 27.9708 | 32.9667 | 4.9958 | 254.3917 | 750.7875 | [19 empty] | 132356.5476 | 1637.5992 | 82600 | 4400 | 54 | 91.5333 | 0.62407
2025-03-26 | 64.7583 | 28.9333 | 23.5667 | 14.0375 | 7.8083 | 31.6792 | 27.0875 | 17 | 43829.8611 | 24500 | 0.55003 | 6.4121 | 21.8845 | 2.0583 | 2.9632 | 91.9 | 0.42353 | 0.57647 | 13.9294 | 5.9 | 8.0294 | 26.6176 | 32.0294 | 5.4118 | 252.2529 | 723.8706 | [19 empty] | 24 | 60912.2685 | 36000 | 0.59141 | 5.9768 | 20.399 | 2.1362 | 2.8965 | 93.3 | 0.63333 | 0.55417 | 14.0917 | 6.1875 | 7.9042 | 27.1958 | 31.65 | 4.4542 | 256.1375 | 720.5208 | [19 empty] | 11 | 27742.8571 | 15600 | 0.56092 | 6.4054 | 21.8617 | 2.2003 | 3.3959 | 96 | 0.58182 | 0.86364 | 14.6091 | 6.7545 | 7.8545 | 27.8818 | 32.8455 | 4.9636 | 258.9909 | 747.5182 | [19 empty] | 132484.9868 | 128.4392 | 76100 | -6500 | 52 | 93.7333 | 0.5744
2025-03-27 | 63.5875 | 28.0083 | 22.5958 | 13.625 | 7.6083 | 30.325 | 25.7917 | 24 | 62517.7579 | 33600 | 0.5372 | 6.5814 | 22.4624 | 2.0704 | 3.0736 | 87.8 | 0.425 | 0.625 | 13.7792 | 5.6667 | 8.1125 | 25.475 | 30.925 | 5.45 | 248.6042 | 699.5333 | 1 | 2279.795 | 1700 | 0.57023 | 6.166 | 21.0445 | 2.3213 | 2.4222 | 78 | 0.8 | 0.4 | 12.6 | 5.5 | 7.1 | 24.5 | 28.8 | 4.3 | 248.9 | 653.6 | 23 | 58632.4735 | 33500 | 0.57062 | 6.2524 | 21.3393 | 2.0918 | 2.9261 | 89.8 | 0.6 | 0.56522 | 13.687 | 5.7478 | 7.9391 | 25.9957 | 30.4609 | 4.4652 | 250.6913 | 692.6522 | [57 empty] | 123430.0265 | -9054.9603 | 68800 | -7300 | 48 | 85.2 | 0.5574
2025-03-28 | 43.4792 | 29.8625 | 20.5625 | 13.6042 | 7.8917 | 28.7583 | 24.1 | 24 | 62774.6362 | 33300 | 0.53065 | 6.6636 | 22.7427 | 2.0724 | 3.3587 | 84.2 | 0.42917 | 0.80833 | 13.7208 | 5.575 | 8.1458 | 23.7625 | 29.2 | 5.4375 | 245.1875 | 662.6667 | 19 | 48164.6825 | 27400 | 0.56669 | 6.4355 | 21.9643 | 2.3088 | 3.3826 | 89.4 | 0.64211 | 0.84737 | 13.5211 | 5.6263 | 7.8947 | 24.7211 | 29.7526 | 5.0316 | 245.4421 | 677.3158 | [21 empty] | 100 | [54 empty] | 110939.3188 | -12490.7077 | 60800 | -8000 | 43 | 86.8 | 0.54805
2025-03-29 | 43.8542 | 30.8958 | 21.2125 | 13.6167 | 7.9917 | 28.5958 | 24.3 | 24 | 57733.3995 | 29900 | 0.51878 | 6.831 | 23.3141 | 1.9834 | 3.6812 | 79.5 | 0.42917 | 1.1625 | 13.7708 | 6.2792 | 7.4917 | 23.9792 | 29.0583 | 5.0792 | 251.25 | 658.5583 | [38 empty] | 24 | 54008.664 | 31700 | 0.56545 | 6.2631 | 21.376 | 2.9529 | 2.9492 | 84.5 | 1.3 | 0.67826 | 13.787 | 6.4739 | 7.313 | 24.5783 | 28.9174 | 4.3391 | 258.8478 | 672.9217 | [38 empty] | 111742.0635 | 802.7447 | 61600 | 800 | 48 | 82 | 0.55127
2025-03-30 | 48.9708 | 31.3292 | 22.625 | 13.6375 | 7.6833 | 30.65 | 25.5375 | 24 | 62068.2209 | 33500 | 0.53969 | 6.5493 | 22.3529 | 2.1843 | 3.2383 | 85 | 0.5 | 0.7375 | 13.7667 | 5.7125 | 8.0542 | 25.2458 | 30.65 | 5.4042 | 246.1458 | 694.05 | [38 empty] | 24 | 59627.877 | 34300 | 0.57602 | 6.125 | 20.9046 | 2.9577 | 2.859 | 89.2 | 1.2208 | 0.55833 | 13.8125 | 6.075 | 7.7375 | 25.6375 | 30.2792 | 4.6417 | 254.6458 | 702.3042 | [38 empty] | 121696.0979 | 9954.0344 | 67800 | 6200 | 48 | 87.1 | 0.55713
2025-03-31 | 56.575 | 30.7708 | 23.7667 | 13.7583 | 7.3833 | 31.7042 | 26.5042 | 24 | 63320.5026 | 34700 | 0.54752 | 6.4384 | 21.9741 | 2.1947 | 3.2607 | 86.6 | 0.49167 | 0.72083 | 13.8833 | 5.6667 | 8.2167 | 26.2042 | 31.7042 | 5.5 | 247.0583 | 718.975 | [19 empty] | 12 | 29926.3228 | 19700 | 0.5813 | 6.0641 | 20.6967 | 1.9842 | 2.9019 | 83.7 | 0.55 | 0.575 | 13.2667 | 5.5 | 7.7667 | 26.1083 | 30.45 | 4.3417 | 247.4417 | 692.4167 | 2 | 4944.9074 | 1100 | 0.22433 | 26.7819 | 91.4067 | 2.7626 | 2.6567 | 85 | 1.15 | 0.45 | 13.3 | 5.6 | 7.7 | 26.7 | 31 | 4.3 | 249.6 | 717.1 | [19 empty] | 11 | 28577.7116 | 17000 | 0.59525 | 5.924 | 20.2187 | 3.1577 | 2.9424 | 86.1 | 1.1455 | 0.55455 | 14.5818 | 6.4909 | 8.0909 | 27 | 32.6 | 5.6 | 259.9364 | 754.9182 | 126769.4444 | 5073.3466 | 72500 | 4700 | 49 | 85.35 | 0.5719
Average/Total | 48.2442 | 30.0329 | 21.3734 | 13.6191 | 8.0089 | 29.8866 | 25.264 | 447 | 1103260.2183 | 601800 | 0.54619 | 6.536 | 22.3074 | 3.3402 | 3.2923 | 86.1318 | 1.4788 | 0.80635 | 13.5694 | 6.3233 | 7.6326 | 24.6933 | 29.7096 | 5.2675 | 250.3736 | 704.6776 | 29 | 69517.6918 | 42100 | 0.55871 | 6.4612 | 22.052 | 2.2668 | 2.9239 | 85.675 | 0.73053 | 0.64684 | 13.5469 | 6.1066 | 7.4404 | 26.2011 | 30.7298 | 4.5287 | 253.1522 | 702.9789 | 383 | 949839.6495 | 553600 | 0.57674 | 6.1315 | 20.9269 | 2.1759 | 2.7824 | 86.7278 | 0.69384 | 0.5211 | 13.6666 | 5.986 | 7.6806 | 25.8276 | 30.1318 | 4.3042 | 254.1708 | 687.9119 | 174 | 424555.6217 | 251400 | 0.55437 | 7.6853 | 26.2301 | 3.3488 | 2.7823 | 88 | 1.5813 | 0.5297 | 14.0134 | 6.233 | 7.6342 | 25.8715 | 30.5221 | 4.5352 | 256.3105 | 717.5866 | 107 | 269080.0265 | 162700 | 0.58735 | 6.0385 | 20.6095 | 2.2552 | 3.4836 | 94.8833 | 0.61703 | 0.91882 | 14.1734 | 6.2941 | 7.8793 | 27.3536 | 32.3285 | 4.9749 | 252.5196 | 735.739 | 301 | 715630.8532 | 417900 | 0.5691 | 6.5574 | 22.3803 | 3.0307 | 2.745 | 81.0562 | 1.21 | 0.51646 | 13.5472 | 5.9716 | 7.5757 | 25.1259 | 30.0469 | 4.9209 | 254.6868 | 697.5918 | 3531884.0608 | 20999.8016 | 2029500 | 7300 | 1441 | 85.8989 | 0.57381
[6 empty] | 2025-03-01 |  |  |  |  | 2024-03-01
[6 empty] | 20.3458 | 65200 | 3204.5873 | 4.915 |  | 21.6542 | 61900 | 2858.5723 | 4.618
[6 empty] | 20.1625 | 61000 | 3025.4185 | 4.9597 |  | 22.1 | 63800 | 2886.8778 | 4.5249
[6 empty] | 19.05 | 59700 | 3133.8583 | 5.2493 |  | 23.05 | 67800 | 2941.4317 | 4.3384
[6 empty] | 19.6542 | 61300 | 3118.9315 | 5.088 |  | 19.8208 | 50500 | 2547.8243 | 5.0452
[6 empty] | 19.1375 | 58600 | 3062.0509 | 5.2253 |  | 18.3375 | 45400 | 2475.801 | 5.4533
[6 empty] | 17.7875 | 51900 | 2917.7793 | 5.6219 |  | 16.9125 | 40400 | 2388.7657 | 5.9128
[6 empty] | 16.75 | 48700 | 2907.4627 | 5.9701 |  | 16.7 | 38700 | 2317.3653 | 5.988
[6 empty] | 17.3292 | 49800 | 2873.7677 | 5.7706 |  | 17.9667 | 43900 | 2443.4137 | 5.5659
[6 empty] | 20.3375 | 60300 | 2964.9662 | 4.917 |  | 17.1083 | 45100 | 2636.1422 | 5.8451
[6 empty] | 21.2583 | 63200 | 2972.9518 | 4.704 |  | 17.925 | 46900 | 2616.4575 | 5.5788
[6 empty] | 20.1833 | 59400 | 2943.0223 | 4.9546 |  | 18.2708 | 46600 | 2550.5131 | 5.4732
[6 empty] | 21.2917 | 65500 | 3076.3209 | 4.6967 |  | 18.5208 | 50600 | 2732.0585 | 5.3993
[6 empty] | 21.7417 | 66000 | 3035.6458 | 4.5995 |  | 20.5 | 55000 | 2682.9268 | 4.878
[6 empty] | 24.2167 | 74000 | 3055.7467 | 4.1294 |  | 21 | 56000 | 2666.6667 | 4.7619
[6 empty] | 22.8583 | 74700 | 3267.9548 | 4.3748 |  | 21.5 | 55100 | 2562.7907 | 4.6512
[6 empty] | 21.5417 | 68900 | 3198.4526 | 4.6422 |  | 20.8 | 52900 | 2543.2692 | 4.8077
[6 empty] | 22.3208 | 69400 | 3109.2029 | 4.4801 |  | 21.3 | 55200 | 2591.5493 | 4.6948
[6 empty] | 22.2 | 65800 | 2963.964 | 4.5045 |  | 22.1 | 60700 | 2746.6063 | 4.5249
[6 empty] | 21.8625 | 67900 | 3105.7747 | 4.574 |  | 22.9 | 62400 | 2724.8908 | 4.3668
[6 empty] | 21.8458 | 65100 | 2979.9733 | 4.5775 |  | 21.3958 | 59200 | 2766.8939 | 4.6738
[6 empty] | 20.7125 | 60700 | 2930.5975 | 4.828 |  | 18.2 | 49200 | 2703.2967 | 5.4945
[6 empty] | 20.7917 | 59800 | 2876.1523 | 4.8096 |  | 18.9 | 51000 | 2698.4127 | 5.291
[6 empty] | 22.7583 | 69800 | 3067.0084 | 4.394 |  | 24 | 394700 | 16445.8333 | 4.1667
[6 empty] | 24.3625 | 79600 | 3267.3166 | 4.1047 |  | 23.6 | 70100 | 2970.339 | 4.2373
[6 empty] | 23.7667 | 78200 | 3290.3226 | 4.2076 |  | 23.475 | 72100 | 3071.3525 | 4.2599
[6 empty] | 24.325 | 82600 | 3395.6835 | 4.111 |  | 23.6792 | 74200 | 3133.5562 | 4.2231
[6 empty] | 23.5667 | 76100 | 3229.1372 | 4.2433 |  | 24.3 | 74200 | 3053.4979 | 4.1152
[6 empty] | 22.5958 | 68800 | 3044.8091 | 4.4256 |  | 24.7 | 72500 | 2935.2227 | 4.0486
[6 empty] | 20.5625 | 60800 | 2956.8389 | 4.8632 |  | 24.3917 | 72800 | 2984.6259 | 4.0998
[6 empty] | 21.2125 | 61600 | 2903.9481 | 4.7142 |  | 24.3333 | 71600 | 2942.4658 | 4.1096
[6 empty] | 22.625 | 67800 | 2996.6851 | 4.4199 |  | 23.8417 | 71300 | 2990.5627 | 4.1943
[7 empty] | 0 |  |  |  | 22.9167 | 66700 | 2910.5455 | 4.3636
[6 empty] | 21.263 |  |  | 4.7444 |  | 21.0737 |  |  | 4.8175
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100

## 01-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 01/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.9 | 1.7 | 2 | 1.7 | 1.6 | 1.5 | 1.7 | 1.9 | 1.8 | 2 | 1.8 | 1.8 | 2.1 | 1.9 | 1.8 | 1.8 | 1.9 | 1.8 | [6 empty] | 1.8167
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 1.1 | 1.3 | 0.9 | 1 | 1.2 | 0.9 | 0.9 | 0.8 | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.8 | 0.8 | [6 empty] | 0.86111
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.7 | 13.1 | 12.8 | 12.6 | 12.6 | 12.6 | 12.9 | 13.3 | 13.5 | 13.6 | 13.9 | 13.9 | 13.8 | 13.6 | 13.4 | 13.3 | 13.1 | 12.7 | [6 empty] | 13.2444
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.4 | 5.7 | 5.5 | 5.4 | 5.4 | 5.5 | 5.7 | 5.6 | 5.4 | 5.7 | 5.7 | 5.7 | 5.6 | 5.4 | 5.3 | 5.4 | 5.6 | 5.6 | [6 empty] | 5.5889
| Evaporator Delta "T" |  |  | 7.3 | 7.4 | 7.3 | 7.2 | 7.2 | 7.1 | 7.2 | 7.7 | 8.1 | 7.9 | 8.2 | 8.2 | 8.2 | 8.2 | 8.1 | 7.9 | 7.5 | 7.1 | [6 empty] | 7.6556
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.7 | 24.2 | 23.8 | 25.1 | 26.4 | 27.2 | 28.5 | 28.6 | 28.2 | 28.2 | 27.9 | 27.7 | 27.2 | 27.2 | 27.1 | 26.3 | 26.3 | 26 | [6 empty] | 26.6444
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.9 | 29.3 | 29.1 | 30.2 | 31.5 | 32.5 | 33.9 | 34 | 33.9 | 34.1 | 33.7 | 33.3 | 32.7 | 32.9 | 32.6 | 32.1 | 31.5 | 31.1 | [6 empty] | 32.0722
| Condenser Delta "T" | ºC |  | 5.2 | 5.1 | 5.3 | 5.1 | 5.1 | 5.3 | 5.4 | 5.4 | 5.7 | 5.9 | 5.8 | 5.6 | 5.5 | 5.7 | 5.5 | 5.8 | 5.2 | 5.1 | [6 empty] | 5.4278
| Evaporator pressure (Kpag) | kpag |  | 253.7 | 242 | 243.4 | 240.6 | 242 | 239.9 | 243.4 | 246.1 | 245.5 | 248.9 | 247.5 | 246.1 | 246.1 | 243.4 | 243.4 | 245.5 | 243.4 | 242.7 | [6 empty] | 244.6444
| Condenser pressure (kpag) | kpag |  | 690.9 | 691.5 | 686 | 714.3 | 740.5 | 764.6 | 798.4 | 803.2 | 803.9 | 803.2 | 805.3 | 795 | 780.5 | 781.9 | 779.8 | 758.4 | 744.6 | 735.7 | [6 empty] | 759.8722
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | [6 empty] | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | [6 empty] | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [6 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [6 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [6 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [6 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [6 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2344.0146 | 2376.1243 | 2344.0146 | 2311.9048 | 2311.9048 | 2279.795 | 2311.9048 | 2472.4537 | 2600.8929 | 2536.6733 | 2633.0026 | 2633.0026 | 2633.0026 | 2633.0026 | 2600.8929 | 2536.6733 | 2408.2341 | 2279.795 | [6 empty] | 44247.2884
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1200 | 1400 | 1300 | 1400 | 1500 | 1500 | 1500 | 1600 | 1600 | 1600 | 1400 | 1500 | 1600 | 1400 | 1400 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 25500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.5546 | 0.54711 | 0.51194 | 0.60556 | 0.56231 | 0.61409 | 0.64882 | 0.60668 | 0.57673 | 0.63075 | 0.60767 | 0.60767 | 0.53171 | 0.56969 | 0.61517 | 0.5519 | 0.58134 | 0.43864 | [6 empty] | 0.57569
17 | Average iKW/TR |  |  | Hours 7: 0.57569 | 0.57569
18 | COP of chiller |  |  | 6.3397 | 6.4265 | 6.868 | 5.8062 | 6.2528 | 5.7255 | 5.4191 | 5.7954 | 6.0965 | 5.5743 | 5.786 | 5.786 | 6.6126 | 6.1718 | 5.7155 | 6.3707 | 6.0481 | 8.0158 | [6 empty] | 6.1561
19 | EER of Chiller |  |  | 21.6373 | 21.9337 | 23.4404 | 19.8165 | 21.3409 | 19.5413 | 18.4954 | 19.7798 | 20.8073 | 19.0252 | 19.7477 | 19.7477 | 22.5688 | 21.0642 | 19.5069 | 21.7431 | 20.6422 | 27.3578 | [6 empty] | 21.0109
20 | LMTD of Condenser | ºC |  | 3.9447 | 3.6789 | 4.0935 | 3.6789 | 3.5612 | 3.5065 | 3.7776 | 4.0118 | 3.9941 | 4.2949 | 4.0268 | 3.9613 | 4.2761 | 4.1117 | 3.9283 | 4.0268 | 3.9447 | 3.7954 | [6 empty] | 3.9229
21 | LMTD of Evaporator | ºC |  | 2.832 | 3.619 | 3.8637 | 3.2769 | 3.4218 | 3.6713 | 3.2769 | 3.4114 | 3.3621 | 3.1494 | 3.2249 | 3.2249 | 3.3879 | 3.3879 | 3.3621 | 3.1494 | 3.206 | 3.1004 | [6 empty] | 3.3293
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.8 | 0.6 | 0.6 | 0.5 | 0.6 | 0.7 | 0.7 | 0.6 | 0.7 | 0.6 | 0.7 | 0.7 | 0.8 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.67917
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.5 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.6 | 0.5 | 0.6 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.49583
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.9 | 13.1 | 12.8 | 12.7 | 12.7 | 12.5 | 12.9 | 13.2 | 13.6 | 13.6 | 13.8 | 13.7 | 13.8 | 13.5 | 13.3 | 13.3 | 12.8 | 12.6 | 12.2 | 13 | 14.1 | 14.7 | 15.2 | 15.5 | 13.4375
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 5.7 | 5.5 | 5.5 | 5.7 | 5.4 | 5.6 | 5.9 | 6 | 6.1 | 6.2 | 6.2 | 6 | 6 | 5.8 | 5.7 | 5.5 | 5.6 | 5.6 | 5.6 | 5.7 | 6.2 | 6.5 | 6.6 | 5.8708
| Evaporator Delta "T" |  |  | 7.6 | 7.4 | 7.3 | 7.2 | 7 | 7.1 | 7.3 | 7.3 | 7.6 | 7.5 | 7.6 | 7.5 | 7.8 | 7.5 | 7.5 | 7.6 | 7.3 | 7 | 6.6 | 7.4 | 8.4 | 8.5 | 8.7 | 8.9 | 7.5667
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.2 | 24.4 | 24.3 | 25.5 | 26.8 | 27.6 | 29 | 28.9 | 28.6 | 28.6 | 28.6 | 27.8 | 27.4 | 27.7 | 27.6 | 27.1 | 26.8 | 26.3 | 26.2 | 23.1 | 23.1 | 23.7 | 24.1 | 23.8 | 26.3
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.5 | 28.6 | 28.3 | 29.7 | 30.8 | 31.8 | 33.2 | 33.2 | 32.9 | 33.1 | 32.9 | 32.6 | 31.8 | 31.9 | 31.9 | 31.4 | 31.1 | 30.6 | 29.9 | 27.1 | 27.8 | 28.5 | 29.1 | 29.1 | 30.6583
| Condenser Delta "T" | ºC |  | 4.3 | 4.2 | 4 | 4.2 | 4 | 4.2 | 4.2 | 4.3 | 4.3 | 4.5 | 4.3 | 4.8 | 4.4 | 4.2 | 4.3 | 4.3 | 4.3 | 4.3 | 3.7 | 4 | 4.7 | 4.8 | 5 | 5.3 | 4.3583
| Evaporator pressure (Kpag) | kpag |  | 259.2 | 252.3 | 249.6 | 248.9 | 250.3 | 247.5 | 248.9 | 253 | 254.4 | 255.8 | 257.2 | 257.2 | 254.4 | 253.7 | 253 | 251 | 248.2 | 248.9 | 250.3 | 250.3 | 249.6 | 256.5 | 259.2 | 259.9 | 252.8875
| Condenser pressure (kpag) | kpag |  | 651.6 | 649.5 | 650.2 | 675.7 | 697.1 | 723.3 | 757.7 | 757 | 752.2 | 753.6 | 752.9 | 741.9 | 730.2 | 728.8 | 727.4 | 715 | 706.7 | 697.1 | 682.6 | 624 | 639.1 | 653.6 | 666.7 | 698.4 | 701.3458
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2376.1243 | 2344.0146 | 2311.9048 | 2247.6852 | 2279.795 | 2344.0146 | 2344.0146 | 2440.3439 | 2408.2341 | 2440.3439 | 2408.2341 | 2504.5635 | 2408.2341 | 2408.2341 | 2440.3439 | 2344.0146 | 2247.6852 | 2119.246 | 2376.1243 | 2697.2222 | 2729.332 | 2793.5516 | 2857.7712 | 58311.3757
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1300 | 1400 | 1300 | 1500 | 1500 | 1500 | 1400 | 1600 | 1500 | 1500 | 1400 | 1600 | 1500 | 1300 | 1400 | 1300 | 1300 | 1400 | 1400 | 1600 | 1500 | 1500 | 34300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53271 | 0.54711 | 0.5546 | 0.60556 | 0.57837 | 0.65795 | 0.63993 | 0.63993 | 0.57369 | 0.66439 | 0.61467 | 0.62286 | 0.55898 | 0.66439 | 0.62286 | 0.53271 | 0.59727 | 0.57837 | 0.61343 | 0.58919 | 0.51905 | 0.58622 | 0.53695 | 0.52488 | 0.58984
17 | Average iKW/TR |  |  | Hours 7: 0.58984 | 0.58984
18 | COP of chiller |  |  | 6.6002 | 6.4265 | 6.3397 | 5.8062 | 6.0791 | 5.3438 | 5.4944 | 5.4944 | 6.1287 | 5.2921 | 5.7202 | 5.6449 | 6.29 | 5.2921 | 5.6449 | 6.6002 | 5.8868 | 6.0791 | 5.7317 | 5.9675 | 6.7739 | 5.9977 | 6.5481 | 6.6986 | 5.995
19 | EER of Chiller |  |  | 22.5265 | 21.9337 | 21.6373 | 19.8165 | 20.748 | 18.2385 | 18.7523 | 18.7523 | 20.9174 | 18.0619 | 19.5229 | 19.266 | 21.4679 | 18.0619 | 19.266 | 22.5265 | 20.0917 | 20.748 | 19.5624 | 20.367 | 23.1193 | 20.4702 | 22.3486 | 22.8624 | 20.4611
20 | LMTD of Condenser | ºC |  | 2.1871 | 2.1584 | 2.1006 | 2.0198 | 1.9638 | 2.0198 | 2.2918 | 2.0476 | 2.0476 | 1.9543 | 2.0476 | 2.3285 | 2.2156 | 2.0198 | 2.1871 | 2.0476 | 2.1871 | 2.1871 | 2.1422 | 1.9638 | 2.4379 | 2.4667 | 2.524 | 2.609 | 2.1731
21 | LMTD of Evaporator | ºC |  | 2.5369 | 2.6811 | 2.4683 | 2.6332 | 2.5849 | 2.4222 | 2.4683 | 2.6572 | 2.7289 | 2.8816 | 2.7289 | 2.7051 | 2.9556 | 2.7051 | 2.8816 | 2.7289 | 2.6572 | 2.3991 | 2.4875 | 2.4912 | 2.9175 | 2.9408 | 3.1742 | 3.2222 | 2.7107
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1200
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## 02-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 02/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.8 | 0.7 | 0.8 | 0.8 | 0.8 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.8 | 0.8 | 0.72083
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.5 | 0.5 | 0.6 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.6 | 0.6 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.6 | 0.7 | 0.7 | 0.6 | 0.51667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.9 | 13.8 | 13.4 | 12.8 | 12.7 | 12.5 | 12.7 | 13 | 13.4 | 13.7 | 13.9 | 14.1 | 13.7 | 13.6 | 13.3 | 13.1 | 12.5 | 12.2 | 12.5 | 13.8 | 14.4 | 14.8 | 14.9 | 15.1 | 13.5333
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7 | 6.1 | 5.7 | 5.6 | 5.4 | 5.6 | 5.4 | 5.9 | 6 | 6.2 | 6.2 | 6.1 | 5.9 | 5.7 | 5.5 | 5.5 | 5.5 | 5.4 | 5.6 | 5.6 | 5.6 | 5.7 | 5.9 | 6 | 5.7958
| Evaporator Delta "T" |  |  | 7.9 | 7.7 | 7.7 | 7.2 | 7.3 | 6.9 | 7.3 | 7.1 | 7.4 | 7.5 | 7.7 | 8 | 7.8 | 7.9 | 7.8 | 7.6 | 7 | 6.8 | 6.9 | 8.2 | 8.8 | 9.1 | 9 | 9.1 | 7.7375
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26.8 | 27 | 26.6 | 26.6 | 26.5 | 26.2 | 28.3 | 28.9 | 28.3 | 27.9 | 28.2 | 27.8 | 27.1 | 27 | 26.7 | 26.4 | 25.9 | 25.3 | 22.1 | 21.7 | 21.3 | 21.3 | 21.4 | 21.9 | 25.7167
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.4 | 31.3 | 31.1 | 30.8 | 30.4 | 30.2 | 32.5 | 32.9 | 32.7 | 32.3 | 32.7 | 32.2 | 31.8 | 31.5 | 31.2 | 30.7 | 30 | 29.3 | 26.1 | 26.4 | 26.4 | 26.6 | 26.7 | 27.2 | 30.1833
| Condenser Delta "T" | ºC |  | 4.6 | 4.3 | 4.5 | 4.2 | 3.9 | 4 | 4.2 | 4 | 4.4 | 4.4 | 4.5 | 4.4 | 4.7 | 4.5 | 4.5 | 4.3 | 4.1 | 4 | 4 | 4.7 | 5.1 | 5.3 | 5.3 | 5.3 | 4.4667
| Evaporator pressure (Kpag) | kpag |  | 268.2 | 255.8 | 251 | 250.3 | 248.2 | 251.7 | 247.5 | 255.1 | 253.7 | 255.8 | 255.1 | 255.8 | 251.7 | 251 | 247.5 | 247.5 | 248.2 | 248.9 | 250.3 | 248.9 | 247.5 | 248.2 | 250.3 | 252.3 | 251.6875
| Condenser pressure (kpag) | kpag |  | 717.1 | 716.4 | 709.5 | 700.5 | 698.4 | 686 | 740.5 | 750.8 | 746.7 | 738.4 | 746 | 736.4 | 728.8 | 719.1 | 712.2 | 701.9 | 684 | 664 | 601.2 | 608.1 | 608.1 | 612.9 | 614.3 | 623.3 | 690.1917
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2472.4537 | 2472.4537 | 2311.9048 | 2344.0146 | 2215.5754 | 2344.0146 | 2279.795 | 2376.1243 | 2408.2341 | 2472.4537 | 2568.7831 | 2504.5635 | 2536.6733 | 2504.5635 | 2440.3439 | 2247.6852 | 2183.4656 | 2215.5754 | 2633.0026 | 2825.6614 | 2921.9907 | 2889.881 | 2921.9907 | 59627.877
15 | Power Consumption of Chiller | KWH |  | 1500 | 1400 | 1400 | 1500 | 1400 | 1300 | 1500 | 1500 | 1500 | 1500 | 1400 | 1700 | 1300 | 1600 | 1500 | 1400 | 1300 | 1200 | 1400 | 1400 | 1500 | 1500 | 1500 | 1600 | 34800
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.59133 | 0.56624 | 0.56624 | 0.64882 | 0.59727 | 0.58676 | 0.63993 | 0.65795 | 0.63128 | 0.62286 | 0.56624 | 0.66179 | 0.51905 | 0.63075 | 0.59891 | 0.57369 | 0.57837 | 0.54959 | 0.63189 | 0.53171 | 0.53085 | 0.51335 | 0.51905 | 0.54757 | 0.58589
17 | Average iKW/TR |  |  | Hours 7: 0.58589 | 0.58589
18 | COP of chiller |  |  | 5.946 | 6.2094 | 6.2094 | 5.4191 | 5.8868 | 5.9923 | 5.4944 | 5.3438 | 5.5696 | 5.6449 | 6.2094 | 5.3128 | 6.7739 | 5.5743 | 5.8707 | 6.1287 | 6.0791 | 6.3976 | 5.5643 | 6.6126 | 6.6234 | 6.8491 | 6.7739 | 6.4211 | 6.0378
19 | EER of Chiller |  |  | 20.2936 | 21.1927 | 21.1927 | 18.4954 | 20.0917 | 20.4516 | 18.7523 | 18.2385 | 19.0092 | 19.266 | 21.1927 | 18.1327 | 23.1193 | 19.0252 | 20.0367 | 20.9174 | 20.748 | 21.8349 | 18.9908 | 22.5688 | 22.6055 | 23.3761 | 23.1193 | 21.9151 | 20.6069
20 | LMTD of Condenser | ºC |  | 2.409 | 2.1871 | 2.3799 | 2.2918 | 2.2025 | 1.9638 | 2.0198 | 2.1006 | 2.0752 | 2.0752 | 2.244 | 2.3507 | 2.4379 | 2.3799 | 2.244 | 2.1871 | 2.2622 | 2.1006 | 2.1006 | 2.1574 | 2.4119 | 2.4669 | 2.609 | 2.609 | 2.2611
21 | LMTD of Evaporator | ºC |  | 2.9801 | 2.931 | 2.7527 | 2.6332 | 2.832 | 2.3759 | 2.4683 | 2.6091 | 2.4912 | 2.5141 | 2.931 | 3.0046 | 2.7764 | 2.9801 | 2.7764 | 2.7289 | 2.5849 | 2.3526 | 2.3759 | 2.4521 | 3.1982 | 3.4482 | 3.4236 | 3.2699 | 2.7871
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.7 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | [7 empty] | 0.64118
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 1 | 0.8 | 0.8 | 0.8 | 0.7 | 0.8 | 0.7 | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | [7 empty] | 0.81176
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.2 | 14 | 13.6 | 13.2 | 12.9 | 12.8 | 12.8 | 13.1 | 13.6 | 13.9 | 14 | 14.1 | 14 | 13.8 | 13.6 | 13.2 | 12.8 | [7 empty] | 13.5647
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.4 | 6.3 | 6 | 5.8 | 5.6 | 5.6 | 5.9 | 6.2 | 6.6 | 6.2 | 6.2 | 6.2 | 6 | 5.8 | 5.7 | 5.4 | 5.2 | [7 empty] | 6.0059
| Evaporator Delta "T" |  |  | 7.8 | 7.7 | 7.6 | 7.4 | 7.3 | 7.2 | 6.9 | 6.9 | 7 | 7.7 | 7.8 | 7.9 | 8 | 8 | 7.9 | 7.8 | 7.6 | [7 empty] | 7.5588
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26.7 | 27 | 26.8 | 26.6 | 26.6 | 26.3 | 28.2 | 29 | 28.4 | 28 | 28.2 | 27.9 | 27.4 | 27.1 | 26.8 | 26.4 | 26.1 | [7 empty] | 27.2647
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.7 | 31.7 | 31.4 | 31.2 | 31 | 30.8 | 32.6 | 33.3 | 32.7 | 32.9 | 33.2 | 32.7 | 32.4 | 32.1 | 31.6 | 31.3 | 30.7 | [7 empty] | 31.9588
| Condenser Delta "T" | ºC |  | 5 | 4.7 | 4.6 | 4.6 | 4.4 | 4.5 | 4.4 | 4.3 | 4.3 | 4.9 | 5 | 4.8 | 5 | 5 | 4.8 | 4.9 | 4.6 | [7 empty] | 4.6941
| Evaporator pressure (Kpag) | kpag |  | 266.1 | 255.1 | 251.7 | 248.2 | 246.1 | 244.8 | 251.7 | 253.7 | 259.9 | 252.3 | 252.3 | 252.3 | 250.3 | 246.8 | 245.5 | 242.7 | 242 | [7 empty] | 250.6765
| Condenser pressure (kpag) | kpag |  | 719.1 | 719.8 | 712.9 | 709.5 | 705.3 | 698.4 | 741.9 | 757.7 | 744.6 | 748.8 | 756.4 | 746 | 735.7 | 728.8 | 719.1 | 711.5 | 696.4 | [7 empty] | 726.5824
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | [7 empty] | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | [7 empty] | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2504.5635 | 2472.4537 | 2440.3439 | 2376.1243 | 2344.0146 | 2311.9048 | 2215.5754 | 2215.5754 | 2247.6852 | 2472.4537 | 2504.5635 | 2536.6733 | 2568.7831 | 2568.7831 | 2536.6733 | 2504.5635 | 2440.3439 | [7 empty] | 41261.078
15 | Power Consumption of Chiller | KWH |  | 1600 | 1500 | 1300 | 1400 | 1400 | 1400 | 1300 | 1400 | 1400 | 1600 | 1400 | 1600 | 1600 | 1400 | 1600 | 1400 | 1300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 24900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.63883 | 0.60668 | 0.53271 | 0.58919 | 0.59727 | 0.60556 | 0.58676 | 0.63189 | 0.62286 | 0.64713 | 0.55898 | 0.63075 | 0.62286 | 0.54501 | 0.63075 | 0.55898 | 0.53271 | [7 empty] | 0.59641
17 | Average iKW/TR |  |  | Hours 7: 0.59641 | 0.59641
18 | COP of chiller |  |  | 5.5038 | 5.7954 | 6.6002 | 5.9675 | 5.8868 | 5.8062 | 5.9923 | 5.5643 | 5.6449 | 5.4332 | 6.29 | 5.5743 | 5.6449 | 6.4513 | 5.5743 | 6.29 | 6.6002 | [7 empty] | 5.9188
19 | EER of Chiller |  |  | 18.7844 | 19.7798 | 22.5265 | 20.367 | 20.0917 | 19.8165 | 20.4516 | 18.9908 | 19.266 | 18.5436 | 21.4679 | 19.0252 | 19.266 | 22.0183 | 19.0252 | 21.4679 | 22.5265 | [7 empty] | 20.2009
20 | LMTD of Condenser | ºC |  | 2.7906 | 2.1574 | 2.1301 | 2.1301 | 2.2156 | 2.1027 | 2.0752 | 2.1871 | 2.0476 | 2.3564 | 2.2385 | 2.1846 | 2.2385 | 2.2385 | 2.1846 | 2.2116 | 2.1301 | [7 empty] | 2.2129
21 | LMTD of Evaporator | ºC |  | 3.4381 | 3.5593 | 3.2322 | 3.1797 | 3.1533 | 2.9709 | 3.0472 | 2.8933 | 2.757 | 3.0987 | 3.2843 | 3.3103 | 3.3363 | 3.4913 | 3.4647 | 3.4381 | 3.3847 | [7 empty] | 3.2376
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## 03-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 03/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.8 | 0.9 | 1 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.9 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.9 | 0.7 | 0.8 | 0.8 | 0.8 | 0.76667
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.6 | 0.5 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.5375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.2 | 15.4 | 14.2 | 13.4 | 12.8 | 12.9 | 12.8 | 13.1 | 13.7 | 13.9 | 13.8 | 13.6 | 13.6 | 13.4 | 13.3 | 13.2 | 12.9 | 12.6 | 12.4 | 12.4 | 13.6 | 14.4 | 14.9 | 15.2 | 13.6125
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6 | 6.7 | 6.1 | 5.7 | 5.6 | 5.5 | 5.5 | 5.6 | 5.9 | 5.9 | 5.7 | 5.7 | 5.5 | 5.6 | 5.6 | 5.5 | 5.5 | 5.7 | 5.6 | 5.6 | 5.6 | 5.7 | 6.2 | 6.3 | 5.7625
| Evaporator Delta "T" |  |  | 9.2 | 8.7 | 8.1 | 7.7 | 7.2 | 7.4 | 7.3 | 7.5 | 7.8 | 8 | 8.1 | 7.9 | 8.1 | 7.8 | 7.7 | 7.7 | 7.4 | 6.9 | 6.8 | 6.8 | 8 | 8.7 | 8.7 | 8.9 | 7.85
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.6 | 23.7 | 26.3 | 26.8 | 27.1 | 27.4 | 27.3 | 26.8 | 26.7 | 26.5 | 25.7 | 26 | 25.6 | 25.5 | 25.4 | 24.9 | 24.4 | 24.2 | 24.1 | 23.2 | 22.7 | 23.2 | 22.9 | 22.8 | 25.0333
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27 | 28.7 | 31.1 | 31.2 | 31.2 | 31.6 | 31.4 | 30.8 | 31 | 30.9 | 30.3 | 30.6 | 30.1 | 29.8 | 29.8 | 29.2 | 28.4 | 28.1 | 27.9 | 27.1 | 27.3 | 28.2 | 28.2 | 28.1 | 29.5
| Condenser Delta "T" | ºC |  | 5.4 | 5 | 4.8 | 4.4 | 4.1 | 4.2 | 4.1 | 4 | 4.3 | 4.4 | 4.6 | 4.6 | 4.5 | 4.3 | 4.4 | 4.3 | 4 | 3.9 | 3.8 | 3.9 | 4.6 | 5 | 5.3 | 5.3 | 4.4667
| Evaporator pressure (Kpag) | kpag |  | 251.7 | 262 | 253.7 | 250.3 | 250.3 | 248.2 | 247.5 | 250.3 | 252.3 | 252.3 | 249.6 | 249.6 | 247.5 | 248.9 | 248.9 | 249.6 | 248.9 | 251 | 250.3 | 250.3 | 250.3 | 250.3 | 255.1 | 256.5 | 251.0583
| Condenser pressure (kpag) | kpag |  | 620.5 | 652.9 | 707.4 | 712.9 | 712.2 | 719.8 | 717.7 | 705.3 | 706.7 | 704 | 690.9 | 697.7 | 690.9 | 684 | 682.6 | 666.7 | 654.3 | 644 | 639.1 | 619.1 | 624.7 | 648.1 | 644.7 | 644.7 | 674.6208
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2954.1005 | 2793.5516 | 2600.8929 | 2472.4537 | 2311.9048 | 2376.1243 | 2344.0146 | 2408.2341 | 2504.5635 | 2568.7831 | 2600.8929 | 2536.6733 | 2600.8929 | 2504.5635 | 2472.4537 | 2472.4537 | 2376.1243 | 2215.5754 | 2183.4656 | 2183.4656 | 2568.7831 | 2793.5516 | 2793.5516 | 2857.7712 | 60494.8413
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1500 | 1300 | 1500 | 1500 | 1300 | 1500 | 1600 | 1400 | 1500 | 1500 | 1400 | 1500 | 1400 | 1300 | 1400 | 1300 | 1100 | 1400 | 1400 | 1500 | 1500 | 1500 | 34400
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.50777 | 0.57275 | 0.57673 | 0.52579 | 0.64882 | 0.63128 | 0.5546 | 0.62286 | 0.63883 | 0.54501 | 0.57673 | 0.59133 | 0.53828 | 0.59891 | 0.56624 | 0.52579 | 0.58919 | 0.58676 | 0.50379 | 0.64118 | 0.54501 | 0.53695 | 0.53695 | 0.52488 | 0.57027
17 | Average iKW/TR |  |  | Hours 7: 0.57027 | 0.57027
18 | COP of chiller |  |  | 6.9244 | 6.1388 | 6.0965 | 6.687 | 5.4191 | 5.5696 | 6.3397 | 5.6449 | 5.5038 | 6.4513 | 6.0965 | 5.946 | 6.532 | 5.8707 | 6.2094 | 6.687 | 5.9675 | 5.9923 | 6.9792 | 5.4836 | 6.4513 | 6.5481 | 6.5481 | 6.6986 | 6.1994
19 | EER of Chiller |  |  | 23.633 | 20.9518 | 20.8073 | 22.8229 | 18.4954 | 19.0092 | 21.6373 | 19.266 | 18.7844 | 22.0183 | 20.8073 | 20.2936 | 22.2936 | 20.0367 | 21.1927 | 22.8229 | 20.367 | 20.4516 | 23.8198 | 18.7156 | 22.0183 | 22.3486 | 22.3486 | 22.8624 | 21.1585
20 | LMTD of Condenser | ºC |  | 2.6371 | 2.6591 | 2.7306 | 2.3507 | 2.1295 | 2.1584 | 2.1295 | 2.1006 | 2.1871 | 2.2156 | 2.2723 | 2.409 | 2.244 | 2.4515 | 2.2156 | 2.1871 | 2.2324 | 2.0715 | 2.0422 | 2.3298 | 2.2723 | 2.524 | 2.609 | 2.609 | 2.3237
21 | LMTD of Evaporator | ºC |  | 3.4727 | 3.3495 | 3.029 | 2.931 | 2.8071 | 2.4912 | 2.4683 | 2.7051 | 2.9556 | 3.0046 | 3.029 | 2.8 | 2.8472 | 2.9556 | 2.7527 | 2.931 | 2.8568 | 2.3759 | 2.3526 | 2.3526 | 2.6277 | 2.9873 | 3.1742 | 3.2222 | 2.8533
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.6; Hours 11: 0.6; Hours 12: 0.6; Hours 13: 0.6 | 0.66667
2 | Small temperature difference of evaporator | ºC |  | Hours 8: 0.9; Hours 9: 0.9; Hours 10: 0.9; Hours 11: 0.9; Hours 12: 0.8; Hours 13: 0.8 | 0.86667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 8: 15.5; Hours 9: 14.5; Hours 10: 13.6; Hours 11: 13.1; Hours 12: 12.9; Hours 13: 12.9 | 13.75
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 8: 6.9; Hours 9: 6.4; Hours 10: 5.7; Hours 11: 5.4; Hours 12: 5.4; Hours 13: 5.5 | 5.8833
| Evaporator Delta "T" |  |  | Hours 8: 8.6; Hours 9: 8.1; Hours 10: 7.9; Hours 11: 7.7; Hours 12: 7.5; Hours 13: 7.4 | 7.8667
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 8: 23.6; Hours 9: 26.2; Hours 10: 26.8; Hours 11: 27.1; Hours 12: 27.4; Hours 13: 27.3 | 26.4
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 8: 29.1; Hours 9: 31.3; Hours 10: 31.8; Hours 11: 31.9; Hours 12: 32; Hours 13: 32 | 31.35
| Condenser Delta "T" | ºC |  | Hours 8: 5.5; Hours 9: 5.1; Hours 10: 5; Hours 11: 4.8; Hours 12: 4.6; Hours 13: 4.7 | 4.95
| Evaporator pressure (Kpag) | kpag |  | Hours 8: 251.7; Hours 9: 252.3; Hours 10: 244.8; Hours 11: 243.4; Hours 12: 243.4; Hours 13: 244.1 | 246.6167
| Condenser pressure (kpag) | kpag |  | Hours 8: 658.4; Hours 9: 713.6; Hours 10: 721.9; Hours 11: 726.7; Hours 12: 729.5; Hours 13: 728.8 | 713.15
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 8: 4.2; Hours 9: 4.2; Hours 10: 4.2; Hours 11: 4.2; Hours 12: 4.2; Hours 13: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 8: 3.7; Hours 9: 3.7; Hours 10: 3.7; Hours 11: 3.7; Hours 12: 3.7; Hours 13: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 8: 3; Hours 9: 3; Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 8: 971; Hours 9: 971; Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 8: 2761.4418; Hours 9: 2600.8929; Hours 10: 2536.6733; Hours 11: 2472.4537; Hours 12: 2408.2341; Hours 13: 2376.1243 | 15155.8201
15 | Power Consumption of Chiller | KWH |  | 400 | 1600 | 1400 | 1400 | 1700 | 1400 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9100
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 8: 0.57941; Hours 9: 0.53828; Hours 10: 0.5519; Hours 11: 0.68758; Hours 12: 0.58134; Hours 13: 0.50502 | 0.57392
17 | Average iKW/TR |  |  | Hours 7: 0.57392 | 0.57392
18 | COP of chiller |  |  | Hours 8: 6.0683; Hours 9: 6.532; Hours 10: 6.3707; Hours 11: 5.1136; Hours 12: 6.0481; Hours 13: 6.962 | 6.1824
19 | EER of Chiller |  |  | Hours 8: 20.711; Hours 9: 22.2936; Hours 10: 21.7431; Hours 11: 17.4528; Hours 12: 20.6422; Hours 13: 23.7615 | 21.1007
20 | LMTD of Condenser | ºC |  | Hours 8: 2.6651; Hours 9: 2.5524; Hours 10: 2.2385; Hours 11: 2.1846; Hours 12: 2.1301; Hours 13: 2.1574 | 2.3214
21 | LMTD of Evaporator | ºC |  | Hours 8: 3.6492; Hours 9: 3.5178; Hours 10: 3.4647; Hours 11: 3.4114; Hours 12: 3.206; Hours 13: 3.1797 | 3.4048
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 15: 1.2; Hours 16: 1.2; Hours 17: 1.2; Hours 18: 1.3; Hours 19: 1; Hours 20: 1.2; Hours 21: 1.2; Hours 22: 1.1; Hours 23: 1.2; Hours 0: 1.1 | 1.17
2 | Small temperature difference of evaporator | ºC |  | Hours 15: 0.6; Hours 16: 0.7; Hours 17: 0.7; Hours 18: 0.6; Hours 19: 0.6; Hours 20: 0.6; Hours 21: 0.6; Hours 22: 0.6; Hours 23: 0.6; Hours 0: 0.6 | 0.62
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 15: 13.7; Hours 16: 13.6; Hours 17: 13.7; Hours 18: 13.5; Hours 19: 13.4; Hours 20: 13.3; Hours 21: 13.2; Hours 22: 13.1; Hours 23: 12.8; Hours 0: 12.5 | 13.28
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 15: 5.8; Hours 16: 5.8; Hours 17: 5.5; Hours 18: 6; Hours 19: 5.8; Hours 20: 6; Hours 21: 5.7; Hours 22: 5.9; Hours 23: 5.9; Hours 0: 5.9 | 5.83
| Evaporator Delta "T" |  |  | Hours 15: 7.9; Hours 16: 7.8; Hours 17: 8.2; Hours 18: 7.5; Hours 19: 7.6; Hours 20: 7.3; Hours 21: 7.5; Hours 22: 7.2; Hours 23: 6.9; Hours 0: 6.6 | 7.45
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 15: 26.6; Hours 16: 26.6; Hours 17: 25.7; Hours 18: 26.1; Hours 19: 25.7; Hours 20: 25.6; Hours 21: 25.6; Hours 22: 25; Hours 23: 24.6; Hours 0: 24.4 | 25.59
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 15: 31.8; Hours 16: 31.8; Hours 17: 31.3; Hours 18: 31.1; Hours 19: 30.9; Hours 20: 30.5; Hours 21: 30.6; Hours 22: 29.7; Hours 23: 29.3; Hours 0: 28.8 | 30.58
| Condenser Delta "T" | ºC |  | Hours 15: 5.2; Hours 16: 5.2; Hours 17: 5.6; Hours 18: 5; Hours 19: 5.2; Hours 20: 4.9; Hours 21: 5; Hours 22: 4.7; Hours 23: 4.7; Hours 0: 4.4 | 4.99
| Evaporator pressure (Kpag) | kpag |  | Hours 15: 249.6; Hours 16: 249.6; Hours 17: 246.8; Hours 18: 252.3; Hours 19: 250.3; Hours 20: 253; Hours 21: 248.2; Hours 22: 253; Hours 23: 253; Hours 0: 253 | 250.88
| Condenser pressure (kpag) | kpag |  | Hours 15: 741.2; Hours 16: 739.1; Hours 17: 726; Hours 18: 722.6; Hours 19: 715; Hours 20: 706.7; Hours 21: 711.5; Hours 22: 688.8; Hours 23: 676.4; Hours 0: 667.4 | 709.47
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2; Hours 18: 4.2; Hours 19: 4.2; Hours 20: 4.2; Hours 21: 4.2; Hours 22: 4.2; Hours 23: 4.2; Hours 0: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7; Hours 18: 3.7; Hours 19: 3.7; Hours 20: 3.7; Hours 21: 3.7; Hours 22: 3.7; Hours 23: 3.7; Hours 0: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 15: 2536.6733; Hours 16: 2504.5635; Hours 17: 2633.0026; Hours 18: 2408.2341; Hours 19: 2440.3439; Hours 20: 2344.0146; Hours 21: 2408.2341; Hours 22: 2311.9048; Hours 23: 2215.5754; Hours 0: 2119.246 | 23921.7923
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1400 | 1500 | 1600 | 1500 | 1500 | 1400 | 1500 | 1400 | 1300 | 1200 | 1300 | 700 | 0 | 0 | 0 | 0 | 1400 | 17800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 15: 0.59133; Hours 16: 0.63883; Hours 17: 0.56969; Hours 18: 0.62286; Hours 19: 0.57369; Hours 20: 0.63993; Hours 21: 0.58134; Hours 22: 0.56231; Hours 23: 0.54162; Hours 0: 0.61343 | 0.5935
17 | Average iKW/TR |  |  | Hours 7: 0.5935 | 0.5935
18 | COP of chiller |  |  | Hours 15: 5.946; Hours 16: 5.5038; Hours 17: 6.1718; Hours 18: 5.6449; Hours 19: 6.1287; Hours 20: 5.4944; Hours 21: 6.0481; Hours 22: 6.2528; Hours 23: 6.4916; Hours 0: 5.7317 | 5.9414
19 | EER of Chiller |  |  | Hours 15: 20.2936; Hours 16: 18.7844; Hours 17: 21.0642; Hours 18: 19.266; Hours 19: 20.9174; Hours 20: 18.7523; Hours 21: 20.6422; Hours 22: 21.3409; Hours 23: 22.156; Hours 0: 19.5624 | 20.2779
20 | LMTD of Condenser | ºC |  | Hours 15: 3.1064; Hours 16: 3.1064; Hours 17: 3.2284; Hours 18: 3.1682; Hours 19: 2.85; Hours 20: 3.0136; Hours 21: 3.0446; Hours 22: 2.827; Hours 23: 2.9511; Hours 0: 2.7339 | 3.003
21 | LMTD of Evaporator | ºC |  | Hours 15: 2.9801; Hours 16: 3.1241; Hours 17: 3.2249; Hours 18: 2.8816; Hours 19: 2.9064; Hours 20: 2.832; Hours 21: 2.8816; Hours 22: 2.8071; Hours 23: 2.7319; Hours 0: 2.656 | 2.9026

## 04-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 04/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.8 | 0.7 | 0.6 | 0.6 | 0.7 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.7 | 0.8 | 0.9 | 0.8 | 0.6 | 0.8 | 0.9 | 0.8 | [6 empty] | 0.75
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | [6 empty] | 0.51667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.8 | 13.5 | 13.1 | 13.3 | 13.3 | 12.8 | 12.8 | 13 | 13.3 | 13.7 | 14.1 | 14.2 | 14.5 | 14.2 | 13.9 | 13.8 | 13.2 | 12.6 | [6 empty] | 13.5611
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.4 | 6.6 | 6.6 | 6.5 | 5.6 | 5.4 | 5.5 | 5.6 | 5.7 | 5.9 | 6.1 | 6.1 | 6.2 | 6.1 | 5.8 | 5.7 | 5.5 | 5.6 | [6 empty] | 5.9389
| Evaporator Delta "T" |  |  | 8.4 | 6.9 | 6.5 | 6.8 | 7.7 | 7.4 | 7.3 | 7.4 | 7.6 | 7.8 | 8 | 8.1 | 8.3 | 8.1 | 8.1 | 8.1 | 7.7 | 7 | [6 empty] | 7.6222
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.3 | 23.7 | 23.7 | 23.8 | 23.7 | 24.3 | 24 | 26.1 | 26.8 | 27 | 26.7 | 26.9 | 26.6 | 26.1 | 25.7 | 25.2 | 24.6 | 24.2 | [6 empty] | 25.1889
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.1 | 27.7 | 27.2 | 27.6 | 27.9 | 28.3 | 27.9 | 30.2 | 31.1 | 31.3 | 31.2 | 31.6 | 31.3 | 30.7 | 30.3 | 29.8 | 29 | 27.9 | [6 empty] | 29.45
| Condenser Delta "T" | ºC |  | 4.8 | 4 | 3.5 | 3.8 | 4.2 | 4 | 3.9 | 4.1 | 4.3 | 4.3 | 4.5 | 4.7 | 4.7 | 4.6 | 4.6 | 4.6 | 4.4 | 3.7 | [6 empty] | 4.2611
| Evaporator pressure (Kpag) | kpag |  | 259.2 | 262 | 262 | 260.6 | 248.9 | 248.2 | 248.9 | 247.5 | 250.3 | 254.4 | 254.4 | 255.8 | 255.1 | 254.4 | 251.7 | 250.3 | 247.5 | 249.6 | [6 empty] | 253.3778
| Condenser pressure (kpag) | kpag |  | 665.3 | 631.6 | 622.6 | 630.2 | 642.6 | 647.4 | 639.1 | 690.9 | 708.1 | 715.7 | 712.9 | 721.2 | 714.3 | 701.9 | 692.9 | 680.5 | 664.7 | 640.5 | [6 empty] | 673.4667
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | [6 empty] | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | [6 empty] | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [6 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [6 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [6 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [6 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [6 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2697.2222 | 2215.5754 | 2087.1362 | 2183.4656 | 2472.4537 | 2376.1243 | 2344.0146 | 2376.1243 | 2440.3439 | 2504.5635 | 2568.7831 | 2600.8929 | 2665.1124 | 2600.8929 | 2600.8929 | 2600.8929 | 2472.4537 | 2247.6852 | [6 empty] | 44054.6296
15 | Power Consumption of Chiller | KWH |  | 1300 | 1200 | 1200 | 1300 | 1300 | 1300 | 1400 | 1400 | 1400 | 1600 | 1300 | 1700 | 1500 | 1500 | 1500 | 1500 | 1200 | 1300 | 600 | 0 | 0 | 0 | 0 | 0 | 25500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.48198 | 0.54162 | 0.57495 | 0.59538 | 0.52579 | 0.54711 | 0.59727 | 0.58919 | 0.57369 | 0.63883 | 0.50608 | 0.65362 | 0.56283 | 0.57673 | 0.57673 | 0.57673 | 0.48535 | 0.57837 | [6 empty] | 0.56568
17 | Average iKW/TR |  |  | Hours 7: 0.56568 | 0.56568
18 | COP of chiller |  |  | 7.2949 | 6.4916 | 6.1153 | 5.9054 | 6.687 | 6.4265 | 5.8868 | 5.9675 | 6.1287 | 5.5038 | 6.9476 | 5.3793 | 6.247 | 6.0965 | 6.0965 | 6.0965 | 7.2443 | 6.0791 | [6 empty] | 6.2552
19 | EER of Chiller |  |  | 24.8977 | 22.156 | 20.8716 | 20.1552 | 22.8229 | 21.9337 | 20.0917 | 20.367 | 20.9174 | 18.7844 | 23.7121 | 18.3594 | 21.3211 | 20.8073 | 20.8073 | 20.8073 | 24.7248 | 20.748 | [6 empty] | 21.3492
20 | LMTD of Condenser | ºC |  | 2.4667 | 2.1006 | 1.8212 | 1.9072 | 2.1584 | 2.2324 | 2.2025 | 2.1295 | 2.1871 | 2.3213 | 2.244 | 2.4379 | 2.5709 | 2.409 | 2.1301 | 2.409 | 2.4816 | 2.1422 | [6 empty] | 2.2418
21 | LMTD of Evaporator | ºC |  | 3.1019 | 2.7319 | 2.2825 | 2.3526 | 2.5597 | 2.4912 | 2.6572 | 2.4912 | 2.7289 | 2.7764 | 3.0046 | 3.029 | 3.0776 | 3.029 | 3.029 | 3.029 | 2.7527 | 2.5849 | [6 empty] | 2.7616
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.3 | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.1 | 1.1 | 1 | 1.2 | 0.8 | 1.3 | 0.9 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 1.3 | 1.3 | 1.3 | 1.1417
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.6 | 0.5 | 0.6 | 0.7 | 0.6 | 0.6 | 0.4 | 0.5 | 0.3 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.9 | 1.1 | 0.64167
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.8 | 13.4 | 13.1 | 13.2 | 13.2 | 12.8 | 12.6 | 12.8 | 13.2 | 13.6 | 14 | 14.1 | 14.3 | 14.1 | 13.8 | 13.7 | 13.3 | 12.4 | 12.2 | 11.9 | 12.9 | 13.8 | 14.2 | 14.4 | 13.4083
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 6.3 | 6.5 | 6.4 | 5.8 | 5.6 | 5.7 | 6.1 | 6.3 | 6.6 | 6.6 | 7.1 | 6.7 | 6.6 | 6.6 | 5.7 | 5.3 | 5.4 | 5.6 | 5.6 | 5.7 | 5.7 | 5.8 | 5.8 | 6.0875
| Evaporator Delta "T" |  |  | 8.2 | 7.1 | 6.6 | 6.8 | 7.4 | 7.2 | 6.9 | 6.7 | 6.9 | 7 | 7.4 | 7 | 7.6 | 7.5 | 7.2 | 8 | 8 | 7 | 6.6 | 6.3 | 7.2 | 8.1 | 8.4 | 8.6 | 7.3208
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.4 | 23.9 | 23.7 | 23.9 | 23.9 | 24.4 | 24.2 | 26.1 | 26.8 | 27.1 | 26.7 | 27 | 26.6 | 26.2 | 25.8 | 25.4 | 24.9 | 24.3 | 23.6 | 22.6 | 21.9 | 21.7 | 21.3 | 21.2 | 24.4833
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.9 | 28.6 | 27.9 | 28.3 | 28.7 | 29.2 | 28.6 | 30.6 | 31.4 | 31.7 | 31.7 | 31.9 | 31.8 | 31.2 | 30.8 | 30.7 | 29.9 | 28.8 | 27.8 | 26.6 | 26.6 | 26.9 | 26.8 | 26.8 | 29.3
| Condenser Delta "T" | ºC |  | 5.5 | 4.7 | 4.2 | 4.4 | 4.8 | 4.8 | 4.4 | 4.5 | 4.6 | 4.6 | 5 | 4.9 | 5.2 | 5 | 5 | 5.3 | 5 | 4.5 | 4.2 | 4 | 4.7 | 5.2 | 5.5 | 5.6 | 4.8167
| Evaporator pressure (Kpag) | kpag |  | 258.6 | 257.9 | 260.6 | 259.9 | 251.7 | 248.9 | 249.6 | 253.7 | 259.2 | 264.8 | 260.6 | 263.4 | 260.6 | 257.2 | 259.2 | 248.2 | 245.5 | 247.5 | 248.9 | 248.2 | 248.9 | 244.8 | 246.8 | 244.8 | 253.7292
| Condenser pressure (kpag) | kpag |  | 696.4 | 662.6 | 648.1 | 655 | 665.3 | 674.3 | 661.9 | 710.2 | 721.9 | 728.1 | 732.9 | 739.8 | 737 | 726.7 | 712.2 | 711.5 | 694.3 | 668.1 | 644.7 | 618.5 | 620.5 | 629.5 | 628.1 | 630.9 | 679.9375
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2633.0026 | 2279.795 | 2119.246 | 2183.4656 | 2376.1243 | 2311.9048 | 2215.5754 | 2151.3558 | 2215.5754 | 2247.6852 | 2376.1243 | 2247.6852 | 2440.3439 | 2408.2341 | 2311.9048 | 2568.7831 | 2568.7831 | 2247.6852 | 2119.246 | 2022.9167 | 2311.9048 | 2600.8929 | 2697.2222 | 2761.4418 | 56416.8981
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1300 | 1300 | 1200 | 1400 | 1300 | 1400 | 1300 | 1500 | 1500 | 1300 | 1600 | 1300 | 1500 | 1600 | 1300 | 1400 | 1200 | 1100 | 1500 | 1400 | 1500 | 1600 | 33100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.49373 | 0.57023 | 0.61343 | 0.59538 | 0.50502 | 0.60556 | 0.58676 | 0.65075 | 0.58676 | 0.66735 | 0.63128 | 0.57837 | 0.65565 | 0.53981 | 0.64882 | 0.62286 | 0.50608 | 0.62286 | 0.56624 | 0.54377 | 0.64882 | 0.53828 | 0.55613 | 0.57941 | 0.58806
17 | Average iKW/TR |  |  | Hours 7: 0.58806 | 0.58806
18 | COP of chiller |  |  | 7.1213 | 6.166 | 5.7317 | 5.9054 | 6.962 | 5.8062 | 5.9923 | 5.403 | 5.9923 | 5.2686 | 5.5696 | 6.0791 | 5.3627 | 6.5133 | 5.4191 | 5.6449 | 6.9476 | 5.6449 | 6.2094 | 6.466 | 5.4191 | 6.532 | 6.3223 | 6.0683 | 6.0228
19 | EER of Chiller |  |  | 24.3049 | 21.0445 | 19.5624 | 20.1552 | 23.7615 | 19.8165 | 20.4516 | 18.4404 | 20.4516 | 17.9816 | 19.0092 | 20.748 | 18.3027 | 22.2301 | 18.4954 | 19.266 | 23.7121 | 19.266 | 21.1927 | 22.0684 | 18.4954 | 22.2936 | 21.578 | 20.711 | 20.5558
20 | LMTD of Condenser | ºC |  | 3.3241 | 2.827 | 2.6711 | 2.7339 | 2.8578 | 2.9824 | 2.7339 | 2.7651 | 2.6701 | 2.9196 | 2.524 | 3.1366 | 2.7173 | 3.0446 | 3.0446 | 3.1371 | 3.0446 | 2.7651 | 2.6711 | 2.6077 | 2.827 | 3.2309 | 3.3241 | 3.355 | 2.9131
21 | LMTD of Evaporator | ºC |  | 3.2249 | 2.9451 | 2.656 | 2.5363 | 2.8568 | 2.9709 | 2.7319 | 2.6814 | 2.3759 | 2.5849 | 2.2803 | 2.9192 | 2.9064 | 3.0478 | 2.9709 | 3.1746 | 3.0046 | 2.757 | 2.656 | 2.5795 | 2.8071 | 3.3621 | 3.5969 | 3.9507 | 2.899

## 05-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 05/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 1.9 | 1.9 | 1.9 | 1.6 | 1.7 | 1.6 | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.7 | 1.6 | 1.7 | 1.6 | 1.7 | 1.5 | 1.8 | 1.9 | 1.9 | 2.1 | 2 | 1.7591
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.6 | 0.6 | 0.7 | 0.9 | 1.1 | 0.7 | 1.2 | 1.1 | 1.2 | 0.9 | 1.1 | 1 | 1 | 1 | 0.9 | 1.4 | 1.5 | 1.6 | 1.7 | 1.6 | 1.4 | 1.3 | 1.1136
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 14.8 | 13.9 | 13.2 | 12.6 | 12.5 | 12.3 | 13.3 | 13.2 | 13.1 | 12.9 | 12.8 | 12.8 | 12.8 | 12.7 | 12.3 | 12.1 | 13.2 | 14.1 | 14.3 | 14.5 | 14.4 | 14.4 | 13.2818
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 6.7 | 5.7 | 5.6 | 5.4 | 5.3 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.5 | 5.3 | 5.6 | 5.7 | 5.6 | 5.7 | 5.4 | 5.7 | 5.7 | 5.6227
| Evaporator Delta "T" |  |  |  |  | 8.1 | 8.2 | 7.6 | 7.2 | 7.2 | 6.7 | 7.7 | 7.6 | 7.5 | 7.3 | 7.2 | 7.2 | 7.2 | 7.2 | 7 | 6.5 | 7.5 | 8.5 | 8.6 | 9.1 | 8.7 | 8.7 | 7.6591
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 22.1 | 23.2 | 23.8 | 23.8 | 24.1 | 24.6 | 24.9 | 24.4 | 24.6 | 24.1 | 24.2 | 24.4 | 24.2 | 23.8 | 23.8 | 23.1 | 21.9 | 20.3 | 19.7 | 18.9 | 18.7 | 19.5 | 22.8227
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 27.8 | 28.9 | 29.1 | 28.7 | 29.1 | 29.4 | 30.4 | 29.9 | 29.8 | 29.4 | 29.2 | 29.5 | 29.3 | 28.9 | 28.4 | 27.9 | 27.3 | 26.4 | 25.7 | 25.1 | 24.8 | 25.4 | 28.2
| Condenser Delta "T" | ºC |  |  |  | 5.7 | 5.7 | 5.3 | 4.9 | 5 | 4.8 | 5.5 | 5.5 | 5.2 | 5.3 | 5 | 5.1 | 5.1 | 5.1 | 4.6 | 4.8 | 5.4 | 6.1 | 6 | 6.2 | 6.1 | 5.9 | 5.3773
| Evaporator pressure (Kpag) | kpag |  |  |  | 261.3 | 246.8 | 246.1 | 243.4 | 241.3 | 242 | 241.3 | 242 | 237.9 | 239.9 | 241.3 | 240.6 | 243.4 | 239.9 | 239.2 | 236.5 | 240.6 | 235.8 | 239.2 | 235.8 | 237.9 | 239.9 | 241.4591
| Condenser pressure (kpag) | kpag |  |  |  | 659.1 | 686.7 | 684.6 | 678.4 | 685.3 | 690.9 | 714.3 | 699.1 | 701.9 | 692.9 | 688.1 | 695.7 | 686.7 | 679.8 | 672.9 | 659.1 | 644.7 | 633.6 | 624.7 | 611.6 | 601.9 | 618.5 | 668.6591
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2600.8929 | 2633.0026 | 2440.3439 | 2311.9048 | 2311.9048 | 2151.3558 | 2472.4537 | 2440.3439 | 2408.2341 | 2344.0146 | 2311.9048 | 2311.9048 | 2311.9048 | 2311.9048 | 2247.6852 | 2087.1362 | 2408.2341 | 2729.332 | 2761.4418 | 2921.9907 | 2793.5516 | 2793.5516 | 54104.9934
15 | Power Consumption of Chiller | KWH |  | 0 | 700 | 1400 | 1400 | 1300 | 1200 | 1300 | 1300 | 1300 | 1400 | 1200 | 1400 | 1300 | 1200 | 1300 | 1200 | 1200 | 1200 | 1400 | 1300 | 1600 | 1400 | 1300 | 1400 | 29700
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.53828 | 0.53171 | 0.53271 | 0.51905 | 0.56231 | 0.60427 | 0.52579 | 0.57369 | 0.49829 | 0.59727 | 0.56231 | 0.51905 | 0.56231 | 0.51905 | 0.53388 | 0.57495 | 0.58134 | 0.47631 | 0.57941 | 0.47913 | 0.46536 | 0.50115 | 0.53807
17 | Average iKW/TR |  |  | Hours 7: 0.53807 | 0.53807
18 | COP of chiller |  |  |  |  | 6.532 | 6.6126 | 6.6002 | 6.7739 | 6.2528 | 5.8186 | 6.687 | 6.1287 | 7.0561 | 5.8868 | 6.2528 | 6.7739 | 6.2528 | 6.7739 | 6.5857 | 6.1153 | 6.0481 | 7.3818 | 6.0683 | 7.3384 | 7.5555 | 7.0158 | 6.5687
19 | EER of Chiller |  |  |  |  | 22.2936 | 22.5688 | 22.5265 | 23.1193 | 21.3409 | 19.8588 | 22.8229 | 20.9174 | 24.0826 | 20.0917 | 21.3409 | 23.1193 | 21.3409 | 23.1193 | 22.4771 | 20.8716 | 20.6422 | 25.1941 | 20.711 | 25.0459 | 25.7869 | 23.9449 | 22.4189
20 | LMTD of Condenser | ºC |  |  |  | 4.1117 | 4.1117 | 3.9783 | 3.4955 | 3.6457 | 3.4625 | 3.8103 | 3.8103 | 3.7119 | 3.7448 | 3.7618 | 3.6789 | 3.5612 | 3.6789 | 3.396 | 3.579 | 3.5385 | 4.1242 | 4.2105 | 4.2758 | 4.4781 | 4.2949 | 3.8391
21 | LMTD of Evaporator | ºC |  |  |  | 3.029 | 3.0533 | 3.0733 | 3.2769 | 3.5627 | 2.8412 | 3.8428 | 3.675 | 3.786 | 3.3039 | 3.5627 | 3.4218 | 3.4218 | 3.4218 | 3.2225 | 3.7564 | 4.1858 | 4.6132 | 4.7738 | 4.7889 | 4.4027 | 4.2642 | 3.6945
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 9: 1.9; Hours 10: 1.9; Hours 11: 1.9; Hours 12: 1.7; Hours 13: 1.7 | 1.82
2 | Small temperature difference of evaporator | ºC |  | Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.6; Hours 12: 0.6; Hours 13: 0.6 | 0.68
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 9: 14.9; Hours 10: 14.2; Hours 11: 13.2; Hours 12: 12.7; Hours 13: 12.5 | 13.5
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 9: 6.7; Hours 10: 5.9; Hours 11: 5.4; Hours 12: 5.4; Hours 13: 5.6 | 5.8
| Evaporator Delta "T" |  |  | Hours 9: 8.2; Hours 10: 8.3; Hours 11: 7.8; Hours 12: 7.3; Hours 13: 6.9 | 7.7
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 9: 22.6; Hours 10: 23.6; Hours 11: 24.2; Hours 12: 24.2; Hours 13: 24.4 | 23.8
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 9: 27.4; Hours 10: 28.5; Hours 11: 28.8; Hours 12: 28.5; Hours 13: 28.6 | 28.36
| Condenser Delta "T" | ºC |  | Hours 9: 4.8; Hours 10: 4.9; Hours 11: 4.6; Hours 12: 4.3; Hours 13: 4.2 | 4.56
| Evaporator pressure (Kpag) | kpag |  | Hours 9: 258.6; Hours 10: 251; Hours 11: 246.1; Hours 12: 247.5; Hours 13: 248.2 | 250.28
| Condenser pressure (kpag) | kpag |  | Hours 9: 655.7; Hours 10: 678.4; Hours 11: 681.2; Hours 12: 671.5; Hours 13: 676.4 | 672.64
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 9: 4.2; Hours 10: 4.2; Hours 11: 4.2; Hours 12: 4.2; Hours 13: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 9: 3.7; Hours 10: 3.7; Hours 11: 3.7; Hours 12: 3.7; Hours 13: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 9: 3; Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 9: 0.5; Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 9: 971; Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 9: 2633.0026; Hours 10: 2665.1124; Hours 11: 2504.5635; Hours 12: 2344.0146; Hours 13: 2215.5754 | 12362.2685
15 | Power Consumption of Chiller | KWH |  | 0 | 700 | 1400 | 1400 | 1500 | 1300 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7200
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 9: 0.53171; Hours 10: 0.52531; Hours 11: 0.59891; Hours 12: 0.5546; Hours 13: 0.40622 | 0.52335
17 | Average iKW/TR |  |  | Hours 7: 0.52335 | 0.52335
18 | COP of chiller |  |  | Hours 9: 6.6126; Hours 10: 6.6932; Hours 11: 5.8707; Hours 12: 6.3397; Hours 13: 8.6555 | 6.8343
19 | EER of Chiller |  |  | Hours 9: 22.5688; Hours 10: 22.844; Hours 11: 20.0367; Hours 12: 21.6373; Hours 13: 29.5413 | 23.3256
20 | LMTD of Condenser | ºC |  | Hours 9: 3.8088; Hours 10: 3.8429; Hours 11: 3.74; Hours 12: 3.4096; Hours 13: 3.3753 | 3.6353
21 | LMTD of Evaporator | ºC |  | Hours 9: 3.3879; Hours 10: 3.4136; Hours 11: 2.9556; Hours 12: 2.832; Hours 13: 2.7319 | 3.0642
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.4; Hours 8: 1.4; Hours 14: 1.3; Hours 15: 1.1; Hours 16: 1.1; Hours 17: 1.1; Hours 18: 1.1; Hours 19: 1.1; Hours 20: 1.1; Hours 21: 1; Hours 22: 1.1 | 1.1636
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 1; Hours 8: 1.1; Hours 14: 0.4; Hours 15: 0.4; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.4; Hours 19: 0.5; Hours 20: 0.4; Hours 21: 0.5; Hours 22: 0.5 | 0.56364
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 14.6; Hours 8: 14.6; Hours 14: 13.3; Hours 15: 13.2; Hours 16: 13.1; Hours 17: 13; Hours 18: 12.8; Hours 19: 12.8; Hours 20: 12.8; Hours 21: 12.7; Hours 22: 12.3 | 13.2
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 5.6; Hours 8: 5.7; Hours 14: 6; Hours 15: 5.6; Hours 16: 5.6; Hours 17: 5.5; Hours 18: 5.5; Hours 19: 5.6; Hours 20: 5.6; Hours 21: 5.4; Hours 22: 5.5 | 5.6
| Evaporator Delta "T" |  |  | Hours 7: 9; Hours 8: 8.9; Hours 14: 7.3; Hours 15: 7.6; Hours 16: 7.5; Hours 17: 7.5; Hours 18: 7.3; Hours 19: 7.2; Hours 20: 7.2; Hours 21: 7.3; Hours 22: 6.8 | 7.6
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 21.2; Hours 8: 21.8; Hours 14: 25.6; Hours 15: 25.1; Hours 16: 25.1; Hours 17: 24.8; Hours 18: 24.8; Hours 19: 24.9; Hours 20: 24.8; Hours 21: 24.6; Hours 22: 24.4 | 24.2818
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 27.2; Hours 8: 27.8; Hours 14: 30.1; Hours 15: 29.8; Hours 16: 29.7; Hours 17: 29.4; Hours 18: 29.2; Hours 19: 29.5; Hours 20: 29.3; Hours 21: 29; Hours 22: 28.7 | 29.0636
| Condenser Delta "T" | ºC |  | Hours 7: 6; Hours 8: 6; Hours 14: 4.5; Hours 15: 4.7; Hours 16: 4.6; Hours 17: 4.6; Hours 18: 4.4; Hours 19: 4.6; Hours 20: 4.5; Hours 21: 4.4; Hours 22: 4.3 | 4.7818
| Evaporator pressure (Kpag) | kpag |  | Hours 7: 241.3; Hours 8: 244.1; Hours 14: 254.4; Hours 15: 249.6; Hours 16: 250.3; Hours 17: 248.9; Hours 18: 249.6; Hours 19: 250.3; Hours 20: 250.3; Hours 21: 247.5; Hours 22: 247.5 | 248.5273
| Condenser pressure (kpag) | kpag |  | Hours 7: 639.1; Hours 8: 650.2; Hours 14: 695.7; Hours 15: 688.1; Hours 16: 685.3; Hours 17: 679.8; Hours 18: 675.7; Hours 19: 683.3; Hours 20: 678.4; Hours 21: 671.5; Hours 22: 664.7 | 673.8
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.2; Hours 8: 4.2; Hours 14: 4.2; Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2; Hours 18: 4.2; Hours 19: 4.2; Hours 20: 4.2; Hours 21: 4.2; Hours 22: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.7; Hours 8: 3.7; Hours 14: 3.7; Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7; Hours 18: 3.7; Hours 19: 3.7; Hours 20: 3.7; Hours 21: 3.7; Hours 22: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2889.881; Hours 8: 2857.7712; Hours 14: 2344.0146; Hours 15: 2440.3439; Hours 16: 2408.2341; Hours 17: 2408.2341; Hours 18: 2344.0146; Hours 19: 2311.9048; Hours 20: 2311.9048; Hours 21: 2344.0146; Hours 22: 2183.4656 | 26843.7831
15 | Power Consumption of Chiller | KWH |  | 1700 | 400 | 0 | 0 | 0 | 0 | 200 | 1400 | 1400 | 1300 | 1300 | 1400 | 1300 | 1400 | 1200 | 1300 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.58826; Hours 8: 0.13997; Hours 14: 0.59727; Hours 15: 0.57369; Hours 16: 0.53981; Hours 17: 0.53981; Hours 18: 0.59727; Hours 19: 0.56231; Hours 20: 0.60556; Hours 21: 0.51194; Hours 22: 0.59538 | 0.53193
17 | Average iKW/TR |  |  | Hours 7: 0.53193 | 0.53193
18 | COP of chiller |  |  | Hours 7: 5.977; Hours 8: 25.1198; Hours 14: 5.8868; Hours 15: 6.1287; Hours 16: 6.5133; Hours 17: 6.5133; Hours 18: 5.8868; Hours 19: 6.2528; Hours 20: 5.8062; Hours 21: 6.868; Hours 22: 5.9054 | 7.8962
19 | EER of Chiller |  |  | Hours 7: 20.3993; Hours 8: 85.7339; Hours 14: 20.0917; Hours 15: 20.9174; Hours 16: 22.2301; Hours 17: 22.2301; Hours 18: 20.0917; Hours 19: 21.3409; Hours 20: 19.8165; Hours 21: 23.4404; Hours 22: 20.1552 | 26.9497
20 | LMTD of Condenser | ºC |  | Hours 7: 3.6036; Hours 8: 3.6036; Hours 14: 3.009; Hours 15: 2.827; Hours 16: 2.7961; Hours 17: 2.7961; Hours 18: 2.7339; Hours 19: 2.7961; Hours 20: 2.7651; Hours 21: 2.6091; Hours 22: 2.7026 | 2.9311
21 | LMTD of Evaporator | ºC |  | Hours 7: 3.9087; Hours 8: 4.0321; Hours 14: 2.4683; Hours 15: 2.5369; Hours 16: 2.7051; Hours 17: 2.7051; Hours 18: 2.4683; Hours 19: 2.6332; Hours 20: 2.4453; Hours 21: 2.6572; Hours 22: 2.5363 | 2.8269

## 06-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 06/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.4 | 2.1 | 2.2 | 2 | 1.9 | 1.8 | 1.7 | 1.5 | 1.8 | 1.6 | 1.7 | 1.7 | 1.6 | 1.6 | 1.7 | 1.7 | 1.6 | 1.6 | 1.8 | 1.9 | 2.1 | 2 | 2.1 | 2 | 1.8375
2 | Small temperature difference of evaporator | ºC |  | 1.5 | 1.4 | 1.5 | 1.3 | 1.4 | 1.6 | 1.3 | 0.9 | 1.1 | 1.2 | 1.4 | 1.2 | 1.1 | 1.3 | 1.1 | 1.5 | 1.2 | 1.3 | 2.2 | 1.7 | 1.7 | 1.2 | 1.2 | 1.3 | 1.3583
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.6 | 14.6 | 14.8 | 15.1 | 13.5 | 12.8 | 12.7 | 12.6 | 12.6 | 12.7 | 12.7 | 12.9 | 12.7 | 12.6 | 12.7 | 12.5 | 12.3 | 11.9 | 13.1 | 13.8 | 14.4 | 14.4 | 14.5 | 14.7 | 13.3833
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.6 | 5.7 | 6.6 | 6.4 | 6.1 | 5.6 | 5.6 | 5.6 | 5.5 | 5.7 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.4 | 5.7 | 5.7 | 5.8 | 5.9 | 5.9 | 5.7042
| Evaporator Delta "T" |  |  | 9 | 9 | 9.1 | 8.5 | 7.1 | 6.7 | 7.1 | 7 | 7 | 7.2 | 7 | 7.4 | 7.2 | 7.1 | 7.2 | 7 | 6.8 | 6.4 | 7.7 | 8.1 | 8.7 | 8.6 | 8.6 | 8.8 | 7.6792
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 18.9 | 18.6 | 18.9 | 21.2 | 22.3 | 22.7 | 23.6 | 23.7 | 23.2 | 23.2 | 22.7 | 22.8 | 23 | 23.5 | 23.4 | 22.4 | 22 | 20.7 | 20.7 | 20.6 | 20.3 | 20.5 | 20.6 | 20.4 | 21.6625
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 24.7 | 24.8 | 25.2 | 27.2 | 27.3 | 27.6 | 28.5 | 28.8 | 27.9 | 28.2 | 27.8 | 27.7 | 28.1 | 28.5 | 28.3 | 27.4 | 26.9 | 25.4 | 26.1 | 26.5 | 26.3 | 26.3 | 26.7 | 26.4 | 27.025
| Condenser Delta "T" | ºC |  | 5.8 | 6.2 | 6.3 | 6 | 5 | 4.9 | 4.9 | 5.1 | 4.7 | 5 | 5.1 | 4.9 | 5.1 | 5 | 4.9 | 5 | 4.9 | 4.7 | 5.4 | 5.9 | 6 | 5.8 | 6.1 | 6 | 5.3625
| Evaporator pressure (Kpag) | kpag |  | 237.2 | 236.5 | 242 | 252.3 | 248.2 | 243.4 | 242.7 | 239.9 | 242.7 | 242 | 238.6 | 241.3 | 240.6 | 240.6 | 242 | 239.9 | 237.2 | 233.7 | 230.3 | 239.2 | 243.4 | 243.4 | 244.8 | 245.5 | 241.1417
| Condenser pressure (kpag) | kpag |  | 608.8 | 603.3 | 610.2 | 648.1 | 646.7 | 650.2 | 672.2 | 676.4 | 661.9 | 664.7 | 656.4 | 660.5 | 662.6 | 672.2 | 668.8 | 652.2 | 637.1 | 604.7 | 626 | 634.3 | 634.3 | 636.4 | 640.5 | 639.1 | 644.4833
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2889.881 | 2889.881 | 2921.9907 | 2729.332 | 2279.795 | 2151.3558 | 2279.795 | 2247.6852 | 2247.6852 | 2311.9048 | 2247.6852 | 2376.1243 | 2311.9048 | 2279.795 | 2311.9048 | 2247.6852 | 2183.4656 | 2055.0265 | 2472.4537 | 2600.8929 | 2793.5516 | 2761.4418 | 2761.4418 | 2825.6614 | 59178.3399
15 | Power Consumption of Chiller | KWH |  | 1500 | 1400 | 1400 | 1400 | 1100 | 1200 | 1200 | 1300 | 1100 | 1300 | 1300 | 1200 | 1200 | 1200 | 1300 | 1100 | 1200 | 1100 | 1300 | 1400 | 1400 | 1400 | 1500 | 1300 | 30800
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.51905 | 0.48445 | 0.47913 | 0.51295 | 0.4825 | 0.55779 | 0.52636 | 0.57837 | 0.48939 | 0.56231 | 0.57837 | 0.50502 | 0.51905 | 0.52636 | 0.56231 | 0.48939 | 0.54959 | 0.53527 | 0.52579 | 0.53828 | 0.50115 | 0.50698 | 0.54319 | 0.46007 | 0.52221
17 | Average iKW/TR |  |  | Hours 7: 0.52221 | 0.52221
18 | COP of chiller |  |  | 6.7739 | 7.2577 | 7.3384 | 6.8545 | 7.2871 | 6.3035 | 6.6798 | 6.0791 | 7.1844 | 6.2528 | 6.0791 | 6.962 | 6.7739 | 6.6798 | 6.2528 | 7.1844 | 6.3976 | 6.5686 | 6.687 | 6.532 | 7.0158 | 6.9352 | 6.4728 | 7.6423 | 6.7581
19 | EER of Chiller |  |  | 23.1193 | 24.7706 | 25.0459 | 23.3945 | 24.8707 | 21.5138 | 22.7982 | 20.748 | 24.5204 | 21.3409 | 20.748 | 23.7615 | 23.1193 | 22.7982 | 21.3409 | 24.5204 | 21.8349 | 22.4187 | 22.8229 | 22.2936 | 23.9449 | 23.6697 | 22.0917 | 26.0833 | 23.0654
20 | LMTD of Condenser | ºC |  | 4.7206 | 4.5113 | 4.6611 | 4.3281 | 3.877 | 3.7282 | 3.6124 | 3.4422 | 3.6604 | 3.5284 | 3.6789 | 3.6124 | 3.5612 | 3.5284 | 3.6124 | 3.6457 | 3.4955 | 3.4293 | 3.8953 | 4.1777 | 4.4447 | 4.2616 | 4.4781 | 4.3281 | 3.9258
21 | LMTD of Evaporator | ºC |  | 4.6251 | 4.488 | 4.6538 | 4.2079 | 3.9366 | 4.0699 | 3.8052 | 3.2225 | 3.506 | 3.7001 | 3.9068 | 3.7574 | 3.5627 | 3.8052 | 3.5627 | 4.0355 | 3.5844 | 3.5978 | 5.1194 | 4.6239 | 4.8035 | 4.0951 | 4.0951 | 4.2923 | 4.044
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 10: 1.4; Hours 11: 1.1; Hours 12: 1.2; Hours 13: 0.9; Hours 14: 1.1; Hours 15: 0.9; Hours 16: 1; Hours 17: 1.1; Hours 18: 1.1; Hours 19: 1.1; Hours 20: 1.1; Hours 21: 1; Hours 22: 1.1 | 1.0846
2 | Small temperature difference of evaporator | ºC |  | Hours 10: 0.9; Hours 11: 0.5; Hours 12: 0.4; Hours 13: 0.4; Hours 14: 0.5; Hours 15: 0.4; Hours 16: 0.4; Hours 17: 0.4; Hours 18: 0.5; Hours 19: 0.4; Hours 20: 0.4; Hours 21: 0.4; Hours 22: 0.4 | 0.46154
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 10: 13.8; Hours 11: 12.8; Hours 12: 12.7; Hours 13: 12.6; Hours 14: 12.6; Hours 15: 12.7; Hours 16: 12.7; Hours 17: 12.8; Hours 18: 12.7; Hours 19: 12.7; Hours 20: 12.7; Hours 21: 12.5; Hours 22: 12.3 | 12.7385
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 10: 6.4; Hours 11: 6; Hours 12: 5.6; Hours 13: 5.5; Hours 14: 5.6; Hours 15: 5.6; Hours 16: 5.5; Hours 17: 5.5; Hours 18: 5.5; Hours 19: 5.5; Hours 20: 5.5; Hours 21: 5.5; Hours 22: 5.4 | 5.6231
| Evaporator Delta "T" |  |  | Hours 10: 7.4; Hours 11: 6.8; Hours 12: 7.1; Hours 13: 7.1; Hours 14: 7; Hours 15: 7.1; Hours 16: 7.2; Hours 17: 7.3; Hours 18: 7.2; Hours 19: 7.2; Hours 20: 7.2; Hours 21: 7; Hours 22: 6.9 | 7.1154
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 10: 22.8; Hours 11: 23.1; Hours 12: 24.2; Hours 13: 24.4; Hours 14: 24; Hours 15: 23.9; Hours 16: 23.6; Hours 17: 23.6; Hours 18: 23.6; Hours 19: 24.1; Hours 20: 24.1; Hours 21: 23.5; Hours 22: 22.7 | 23.6615
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 10: 27.4; Hours 11: 27.3; Hours 12: 28.4; Hours 13: 28.9; Hours 14: 28.2; Hours 15: 28.3; Hours 16: 27.8; Hours 17: 27.9; Hours 18: 28; Hours 19: 28.4; Hours 20: 28.4; Hours 21: 27.7; Hours 22: 26.8 | 27.9615
| Condenser Delta "T" | ºC |  | Hours 10: 4.6; Hours 11: 4.2; Hours 12: 4.2; Hours 13: 4.5; Hours 14: 4.2; Hours 15: 4.4; Hours 16: 4.2; Hours 17: 4.3; Hours 18: 4.4; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.2; Hours 22: 4.1 | 4.3
| Evaporator pressure (Kpag) | kpag |  | Hours 10: 259.2; Hours 11: 255.1; Hours 12: 251; Hours 13: 248.2; Hours 14: 250.3; Hours 15: 250.3; Hours 16: 249.6; Hours 17: 248.2; Hours 18: 249.6; Hours 19: 249.6; Hours 20: 248.9; Hours 21: 248.9; Hours 22: 248.2 | 250.5462
| Condenser pressure (kpag) | kpag |  | Hours 10: 635; Hours 11: 635; Hours 12: 659.1; Hours 13: 666.7; Hours 14: 652.2; Hours 15: 652.9; Hours 16: 644.7; Hours 17: 648.1; Hours 18: 648.8; Hours 19: 660.5; Hours 20: 659.8; Hours 21: 640.5; Hours 22: 623.3 | 648.2
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 10: 4.2; Hours 11: 4.2; Hours 12: 4.2; Hours 13: 4.2; Hours 14: 4.2; Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2; Hours 18: 4.2; Hours 19: 4.2; Hours 20: 4.2; Hours 21: 4.2; Hours 22: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 10: 3.7; Hours 11: 3.7; Hours 12: 3.7; Hours 13: 3.7; Hours 14: 3.7; Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7; Hours 18: 3.7; Hours 19: 3.7; Hours 20: 3.7; Hours 21: 3.7; Hours 22: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 10: 2376.1243; Hours 11: 2183.4656; Hours 12: 2279.795; Hours 13: 2279.795; Hours 14: 2247.6852; Hours 15: 2279.795; Hours 16: 2311.9048; Hours 17: 2344.0146; Hours 18: 2311.9048; Hours 19: 2311.9048; Hours 20: 2311.9048; Hours 21: 2247.6852; Hours 22: 2215.5754 | 29701.5542
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 700 | 1500 | 1100 | 1300 | 1300 | 1300 | 1300 | 1200 | 1200 | 1400 | 1300 | 1200 | 1300 | 1200 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17900
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 10: 0.63128; Hours 11: 0.50379; Hours 12: 0.57023; Hours 13: 0.57023; Hours 14: 0.57837; Hours 15: 0.57023; Hours 16: 0.51905; Hours 17: 0.51194; Hours 18: 0.60556; Hours 19: 0.56231; Hours 20: 0.51905; Hours 21: 0.57837; Hours 22: 0.54162 | 0.55862
17 | Average iKW/TR |  |  | Hours 7: 0.55862 | 0.55862
18 | COP of chiller |  |  | Hours 10: 5.5696; Hours 11: 6.9792; Hours 12: 6.166; Hours 13: 6.166; Hours 14: 6.0791; Hours 15: 6.166; Hours 16: 6.7739; Hours 17: 6.868; Hours 18: 5.8062; Hours 19: 6.2528; Hours 20: 6.7739; Hours 21: 6.0791; Hours 22: 6.4916 | 6.3209
19 | EER of Chiller |  |  | Hours 10: 19.0092; Hours 11: 23.8198; Hours 12: 21.0445; Hours 13: 21.0445; Hours 14: 20.748; Hours 15: 21.0445; Hours 16: 23.1193; Hours 17: 23.4404; Hours 18: 19.8165; Hours 19: 21.3409; Hours 20: 23.1193; Hours 21: 20.748; Hours 22: 22.156 | 21.5731
20 | LMTD of Condenser | ºC |  | Hours 10: 3.1609; Hours 11: 2.6711; Hours 12: 2.7924; Hours 13: 2.5115; Hours 14: 2.6711; Hours 15: 2.4816; Hours 16: 2.5475; Hours 17: 2.7026; Hours 18: 2.7339; Hours 19: 2.7026; Hours 20: 2.7026; Hours 21: 2.5475; Hours 22: 2.6395 | 2.6819
21 | LMTD of Evaporator | ºC |  | Hours 10: 3.3309; Hours 11: 2.5363; Hours 12: 2.4222; Hours 13: 2.4222; Hours 14: 2.5849; Hours 15: 2.4222; Hours 16: 2.4453; Hours 17: 2.4683; Hours 18: 2.6332; Hours 19: 2.4453; Hours 20: 2.4453; Hours 21: 2.3991; Hours 22: 2.3759 | 2.5332

## 07-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 07/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.1 | 2.2 | 2.2 | 2.1 | 1.9 | 1.9 | 1.8 | 1.8 | 1.8 | 1.9 | 1.9 | 1.8 | 1.9 | 1.9 | 1.8 | 1.9 | 1.9 | 1.8 | 1.8 | 2.1 | 2.4 | 2.1 | 2.3 | 2.2 | 1.9792
2 | Small temperature difference of evaporator | ºC |  | 1.2 | 1.2 | 1.3 | 1.4 | 0.9 | 0.8 | 1.1 | 1.3 | 0.7 | 1 | 1.2 | 1.2 | 1.1 | 1 | 1.1 | 1.3 | 1.1 | 1.5 | 1.9 | 1.8 | 1.6 | 1.1 | 1.4 | 1.5 | 1.2375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.6 | 14.8 | 15.1 | 14.9 | 13.4 | 12.6 | 12.3 | 12.3 | 12.5 | 12.6 | 12.6 | 12.7 | 12.6 | 12.7 | 12.8 | 12.7 | 12.2 | 12 | 12.8 | 13.8 | 14.2 | 14.5 | 14.6 | 14.7 | 13.3333
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.1 | 6.4 | 6.4 | 6.7 | 5.6 | 5.5 | 5.5 | 5.6 | 5.6 | 5.7 | 5.6 | 5.5 | 5.5 | 5.5 | 5.6 | 5.4 | 5.5 | 5.4 | 5.6 | 5.6 | 5.9 | 5.9 | 6.2 | 6.2 | 5.7708
| Evaporator Delta "T" |  |  | 8.5 | 8.4 | 8.7 | 8.2 | 7.8 | 7.1 | 6.8 | 6.7 | 6.9 | 6.9 | 7 | 7.2 | 7.1 | 7.2 | 7.2 | 7.3 | 6.7 | 6.6 | 7.2 | 8.2 | 8.3 | 8.6 | 8.4 | 8.5 | 7.5625
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.1 | 20.7 | 20.3 | 21.9 | 21.9 | 22.5 | 23.5 | 23.6 | 23.6 | 23.2 | 23.1 | 23.3 | 23.4 | 23.7 | 23.6 | 23.3 | 23 | 22.9 | 20.8 | 20.9 | 21.1 | 20.3 | 20.5 | 20.8 | 22.2083
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.9 | 26.7 | 26.3 | 27.7 | 27.4 | 27.5 | 28.5 | 28.4 | 28.4 | 28.2 | 28 | 28.6 | 28.5 | 28.7 | 28.5 | 28.2 | 27.9 | 27.4 | 25.9 | 26.8 | 26.8 | 26.3 | 26.5 | 26.9 | 27.5417
| Condenser Delta "T" | ºC |  | 5.8 | 6 | 6 | 5.8 | 5.5 | 5 | 5 | 4.8 | 4.8 | 5 | 4.9 | 5.3 | 5.1 | 5 | 4.9 | 4.9 | 4.9 | 4.5 | 5.1 | 5.9 | 5.7 | 6 | 6 | 6.1 | 5.3333
| Evaporator pressure (Kpag) | kpag |  | 248.9 | 248.9 | 250.3 | 255.8 | 240.6 | 239.9 | 239.9 | 237.2 | 237.2 | 240.6 | 241.3 | 240.6 | 240.6 | 240.6 | 242 | 240.6 | 237.9 | 244.1 | 226.8 | 239.9 | 242 | 241.3 | 247.5 | 248.2 | 242.1958
| Condenser pressure (kpag) | kpag |  | 649.5 | 643.3 | 635.7 | 664 | 654.3 | 653.6 | 670.9 | 675.7 | 674.3 | 664.7 | 660.5 | 663.3 | 676.4 | 681.9 | 676.4 | 668.8 | 661.9 | 650.9 | 627.4 | 643.3 | 650.9 | 639.1 | 639.8 | 650.2 | 657.3667
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2729.332 | 2697.2222 | 2793.5516 | 2633.0026 | 2504.5635 | 2279.795 | 2183.4656 | 2151.3558 | 2215.5754 | 2215.5754 | 2247.6852 | 2311.9048 | 2279.795 | 2311.9048 | 2311.9048 | 2344.0146 | 2151.3558 | 2119.246 | 2311.9048 | 2633.0026 | 2665.1124 | 2761.4418 | 2697.2222 | 2729.332 | 58279.2659
15 | Power Consumption of Chiller | KWH |  | 1500 | 1300 | 1400 | 1300 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1300 | 1300 | 1200 | 1300 | 1200 | 1200 | 1100 | 1200 | 1300 | 1400 | 1400 | 1300 | 1400 | 1600 | 30900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.54959 | 0.48198 | 0.50115 | 0.49373 | 0.47913 | 0.52636 | 0.54959 | 0.55779 | 0.54162 | 0.54162 | 0.57837 | 0.56231 | 0.52636 | 0.56231 | 0.51905 | 0.51194 | 0.51131 | 0.56624 | 0.56231 | 0.53171 | 0.52531 | 0.47077 | 0.51905 | 0.58622 | 0.53149
17 | Average iKW/TR |  |  | Hours 7: 0.53149 | 0.53149
18 | COP of chiller |  |  | 6.3976 | 7.2949 | 7.0158 | 7.1213 | 7.3384 | 6.6798 | 6.3976 | 6.3035 | 6.4916 | 6.4916 | 6.0791 | 6.2528 | 6.6798 | 6.2528 | 6.7739 | 6.868 | 6.8765 | 6.2094 | 6.2528 | 6.6126 | 6.6932 | 7.4686 | 6.7739 | 5.9977 | 6.6385
19 | EER of Chiller |  |  | 21.8349 | 24.8977 | 23.9449 | 24.3049 | 25.0459 | 22.7982 | 21.8349 | 21.5138 | 22.156 | 22.156 | 20.748 | 21.3409 | 22.7982 | 21.3409 | 23.1193 | 23.4404 | 23.4695 | 21.1927 | 21.3409 | 22.5688 | 22.844 | 25.4905 | 23.1193 | 20.4702 | 22.6571
20 | LMTD of Condenser | ºC |  | 4.3776 | 4.5604 | 4.5604 | 4.3776 | 4.0452 | 3.877 | 3.7618 | 3.6943 | 3.6943 | 3.877 | 3.8429 | 3.8621 | 3.9109 | 3.877 | 3.7282 | 3.8429 | 3.8429 | 3.5921 | 3.7954 | 4.4112 | 4.686 | 4.4447 | 4.6753 | 4.5941 | 4.0805
21 | LMTD of Evaporator | ºC |  | 4.0674 | 4.0395 | 4.2642 | 4.2591 | 3.4381 | 3.1004 | 3.4491 | 3.6872 | 2.8933 | 3.3384 | 3.6424 | 3.7001 | 3.5344 | 3.4218 | 3.5627 | 3.8637 | 3.4204 | 3.9137 | 4.5965 | 4.7819 | 4.5541 | 3.9507 | 4.3167 | 4.4805 | 3.8448
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 10: 1.3; Hours 11: 1.3; Hours 12: 1.2; Hours 13: 1.2; Hours 14: 1; Hours 15: 1.1; Hours 16: 1; Hours 17: 1; Hours 18: 0.9; Hours 19: 1.1; Hours 20: 1.1; Hours 21: 1.2; Hours 22: 1.1; Hours 23: 1.2 | 1.1214
2 | Small temperature difference of evaporator | ºC |  | Hours 10: 0.9; Hours 11: 0.9; Hours 12: 0.6; Hours 13: 0.4; Hours 14: 0.4; Hours 15: 0.3; Hours 16: 0.4; Hours 17: 0.4; Hours 18: 0.4; Hours 19: 0.4; Hours 20: 0.4; Hours 21: 0.4; Hours 22: 0.4; Hours 23: 0.4 | 0.47857
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 10: 15.1; Hours 11: 13.4; Hours 12: 12.6; Hours 13: 12.2; Hours 14: 12.2; Hours 15: 12.5; Hours 16: 12.6; Hours 17: 12.6; Hours 18: 12.8; Hours 19: 12.8; Hours 20: 12.8; Hours 21: 12.7; Hours 22: 12.6; Hours 23: 12.3 | 12.8
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 10: 6.6; Hours 11: 5.5; Hours 12: 5.5; Hours 13: 5.5; Hours 14: 5.5; Hours 15: 5.5; Hours 16: 5.5; Hours 17: 5.6; Hours 18: 5.5; Hours 19: 5.5; Hours 20: 5.5; Hours 21: 5.6; Hours 22: 5.5; Hours 23: 5.4 | 5.5857
| Evaporator Delta "T" |  |  | Hours 10: 8.5; Hours 11: 7.9; Hours 12: 7.1; Hours 13: 6.7; Hours 14: 6.7; Hours 15: 7; Hours 16: 7.1; Hours 17: 7; Hours 18: 7.3; Hours 19: 7.3; Hours 20: 7.3; Hours 21: 7.1; Hours 22: 7.1; Hours 23: 6.9 | 7.2143
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 10: 22.5; Hours 11: 22.6; Hours 12: 23.1; Hours 13: 24.3; Hours 14: 24.4; Hours 15: 24.3; Hours 16: 23.9; Hours 17: 23.9; Hours 18: 23.9; Hours 19: 24; Hours 20: 24.3; Hours 21: 24.2; Hours 22: 23.9; Hours 23: 23.8 | 23.7929
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 10: 27.9; Hours 11: 27.5; Hours 12: 27.4; Hours 13: 28.4; Hours 14: 28.6; Hours 15: 28.4; Hours 16: 28.2; Hours 17: 28.1; Hours 18: 28.5; Hours 19: 28.5; Hours 20: 28.8; Hours 21: 28.6; Hours 22: 28.2; Hours 23: 27.9 | 28.2143
| Condenser Delta "T" | ºC |  | Hours 10: 5.4; Hours 11: 4.9; Hours 12: 4.3; Hours 13: 4.1; Hours 14: 4.2; Hours 15: 4.1; Hours 16: 4.3; Hours 17: 4.2; Hours 18: 4.6; Hours 19: 4.5; Hours 20: 4.5; Hours 21: 4.4; Hours 22: 4.3; Hours 23: 4.1 | 4.4214
| Evaporator pressure (Kpag) | kpag |  | Hours 10: 256.5; Hours 11: 246.8; Hours 12: 248.9; Hours 13: 248.9; Hours 14: 249.6; Hours 15: 248.9; Hours 16: 249.6; Hours 17: 249.6; Hours 18: 250.3; Hours 19: 248.9; Hours 20: 248.9; Hours 21: 251; Hours 22: 248.9; Hours 23: 247.5 | 249.5929
| Condenser pressure (kpag) | kpag |  | Hours 10: 650.9; Hours 11: 640.5; Hours 12: 635.7; Hours 13: 655.7; Hours 14: 660.5; Hours 15: 656.4; Hours 16: 652.2; Hours 17: 646.7; Hours 18: 646.7; Hours 19: 660.5; Hours 20: 666; Hours 21: 660.5; Hours 22: 655; Hours 23: 648.8 | 652.5786
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 10: 4.2; Hours 11: 4.2; Hours 12: 4.2; Hours 13: 4.2; Hours 14: 4.2; Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2; Hours 18: 4.2; Hours 19: 4.2; Hours 20: 4.2; Hours 21: 4.2; Hours 22: 4.2; Hours 23: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 10: 3.7; Hours 11: 3.7; Hours 12: 3.7; Hours 13: 3.7; Hours 14: 3.7; Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7; Hours 18: 3.7; Hours 19: 3.7; Hours 20: 3.7; Hours 21: 3.7; Hours 22: 3.7; Hours 23: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 10: 2729.332; Hours 11: 2536.6733; Hours 12: 2279.795; Hours 13: 2151.3558; Hours 14: 2151.3558; Hours 15: 2247.6852; Hours 16: 2279.795; Hours 17: 2247.6852; Hours 18: 2344.0146; Hours 19: 2344.0146; Hours 20: 2344.0146; Hours 21: 2279.795; Hours 22: 2279.795; Hours 23: 2215.5754 | 32430.8862
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 1100 | 1500 | 1200 | 1300 | 1200 | 1200 | 1300 | 1300 | 1200 | 1300 | 1300 | 1200 | 1500 | 1100 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18900
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 10: 0.54959; Hours 11: 0.47306; Hours 12: 0.57023; Hours 13: 0.55779; Hours 14: 0.55779; Hours 15: 0.57837; Hours 16: 0.57023; Hours 17: 0.53388; Hours 18: 0.5546; Hours 19: 0.5546; Hours 20: 0.51194; Hours 21: 0.65795; Hours 22: 0.4825; Hours 23: 0.54162 | 0.54958
17 | Average iKW/TR |  |  | Hours 7: 0.54958 | 0.54958
18 | COP of chiller |  |  | Hours 10: 6.3976; Hours 11: 7.4325; Hours 12: 6.166; Hours 13: 6.3035; Hours 14: 6.3035; Hours 15: 6.0791; Hours 16: 6.166; Hours 17: 6.5857; Hours 18: 6.3397; Hours 19: 6.3397; Hours 20: 6.868; Hours 21: 5.3438; Hours 22: 7.2871; Hours 23: 6.4916 | 6.436
19 | EER of Chiller |  |  | Hours 10: 21.8349; Hours 11: 25.367; Hours 12: 21.0445; Hours 13: 21.5138; Hours 14: 21.5138; Hours 15: 20.748; Hours 16: 21.0445; Hours 17: 22.4771; Hours 18: 21.6373; Hours 19: 21.6373; Hours 20: 23.4404; Hours 21: 18.2385; Hours 22: 24.8707; Hours 23: 22.156 | 21.966
20 | LMTD of Condenser | ºC |  | Hours 10: 3.2932; Hours 11: 3.1366; Hours 12: 2.8244; Hours 13: 2.7602; Hours 14: 2.5475; Hours 15: 2.6395; Hours 16: 2.5784; Hours 17: 2.5475; Hours 18: 2.5413; Hours 19: 2.7651; Hours 20: 2.7651; Hours 21: 2.8563; Hours 22: 2.7026; Hours 23: 2.7602 | 2.7656
21 | LMTD of Evaporator | ºC |  | Hours 10: 3.6231; Hours 11: 3.4647; Hours 12: 2.7821; Hours 13: 2.3293; Hours 14: 2.3293; Hours 15: 2.1931; Hours 16: 2.4222; Hours 17: 2.3991; Hours 18: 2.4683; Hours 19: 2.4683; Hours 20: 2.4683; Hours 21: 2.4222; Hours 22: 2.4222; Hours 23: 2.3759 | 2.5834

## 08-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 08/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.9 | 2 | 1.9 | 1.6 | 2 | 1.7 | 1.8 | 1.8 | 1.8 | 1.8 | 2 | 1.8 | 2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 2 | 2 | 1.8 | 2.1 | 2.3 | 1.9042
2 | Small temperature difference of evaporator | ºC |  | 1 | 0.9 | 0.7 | 1.2 | 2.98 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.8 | 0.5 | 0.6 | 0.7 | 0.8 | 0.7 | 0.6 | 0.6 | 0.7 | 0.6 | 0.9 | 0.8 | 0.8 | 0.9 | 0.8825
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.9 | 14.7 | 13.3 | 12.9 | 13.1 | 12.8 | 12.6 | 12.8 | 13.2 | 13.3 | 13.7 | 13.6 | 13.6 | 13.7 | 13.7 | 13.4 | 13.4 | 13.2 | 13.1 | 13.1 | 12.9 | 14.2 | 15.2 | 15.8 | 13.5917
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.6 | 6.5 | 6.4 | 6.1 | 5.8 | 6.1 | 5.9 | 6.1 | 6.2 | 5.9 | 5.8 | 6.2 | 5.9 | 5.7 | 5.7 | 5.8 | 5.8 | 5.5 | 5.5 | 5.6 | 6 | 6.6 | 7.1 | 6.0458
| Evaporator Delta "T" |  |  | 8.6 | 8.1 | 6.8 | 6.5 | 7 | 7 | 6.5 | 6.9 | 7.1 | 7.1 | 7.8 | 7.8 | 7.4 | 7.8 | 8 | 7.7 | 7.6 | 7.4 | 7.6 | 7.6 | 7.3 | 8.2 | 8.6 | 8.7 | 7.5458
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.1 | 23.6 | 23 | 22.8 | 22.8 | 23.7 | 24.1 | 26.3 | 24.6 | 24.7 | 24.8 | 24.9 | 24.8 | 25.1 | 24.9 | 25.5 | 26.2 | 26.8 | 26.7 | 26.8 | 26.3 | 25.1 | 24.3 | 23.9 | 24.7417
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.1 | 29.1 | 27.8 | 27.5 | 27.8 | 28.4 | 28.8 | 30.9 | 29.5 | 29.8 | 30.2 | 30.3 | 30.1 | 30.4 | 30.5 | 31 | 31.4 | 31.9 | 32.1 | 32.2 | 31.4 | 30.9 | 30.4 | 30.1 | 30.025
| Condenser Delta "T" | ºC |  | 6 | 5.5 | 4.8 | 4.7 | 5 | 4.7 | 4.7 | 4.6 | 4.9 | 5.1 | 5.4 | 5.4 | 5.3 | 5.3 | 5.6 | 5.5 | 5.2 | 5.1 | 5.4 | 5.4 | 5.1 | 5.8 | 6.1 | 6.2 | 5.2833
| Evaporator pressure (Kpag) | kpag |  | 247.5 | 258.6 | 250.3 | 256.5 | 243.4 | 250.3 | 246.1 | 244.1 | 248.9 | 249.6 | 249.6 | 249.6 | 254.4 | 248.2 | 247.5 | 249.6 | 250.3 | 248.2 | 244.1 | 246.1 | 246.8 | 250.3 | 256.5 | 262 | 249.9375
| Condenser pressure (kpag) | kpag |  | 681.2 | 692.9 | 662.6 | 652.2 | 661.9 | 675 | 684 | 736.4 | 702.6 | 704.6 | 721.9 | 721.2 | 714.3 | 723.9 | 728.8 | 734.3 | 746 | 759.1 | 763.2 | 764.6 | 748.1 | 737 | 728.8 | 721.9 | 715.2708
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2761.4418 | 2600.8929 | 2183.4656 | 2087.1362 | 2247.6852 | 2247.6852 | 2087.1362 | 2215.5754 | 2279.795 | 2279.795 | 2504.5635 | 2504.5635 | 2376.1243 | 2504.5635 | 2568.7831 | 2472.4537 | 2440.3439 | 2376.1243 | 2440.3439 | 2440.3439 | 2344.0146 | 2633.0026 | 2761.4418 | 2793.5516 | 58150.8267
15 | Power Consumption of Chiller | KWH |  | 1400 | 1100 | 1200 | 1100 | 1200 | 1200 | 1200 | 1200 | 1200 | 1400 | 1300 | 1300 | 1300 | 1500 | 1300 | 1500 | 1400 | 1400 | 1400 | 1400 | 1400 | 1500 | 1500 | 1500 | 31900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.50698 | 0.42293 | 0.54959 | 0.52704 | 0.53388 | 0.53388 | 0.57495 | 0.54162 | 0.52636 | 0.61409 | 0.51905 | 0.51905 | 0.54711 | 0.59891 | 0.50608 | 0.60668 | 0.57369 | 0.58919 | 0.57369 | 0.57369 | 0.59727 | 0.56969 | 0.54319 | 0.53695 | 0.5494
17 | Average iKW/TR |  |  | Hours 7: 0.5494 | 0.5494
18 | COP of chiller |  |  | 6.9352 | 8.3134 | 6.3976 | 6.6712 | 6.5857 | 6.5857 | 6.1153 | 6.4916 | 6.6798 | 5.7255 | 6.7739 | 6.7739 | 6.4265 | 5.8707 | 6.9476 | 5.7954 | 6.1287 | 5.9675 | 6.1287 | 6.1287 | 5.8868 | 6.1718 | 6.4728 | 6.5481 | 6.4384
19 | EER of Chiller |  |  | 23.6697 | 28.3736 | 21.8349 | 22.769 | 22.4771 | 22.4771 | 20.8716 | 22.156 | 22.7982 | 19.5413 | 23.1193 | 23.1193 | 21.9337 | 20.0367 | 23.7121 | 19.7798 | 20.9174 | 20.367 | 20.9174 | 20.9174 | 20.0917 | 21.0642 | 22.0917 | 22.3486 | 21.9744
20 | LMTD of Condenser | ºC |  | 4.2105 | 4.1611 | 3.8088 | 3.4293 | 3.9912 | 3.5454 | 3.6604 | 3.6263 | 3.7282 | 3.7954 | 4.1274 | 3.8953 | 4.0935 | 3.9783 | 4.0785 | 4.0452 | 3.9447 | 3.9109 | 4.0118 | 4.1274 | 4.0254 | 4.0268 | 4.4781 | 4.7431 | 3.9768
21 | LMTD of Evaporator | ºC |  | 3.8023 | 3.5178 | 2.8673 | 3.4967 | 5.7915 | 3.2225 | 3.0852 | 3.0472 | 3.2497 | 3.2497 | 3.2843 | 2.7764 | 2.8568 | 3.1241 | 3.3363 | 3.0987 | 2.9064 | 2.8568 | 3.0733 | 2.9064 | 3.3039 | 3.3879 | 3.4905 | 3.6753 | 3.3086
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  | 1.3 | 1 | 1.1 | 1 | 1.1 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.2 | 1.1 | 1.1 |  |  |  | 1.12
2 | Small temperature difference of evaporator | ºC |  |  | 0.6 | 0.5 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.4 | 0.4 | 0.5 |  |  |  | 0.45
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  | 14.7 | 13.4 | 13 | 13.1 | 12.7 | 12.6 | 12.8 | 13.1 | 13.3 | 13.7 | 13.8 | 13.8 | 13.8 | 13.7 | 13.6 | 13.4 | 13.2 | 13.1 | 13.1 | 13.2 |  |  |  | 13.355
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  | 6.7 | 6.4 | 6.4 | 6.2 | 6.1 | 6.1 | 6.1 | 6.2 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 5.8 | 5.6 | 5.4 | 5.4 | 5.6 | 5.6 | 5.6 |  |  |  | 5.985
| Evaporator Delta "T" |  |  |  | 8 | 7 | 6.6 | 6.9 | 6.6 | 6.5 | 6.7 | 6.9 | 7.2 | 7.6 | 7.7 | 7.7 | 7.7 | 7.9 | 8 | 8 | 7.8 | 7.5 | 7.5 | 7.6 |  |  |  | 7.37
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  | 23.9 | 23.3 | 23.4 | 23.3 | 24.2 | 24.4 | 26.3 | 25.4 | 25.2 | 25.5 | 25.5 | 25.4 | 25.5 | 25.6 | 26 | 26.6 | 27.2 | 27.1 | 27 | 27.3 |  |  |  | 25.405
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  | 29.2 | 27.8 | 27.5 | 27.4 | 28.2 | 28.3 | 30.7 | 29.7 | 29.7 | 30.2 | 30.2 | 30.3 | 30.4 | 30.7 | 31.2 | 31.8 | 32.4 | 32.1 | 32.2 | 32.2 |  |  |  | 30.11
| Condenser Delta "T" | ºC |  |  | 5.3 | 4.5 | 4.1 | 4.1 | 4 | 3.9 | 4.4 | 4.3 | 4.5 | 4.7 | 4.7 | 4.9 | 4.9 | 5.1 | 5.2 | 5.2 | 5.2 | 5 | 5.2 | 4.9 |  |  |  | 4.705
| Evaporator pressure (Kpag) | kpag |  |  | 260.6 | 259.9 | 261.3 | 257.9 | 256.5 | 255.8 | 257.9 | 258.6 | 257.2 | 257.9 | 257.2 | 255.8 | 256.5 | 251.7 | 248.9 | 247.5 | 248.2 | 249.6 | 249.6 | 370.2 |  |  |  | 260.94
| Condenser pressure (kpag) | kpag |  |  | 676.4 | 646 | 638.5 | 638.5 | 655 | 657.8 | 707.4 | 684 | 686 | 698.4 | 699.1 | 700.5 | 701.2 | 710.2 | 723.3 | 737 | 748.8 | 743.3 | 744.6 | 744.6 |  |  |  | 697.03
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  |  |  | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  |  |  | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  | 971
14 | TR Genrated by Chiller | TR |  |  | 2568.7831 | 2247.6852 | 2119.246 | 2215.5754 | 2119.246 | 2087.1362 | 2151.3558 | 2215.5754 | 2311.9048 | 2440.3439 | 2472.4537 | 2472.4537 | 2472.4537 | 2536.6733 | 2568.7831 | 2568.7831 | 2504.5635 | 2408.2341 | 2408.2341 | 2440.3439 |  |  |  | 47329.828
15 | Power Consumption of Chiller | KWH |  | 1200 | 1200 | 1300 | 1100 | 1200 | 1200 | 1200 | 1400 | 1300 | 1300 | 1300 | 1500 | 1400 | 1400 | 1400 | 1600 | 1500 | 1400 | 1500 | 1400 | 1600 |  |  |  | 28400
16 | Specific power consumption of Chiller | (iKW/TR) |  |  | 0.46715 | 0.57837 | 0.51905 | 0.54162 | 0.56624 | 0.57495 | 0.65075 | 0.58676 | 0.56231 | 0.53271 | 0.60668 | 0.56624 | 0.56624 | 0.5519 | 0.62286 | 0.58393 | 0.55898 | 0.62286 | 0.58134 | 0.65565 |  |  |  | 0.57483
17 | Average iKW/TR |  |  | Hours 7: 0.57483 | 0.57483
18 | COP of chiller |  |  |  | 7.5265 | 6.0791 | 6.7739 | 6.4916 | 6.2094 | 6.1153 | 5.403 | 5.9923 | 6.2528 | 6.6002 | 5.7954 | 6.2094 | 6.2094 | 6.3707 | 5.6449 | 6.0212 | 6.29 | 5.6449 | 6.0481 | 5.3627 |  |  |  | 6.152
19 | EER of Chiller |  |  |  | 25.6881 | 20.748 | 23.1193 | 22.156 | 21.1927 | 20.8716 | 18.4404 | 20.4516 | 21.3409 | 22.5265 | 19.7798 | 21.1927 | 21.1927 | 21.7431 | 19.266 | 20.5504 | 21.4679 | 19.266 | 20.6422 | 18.3027 |  |  |  | 20.9969
20 | LMTD of Condenser | ºC |  |  | 3.2621 | 2.6397 | 2.6395 | 2.5165 | 2.6077 | 2.454 | 2.7339 | 2.7026 | 2.7651 | 2.827 | 2.827 | 2.8884 | 3.0136 | 3.0756 | 3.1064 | 3.1064 | 2.9795 | 3.0446 | 2.9795 | 2.8884 |  |  |  | 2.8529
21 | LMTD of Evaporator | ºC |  |  | 3.0046 | 2.5849 | 2.1049 | 2.3759 | 2.3059 | 2.2825 | 2.3293 | 2.3759 | 2.4453 | 2.5369 | 2.7527 | 2.5597 | 2.5597 | 2.8 | 2.8236 | 3.0046 | 2.9556 | 2.5141 | 2.5141 | 2.7289 |  |  |  | 2.578

## 09-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 09/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.2 | 2.1 | 1.9 | 1.9 | 1.9 | 1.9 | 2.2 | 2.1 | 1.9 | 1.9 | 1.9 | 1.8 | 1.7 | 1.8 | 1.9 | 1.9 | 1.7 | 2.1 | 1.8 | 1.9 | 1.9 | 1.9 | 2.1 | 2.2 | 1.9417
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 0.8 | 0.8 | 1.6 | 1.6 | 0.7 | 1.1 | 1 | 0.6 | 1.5 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.8 | 0.7 | 0.6 | 1.1 | 0.8 | 0.7 | 0.8 | 0.84167
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.6 | 13.7 | 13.4 | 13.3 | 13 | 13.1 | 13.2 | 13.5 | 13.8 | 13.9 | 13.9 | 13.9 | 14.1 | 13.8 | 13.5 | 13.3 | 13.2 | 13.1 | 12.7 | 12.6 | 12.6 | 13.9 | 14.9 | 15.4 | 13.6
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.5 | 6.4 | 6.1 | 6 | 6.1 | 6.1 | 6.2 | 6.1 | 6.2 | 6.2 | 6.3 | 6.1 | 6.1 | 5.8 | 5.7 | 5.6 | 5.6 | 5.5 | 5.6 | 5.6 | 5.8 | 6.6 | 7.1 | 6.0667
| Evaporator Delta "T" |  |  | 8.3 | 7.2 | 7 | 7.2 | 7 | 7 | 7.1 | 7.3 | 7.7 | 7.7 | 7.7 | 7.6 | 8 | 7.7 | 7.7 | 7.6 | 7.6 | 7.5 | 7.2 | 7 | 7 | 8.1 | 8.3 | 8.3 | 7.5333
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.7 | 24.8 | 23.9 | 24.3 | 24.4 | 26.1 | 26.8 | 27.7 | 26.2 | 26.7 | 26.4 | 26.3 | 26.1 | 26.2 | 25.6 | 25.8 | 25.9 | 25.6 | 25.7 | 26.3 | 25.6 | 24.8 | 24.6 | 24.6 | 25.6292
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.4 | 29.8 | 28.9 | 29.3 | 29.3 | 31 | 32 | 32.8 | 31.8 | 32.1 | 31.9 | 31.8 | 31.2 | 31.1 | 30.9 | 31.1 | 31.2 | 30.9 | 30.8 | 31.4 | 30.4 | 30.3 | 30.4 | 30.4 | 30.8833
| Condenser Delta "T" | ºC |  | 5.7 | 5 | 5 | 5 | 4.9 | 4.9 | 5.2 | 5.1 | 5.6 | 5.4 | 5.5 | 5.5 | 5.1 | 4.9 | 5.3 | 5.3 | 5.3 | 5.3 | 5.1 | 5.1 | 4.8 | 5.5 | 5.8 | 5.8 | 5.2542
| Evaporator pressure (Kpag) | kpag |  | 256.5 | 256.5 | 252.3 | 249.6 | 248.9 | 248.2 | 249.6 | 255.8 | 255.1 | 253.7 | 255.8 | 255.1 | 254.4 | 254.4 | 251.7 | 249.6 | 247.5 | 246.1 | 244.1 | 242.7 | 243.4 | 251.7 | 258.6 | 264.1 | 251.8917
| Condenser pressure (kpag) | kpag |  | 728.8 | 708.1 | 687.4 | 697.1 | 697.1 | 735.7 | 761.9 | 777.7 | 756.4 | 765.3 | 757.7 | 754.3 | 746 | 741.9 | 735 | 735.7 | 738.4 | 734.3 | 730.2 | 743.9 | 723.3 | 722.6 | 727.4 | 729.5 | 734.8208
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2665.1124 | 2311.9048 | 2247.6852 | 2311.9048 | 2247.6852 | 2247.6852 | 2279.795 | 2344.0146 | 2472.4537 | 2472.4537 | 2472.4537 | 2440.3439 | 2568.7831 | 2472.4537 | 2472.4537 | 2440.3439 | 2440.3439 | 2408.2341 | 2311.9048 | 2247.6852 | 2247.6852 | 2600.8929 | 2665.1124 | 2665.1124 | 58054.4974
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1200 | 1100 | 1400 | 1300 | 1300 | 1500 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1300 | 1500 | 1300 | 1400 | 1300 | 1300 | 1300 | 1400 | 1500 | 1400 | 32500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.48778 | 0.56231 | 0.53388 | 0.4758 | 0.62286 | 0.57837 | 0.57023 | 0.63993 | 0.56624 | 0.56624 | 0.56624 | 0.57369 | 0.54501 | 0.56624 | 0.52579 | 0.61467 | 0.53271 | 0.58134 | 0.56231 | 0.57837 | 0.57837 | 0.53828 | 0.56283 | 0.52531 | 0.56062
17 | Average iKW/TR |  |  | Hours 7: 0.56062 | 0.56062
18 | COP of chiller |  |  | 7.2081 | 6.2528 | 6.5857 | 7.3897 | 5.6449 | 6.0791 | 6.166 | 5.4944 | 6.2094 | 6.2094 | 6.2094 | 6.1287 | 6.4513 | 6.2094 | 6.687 | 5.7202 | 6.6002 | 6.0481 | 6.2528 | 6.0791 | 6.0791 | 6.532 | 6.247 | 6.6932 | 6.299
19 | EER of Chiller |  |  | 24.6013 | 21.3409 | 22.4771 | 25.221 | 19.266 | 20.748 | 21.0445 | 18.7523 | 21.1927 | 21.1927 | 21.1927 | 20.9174 | 22.0183 | 21.1927 | 22.8229 | 19.5229 | 22.5265 | 20.6422 | 21.3409 | 20.748 | 20.748 | 22.2936 | 21.3211 | 22.844 | 21.4986
20 | LMTD of Condenser | ºC |  | 4.4587 | 4.1046 | 3.877 | 3.877 | 3.8429 | 3.8429 | 4.2868 | 4.1391 | 4.0785 | 4.0118 | 4.0452 | 3.9283 | 3.6789 | 3.7282 | 3.9783 | 3.9783 | 3.7448 | 4.2079 | 3.7954 | 3.9109 | 3.8088 | 4.0452 | 4.3776 | 4.4927 | 4.01
21 | LMTD of Evaporator | ºC |  | 3.5706 | 3.1269 | 3.0739 | 4.2235 | 4.1623 | 2.9192 | 3.5344 | 3.4495 | 2.931 | 4.2454 | 2.931 | 2.9064 | 3.0046 | 2.7527 | 2.931 | 2.9064 | 2.9064 | 3.206 | 2.9709 | 2.757 | 3.506 | 3.3621 | 3.2499 | 3.4136 | 3.2517
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.3 | 1.1 | 1 | 1.1 | 1.1 | 1.2 | 1.1 | 1.3 | 1.2 | 1.2 | 1.2 | 1.3 | 1.2 | 1.3 | 1.2 | 1.1 | 1.2 | 1.3 | 1.2 | 1.1 | 1.2 |  |  |  | 1.1857
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  |  |  | 0.49048
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.7 | 13.8 | 13.6 | 13.4 | 13.1 | 13.1 | 13.2 | 13.7 | 13.9 | 13.9 | 14.1 | 14.1 | 14.1 | 13.9 | 13.7 | 13.4 | 13.3 | 13.2 | 12.9 | 12.6 | 12.8 |  |  |  | 13.5476
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.3 | 6.4 | 6.1 | 5.9 | 6.1 | 6.1 | 5.8 | 5.7 | 5.6 | 5.7 | 5.8 | 5.7 | 5.6 | 5.5 | 5.4 | 5.5 | 5.5 | 5.4 | 5.5 | 5.5 |  |  |  | 5.781
| Evaporator Delta "T" |  |  | 8.4 | 7.5 | 7.2 | 7.3 | 7.2 | 7 | 7.1 | 7.9 | 8.2 | 8.3 | 8.4 | 8.3 | 8.4 | 8.3 | 8.2 | 8 | 7.8 | 7.7 | 7.5 | 7.1 | 7.3 |  |  |  | 7.7667
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.2 | 25.2 | 24.6 | 24.7 | 24.7 | 26.5 | 27.2 | 28.1 | 26.9 | 27.3 | 26.9 | 27.1 | 26.6 | 26.4 | 26.1 | 26.3 | 26.4 | 26.2 | 26.2 | 26.8 | 26.7 |  |  |  | 26.2905
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.7 | 30.1 | 29.1 | 29.3 | 29.2 | 31.1 | 32 | 33.3 | 32.3 | 32.7 | 32.4 | 32.3 | 31.8 | 31.7 | 31.4 | 31.3 | 31.5 | 31.3 | 31.1 | 31.5 | 31.5 |  |  |  | 31.3143
| Condenser Delta "T" | ºC |  | 5.5 | 4.9 | 4.5 | 4.6 | 4.5 | 4.6 | 4.8 | 5.2 | 5.4 | 5.4 | 5.5 | 5.2 | 5.2 | 5.3 | 5.3 | 5 | 5.1 | 5.1 | 4.9 | 4.7 | 4.8 |  |  |  | 5.0238
| Evaporator pressure (Kpag) | kpag |  | 257.9 | 259.9 | 259.9 | 255.8 | 254.4 | 255.8 | 256.5 | 251.7 | 248.9 | 248.2 | 248.9 | 251 | 250.3 | 248.9 | 248.2 | 247.5 | 247.5 | 247.5 | 247.5 | 248.9 | 248.9 |  |  |  | 251.6238
| Condenser pressure (kpag) | kpag |  | 712.9 | 693.6 | 670.9 | 679.8 | 677.8 | 717.1 | 741.2 | 773.6 | 749.5 | 759.8 | 752.2 | 746.7 | 738.4 | 736.4 | 726.7 | 726.7 | 728.1 | 721.9 | 718.4 | 727.4 | 727.4 |  |  |  | 725.0714
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  |  |  | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  |  |  | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  | 971
14 | TR Genrated by Chiller | TR |  | 2697.2222 | 2408.2341 | 2311.9048 | 2344.0146 | 2311.9048 | 2247.6852 | 2279.795 | 2536.6733 | 2633.0026 | 2665.1124 | 2697.2222 | 2665.1124 | 2697.2222 | 2665.1124 | 2633.0026 | 2568.7831 | 2504.5635 | 2472.4537 | 2408.2341 | 2279.795 | 2344.0146 |  |  |  | 52371.0648
15 | Power Consumption of Chiller | KWH |  | 1400 | 1300 | 1300 | 1300 | 1400 | 1300 | 1500 | 1500 | 1700 | 1500 | 1700 | 1500 | 1500 | 1700 | 1500 | 1500 | 1400 | 1400 | 1300 | 1500 | 1500 |  |  |  | 30700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.51905 | 0.53981 | 0.56231 | 0.5546 | 0.60556 | 0.57837 | 0.65795 | 0.59133 | 0.64565 | 0.56283 | 0.63028 | 0.56283 | 0.55613 | 0.63787 | 0.56969 | 0.58393 | 0.55898 | 0.56624 | 0.53981 | 0.65795 | 0.63993 |  |  |  | 0.58672
17 | Average iKW/TR |  |  | Hours 7: 0.58672 | 0.58672
18 | COP of chiller |  |  | 6.7739 | 6.5133 | 6.2528 | 6.3397 | 5.8062 | 6.0791 | 5.3438 | 5.946 | 5.4457 | 6.247 | 5.5785 | 6.247 | 6.3223 | 5.5121 | 6.1718 | 6.0212 | 6.29 | 6.2094 | 6.5133 | 5.3438 | 5.4944 |  |  |  | 6.0215
19 | EER of Chiller |  |  | 23.1193 | 22.2301 | 21.3409 | 21.6373 | 19.8165 | 20.748 | 18.2385 | 20.2936 | 18.5861 | 21.3211 | 19.0394 | 21.3211 | 21.578 | 18.8127 | 21.0642 | 20.5504 | 21.4679 | 21.1927 | 22.2301 | 18.2385 | 18.7523 |  |  |  | 20.5514
20 | LMTD of Condenser | ºC |  | 3.3241 | 2.8884 | 2.6397 | 2.7961 | 2.7651 | 2.9196 | 2.8578 | 3.2309 | 3.1676 | 3.1676 | 3.1981 | 3.2309 | 3.1064 | 3.2621 | 3.1371 | 2.9189 | 3.0756 | 3.1996 | 3.0136 | 2.827 | 2.9824 |  |  |  | 3.0337
21 | LMTD of Evaporator | ºC |  | 3.1019 | 2.7051 | 2.4453 | 2.4683 | 2.4453 | 2.3991 | 2.4222 | 2.6051 | 3.0533 | 3.0776 | 3.1019 | 3.0776 | 3.1019 | 3.0776 | 3.0533 | 3.0046 | 2.5824 | 2.5597 | 2.5141 | 2.4222 | 2.4683 |  |  |  | 2.747

## 10-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 10/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.1 | 1.7 | 1.9 | 1.8 | 1.7 | 2 | 2 | 2 | 2 | 1.9 | 1.9 | 2.2 | 2.1 | 1.9 | 1.9 | 1.9 | 1.8 | 1.9 | 1.9 | 1.9 | 1.8 | 1.9 | 1.8 | 1.8 | 1.9083
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.8 | 0.8 | 0.6 | 0.6 | 0.7 | 1.1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 1.2 | 0.9 | 0.6 | 1.1 | 0.8 | 0.7 | 0.4 | 0.4 | 0.7375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.2 | 13.3 | 13.1 | 12.7 | 12.5 | 12.4 | 13.1 | 13.3 | 13.5 | 13.7 | 13.6 | 13.4 | 13.5 | 13.1 | 12.9 | 13 | 12.8 | 12.4 | 12.5 | 13.5 | 14.3 | 15.1 | 15.5 | 15.8 | 13.4667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 5.7 | 5.4 | 5.4 | 5.4 | 5.4 | 5.6 | 5.7 | 5.7 | 5.7 | 5.6 | 5.4 | 5.6 | 5.5 | 5.4 | 5.4 | 5.4 | 5.6 | 5.6 | 5.7 | 6 | 6.4 | 6.8 | 7.2 | 5.7583
| Evaporator Delta "T" |  |  | 7.6 | 7.6 | 7.7 | 7.3 | 7.1 | 7 | 7.5 | 7.6 | 7.8 | 8 | 8 | 8 | 7.9 | 7.6 | 7.5 | 7.6 | 7.4 | 6.8 | 6.9 | 7.8 | 8.3 | 8.7 | 8.7 | 8.6 | 7.7083
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24 | 23.3 | 23.9 | 24.1 | 24.6 | 26.8 | 27.3 | 26.5 | 26.3 | 25.2 | 25.2 | 25.1 | 24.1 | 24.2 | 24.9 | 24.7 | 24.8 | 24.6 | 23.6 | 23.5 | 23.3 | 23.5 | 24.2 | 24.9 | 24.6917
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.4 | 28.6 | 29.3 | 29.2 | 29.5 | 31.7 | 32.8 | 31.8 | 31.9 | 30.8 | 30.8 | 30.6 | 29.6 | 29.6 | 30.1 | 29.9 | 29.8 | 29.3 | 28.3 | 29.1 | 29.4 | 29.6 | 30.2 | 30.7 | 30.0833
| Condenser Delta "T" | ºC |  | 5.4 | 5.3 | 5.4 | 5.1 | 4.9 | 4.9 | 5.5 | 5.3 | 5.6 | 5.6 | 5.6 | 5.5 | 5.5 | 5.4 | 5.2 | 5.2 | 5 | 4.7 | 4.7 | 5.6 | 6.1 | 6.1 | 6 | 5.8 | 5.3917
| Evaporator pressure (Kpag) | kpag |  | 259.2 | 239.9 | 245.5 | 246.8 | 246.8 | 235.8 | 244.1 | 248.2 | 248.2 | 247.5 | 245.5 | 246.1 | 246.8 | 246.1 | 247.5 | 246.1 | 246.1 | 246.1 | 239.9 | 246.8 | 250.3 | 254.4 | 259.9 | 266.1 | 247.9042
| Condenser pressure (kpag) | kpag |  | 697.1 | 684.6 | 695 | 691.5 | 697.1 | 751.5 | 780.5 | 756.4 | 759.1 | 734.3 | 735.7 | 730.2 | 706 | 700.5 | 715 | 710.2 | 707.4 | 695.7 | 673.6 | 693.6 | 707.4 | 710.8 | 726.7 | 737 | 716.5375
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2440.3439 | 2472.4537 | 2344.0146 | 2279.795 | 2247.6852 | 2408.2341 | 2440.3439 | 2504.5635 | 2568.7831 | 2568.7831 | 2568.7831 | 2536.6733 | 2440.3439 | 2408.2341 | 2440.3439 | 2376.1243 | 2183.4656 | 2215.5754 | 2504.5635 | 2665.1124 | 2793.5516 | 2793.5516 | 2761.4418 | 59403.1085
15 | Power Consumption of Chiller | KWH |  | 1200 | 1300 | 1400 | 1200 | 1300 | 1300 | 1500 | 1400 | 1400 | 1500 | 1400 | 1400 | 1200 | 1500 | 1200 | 1400 | 1200 | 1200 | 1300 | 1500 | 1400 | 1600 | 1400 | 1500 | 32700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.49173 | 0.53271 | 0.56624 | 0.51194 | 0.57023 | 0.57837 | 0.62286 | 0.57369 | 0.55898 | 0.58393 | 0.54501 | 0.54501 | 0.47306 | 0.61467 | 0.49829 | 0.57369 | 0.50502 | 0.54959 | 0.58676 | 0.59891 | 0.52531 | 0.57275 | 0.50115 | 0.54319 | 0.55096
17 | Average iKW/TR |  |  | Hours 7: 0.55096 | 0.55096
18 | COP of chiller |  |  | 7.1502 | 6.6002 | 6.2094 | 6.868 | 6.166 | 6.0791 | 5.6449 | 6.1287 | 6.29 | 6.0212 | 6.4513 | 6.4513 | 7.4325 | 5.7202 | 7.0561 | 6.1287 | 6.962 | 6.3976 | 5.9923 | 5.8707 | 6.6932 | 6.1388 | 7.0158 | 6.4728 | 6.4142
19 | EER of Chiller |  |  | 24.4037 | 22.5265 | 21.1927 | 23.4404 | 21.0445 | 20.748 | 19.266 | 20.9174 | 21.4679 | 20.5504 | 22.0183 | 22.0183 | 25.367 | 19.5229 | 24.0826 | 20.9174 | 23.7615 | 21.8349 | 20.4516 | 20.0367 | 22.844 | 20.9518 | 23.9449 | 22.0917 | 21.8917
20 | LMTD of Condenser | ºC |  | 4.2421 | 3.7448 | 4.0118 | 3.7954 | 3.6124 | 3.9568 | 4.1611 | 4.0935 | 4.1948 | 4.0785 | 4.0785 | 4.3903 | 4.2761 | 4.0118 | 3.9447 | 3.9447 | 3.7618 | 3.7744 | 3.7744 | 4.0785 | 4.1242 | 4.2432 | 4.0918 | 4.0268 | 4.0172
21 | LMTD of Evaporator | ºC |  | 3.2322 | 3.2322 | 3.2583 | 2.832 | 2.7821 | 2.9192 | 3.6471 | 3.0733 | 3.1241 | 3.1746 | 3.1746 | 3.1746 | 2.9801 | 3.0733 | 3.0478 | 3.0733 | 3.7574 | 3.1678 | 2.7319 | 3.7307 | 3.4136 | 3.3495 | 2.7844 | 2.7622 | 3.1457
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.3 | 1.1 | 1.2 | 1.2 | 1.2 | 1.4 | 1.2 | 1.2 | 1.3 | 1.2 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | [5 empty] | 1.2053
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | [5 empty] | 0.44211
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.4 | 13.3 | 13.2 | 12.8 | 12.7 | 12.6 | 13.1 | 13.4 | 13.6 | 13.7 | 13.7 | 13.5 | 13.4 | 13.2 | 13.1 | 12.9 | 12.7 | 12.6 | 12.6 | [5 empty] | 13.1842
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 5.7 | 5.6 | 5.5 | 5.5 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.5 | 5.5 | 5.5 | 5.4 | 5.6 | 5.6 | [5 empty] | 5.6053
| Evaporator Delta "T" |  |  | 8.1 | 7.6 | 7.6 | 7.3 | 7.2 | 7 | 7.5 | 7.8 | 8 | 8.1 | 8.1 | 7.9 | 7.8 | 7.7 | 7.6 | 7.4 | 7.3 | 7 | 7 | [5 empty] | 7.5789
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.7 | 24 | 24.4 | 24.7 | 25.2 | 26.9 | 27.8 | 26.9 | 27 | 25.9 | 25.8 | 25.7 | 25.1 | 24.8 | 25.3 | 25.3 | 25.4 | 25.2 | 24.9 | [5 empty] | 25.5263
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.9 | 28.7 | 29.3 | 29.2 | 29.7 | 31.5 | 32.7 | 31.9 | 32 | 31 | 30.9 | 30.7 | 29.8 | 29.7 | 30.1 | 29.9 | 30 | 29.5 | 29.5 | [5 empty] | 30.3158
| Condenser Delta "T" | ºC |  | 5.2 | 4.7 | 4.9 | 4.5 | 4.5 | 4.6 | 4.9 | 5 | 5 | 5.1 | 5.1 | 5 | 4.7 | 4.9 | 4.8 | 4.6 | 4.6 | 4.3 | 4.6 | [5 empty] | 4.7895
| Evaporator pressure (Kpag) | kpag |  | 257.9 | 252.3 | 249.6 | 248.9 | 248.9 | 250.3 | 250.3 | 249.6 | 249.6 | 248.2 | 248.9 | 248.2 | 250.3 | 247.5 | 248.9 | 248.2 | 248.2 | 250.3 | 377.1 | [5 empty] | 256.4842
| Condenser pressure (kpag) | kpag |  | 690.2 | 667.4 | 677.8 | 678.4 | 684.6 | 725.3 | 758.4 | 738.4 | 742.6 | 719.8 | 717.7 | 714.3 | 690.2 | 687.4 | 699.1 | 693.6 | 693.6 | 681.9 | 681.9 | [5 empty] | 702.2421
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | [5 empty] | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | [5 empty] | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [5 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [5 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2600.8929 | 2440.3439 | 2440.3439 | 2344.0146 | 2311.9048 | 2247.6852 | 2408.2341 | 2504.5635 | 2568.7831 | 2600.8929 | 2600.8929 | 2536.6733 | 2504.5635 | 2472.4537 | 2440.3439 | 2376.1243 | 2344.0146 | 2247.6852 | 2247.6852 | [5 empty] | 46238.0952
15 | Power Consumption of Chiller | KWH |  | 1300 | 1400 | 1200 | 1500 | 1300 | 1300 | 1500 | 1600 | 1400 | 1600 | 1400 | 1500 | 1400 | 1300 | 1400 | 1500 | 1200 | 1200 | 1700 | [5 empty] | 26700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.49983 | 0.57369 | 0.49173 | 0.63993 | 0.56231 | 0.57837 | 0.62286 | 0.63883 | 0.54501 | 0.61517 | 0.53828 | 0.59133 | 0.55898 | 0.52579 | 0.57369 | 0.63128 | 0.51194 | 0.53388 | 0.75633 | [5 empty] | 0.57838
17 | Average iKW/TR |  |  | Hours 7: 0.57838 | 0.57838
18 | COP of chiller |  |  | 7.0344 | 6.1287 | 7.1502 | 5.4944 | 6.2528 | 6.0791 | 5.6449 | 5.5038 | 6.4513 | 5.7155 | 6.532 | 5.946 | 6.29 | 6.687 | 6.1287 | 5.5696 | 6.868 | 6.5857 | 4.6487 | [5 empty] | 6.1427
19 | EER of Chiller |  |  | 24.0085 | 20.9174 | 24.4037 | 18.7523 | 21.3409 | 20.748 | 19.266 | 18.7844 | 22.0183 | 19.5069 | 22.2936 | 20.2936 | 21.4679 | 22.8229 | 20.9174 | 19.0092 | 23.4404 | 22.4771 | 15.8662 | [5 empty] | 20.965
20 | LMTD of Condenser | ºC |  | 3.2309 | 2.827 | 3.0136 | 2.8881 | 2.8881 | 3.1609 | 3.0136 | 3.0446 | 3.1682 | 3.0756 | 2.9493 | 3.0446 | 2.9511 | 3.0136 | 2.9824 | 2.9196 | 2.9196 | 2.8244 | 2.7961 | [5 empty] | 2.9848
21 | LMTD of Evaporator | ºC |  | 2.8472 | 2.7289 | 2.5369 | 2.4683 | 2.4453 | 2.3991 | 2.5141 | 2.5824 | 2.6277 | 2.8472 | 3.029 | 2.9801 | 2.7764 | 2.5597 | 2.5369 | 2.4912 | 2.4683 | 2.3991 | 2.3991 | [5 empty] | 2.6125

## 11-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 11/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.3 | 2.1 | 2.2 | 2.1 | 1.9 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1 | 2.1 | 2.1 | 1.9 | 1.9 | 1.7 | 2 | 2.1 | 1.9 | 2.0833
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.7 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.6 | 0.8 | 0.7 | 1.9 | 2 | 1.6 | 0.80833
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.3 | 13.6 | 13.1 | 13 | 13.1 | 12.9 | 13.1 | 13.1 | 13.2 | 13.6 | 13.8 | 13.9 | 13.8 | 13.9 | 13.9 | 13.9 | 13.9 | 13.7 | 13.8 | 13.6 | 12.9 | 13.1 | 13 | 12.8 | 13.4583
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.2 | 5.6 | 5.6 | 5.5 | 5.4 | 5.5 | 5.6 | 5.5 | 5.6 | 5.7 | 5.7 | 5.8 | 5.8 | 5.8 | 5.9 | 5.9 | 5.7 | 6.3 | 6.5 | 6.5 | 6.8 | 6.7 | 6.6 | 6.6 | 5.95
| Evaporator Delta "T" |  |  | 8.1 | 8 | 7.5 | 7.5 | 7.7 | 7.4 | 7.5 | 7.6 | 7.6 | 7.9 | 8.1 | 8.1 | 8 | 8.1 | 8 | 8 | 8.2 | 7.4 | 7.3 | 7.1 | 6.1 | 6.4 | 6.4 | 6.2 | 7.5083
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.2 | 25.1 | 25.1 | 24.9 | 24.3 | 24.8 | 24.9 | 24.7 | 25.1 | 25.9 | 25.7 | 25.3 | 25.5 | 25.7 | 25.8 | 25.8 | 25.8 | 25.4 | 24.6 | 24.1 | 23.8 | 23.6 | 23.7 | 23.8 | 24.9417
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.9 | 30.8 | 30.1 | 30.1 | 29.6 | 29.9 | 30.2 | 29.9 | 30.4 | 31.4 | 31.2 | 30.8 | 31 | 31.2 | 31.3 | 31.4 | 31.4 | 30.5 | 29.6 | 29 | 28.6 | 28.1 | 28.3 | 28.4 | 30.1708
| Condenser Delta "T" | ºC |  | 5.7 | 5.7 | 5 | 5.2 | 5.3 | 5.1 | 5.3 | 5.2 | 5.3 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.1 | 5 | 4.9 | 4.8 | 4.5 | 4.6 | 4.6 | 5.2292
| Evaporator pressure (Kpag) | kpag |  | 249.6 | 246.8 | 246.8 | 246.1 | 245.5 | 245.5 | 245.5 | 247.5 | 247.5 | 250.3 | 249.6 | 249.6 | 249.6 | 249.6 | 251 | 251.7 | 251 | 257.9 | 255.8 | 257.2 | 253.7 | 249.6 | 251.7 | 243.4 | 249.6875
| Condenser pressure (kpag) | kpag |  | 740.5 | 733.6 | 718.4 | 718.4 | 706 | 714.3 | 721.9 | 712.2 | 729.5 | 750.8 | 746.7 | 739.1 | 739.8 | 746 | 745.3 | 750.8 | 749.5 | 722.6 | 708.1 | 688.8 | 677.1 | 671.5 | 674.3 | 677.1 | 720.0958
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2600.8929 | 2568.7831 | 2408.2341 | 2408.2341 | 2472.4537 | 2376.1243 | 2408.2341 | 2440.3439 | 2440.3439 | 2536.6733 | 2600.8929 | 2600.8929 | 2568.7831 | 2600.8929 | 2568.7831 | 2568.7831 | 2633.0026 | 2376.1243 | 2344.0146 | 2279.795 | 1958.6971 | 2055.0265 | 2055.0265 | 1990.8069 | 57861.8386
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1400 | 1300 | 1200 | 1400 | 1400 | 1300 | 1400 | 1400 | 1400 | 1500 | 1400 | 1500 | 1400 | 1500 | 1400 | 1200 | 1200 | 1300 | 1200 | 1100 | 1100 | 1300 | 32100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53828 | 0.54501 | 0.58134 | 0.53981 | 0.48535 | 0.58919 | 0.58134 | 0.53271 | 0.57369 | 0.5519 | 0.53828 | 0.57673 | 0.54501 | 0.57673 | 0.54501 | 0.58393 | 0.53171 | 0.50502 | 0.51194 | 0.57023 | 0.61265 | 0.53527 | 0.53527 | 0.653 | 0.55581
17 | Average iKW/TR |  |  | Hours 7: 0.55581 | 0.55581
18 | COP of chiller |  |  | 6.532 | 6.4513 | 6.0481 | 6.5133 | 7.2443 | 5.9675 | 6.0481 | 6.6002 | 6.1287 | 6.3707 | 6.532 | 6.0965 | 6.4513 | 6.0965 | 6.4513 | 6.0212 | 6.6126 | 6.962 | 6.868 | 6.166 | 5.739 | 6.5686 | 6.5686 | 5.3844 | 6.3509
19 | EER of Chiller |  |  | 22.2936 | 22.0183 | 20.6422 | 22.2301 | 24.7248 | 20.367 | 20.6422 | 22.5265 | 20.9174 | 21.7431 | 22.2936 | 20.8073 | 22.0183 | 20.8073 | 22.0183 | 20.5504 | 22.5688 | 23.7615 | 23.4404 | 21.0445 | 19.5871 | 22.4187 | 22.4187 | 18.3768 | 21.6757
20 | LMTD of Condenser | ºC |  | 4.5727 | 4.3439 | 4.2172 | 4.1736 | 3.9783 | 4.2521 | 4.2079 | 4.1736 | 4.2079 | 4.3903 | 4.2761 | 4.3903 | 4.3903 | 4.3903 | 4.3903 | 4.3101 | 4.3101 | 4.1391 | 3.877 | 3.8429 | 3.579 | 3.8179 | 3.9649 | 3.74 | 4.164
21 | LMTD of Evaporator | ºC |  | 3.3621 | 3.1746 | 2.8816 | 2.8816 | 3.0987 | 2.8568 | 2.8816 | 2.9064 | 2.9064 | 3.1494 | 3.029 | 3.1998 | 3.0046 | 3.1998 | 3.1746 | 3.1746 | 3.0533 | 3.0222 | 2.832 | 3.1004 | 2.683 | 4.3407 | 4.4597 | 3.9138 | 3.1786
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.4 | 1.3 | 1.3 | 1.2 | 1 | 1.3 | 1.2 | 1.2 | 1.1 | 1.3 | 1.2 | 1.3 | 1.3 | 1.3 | 1.3 | 1.4 | 1.4 | 1.3 | 1.2 | 1.2 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2458
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.6 | 0.5 | 0.5 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.49167
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.6 | 13.7 | 13.2 | 13.2 | 13.1 | 12.9 | 13.1 | 13.3 | 13.3 | 13.6 | 13.9 | 13.9 | 13.9 | 14 | 14 | 14 | 13.9 | 13.8 | 13.8 | 13.7 | 13.4 | 13.2 | 13.1 | 13.1 | 13.5708
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.9 | 5.4 | 5.4 | 6 | 5.9 | 5.7 | 5.5 | 5.7 | 5.7 | 6.2 | 6.1 | 5.7 | 5.7 | 5.6 | 5.8 | 5.6 | 5.6 | 6.3 | 6.6 | 6.6 | 6.6 | 6.6 | 6.4 | 6.6 | 5.9667
| Evaporator Delta "T" |  |  | 8.7 | 8.3 | 7.8 | 7.2 | 7.2 | 7.2 | 7.6 | 7.6 | 7.6 | 7.4 | 7.8 | 8.2 | 8.2 | 8.4 | 8.2 | 8.4 | 8.3 | 7.5 | 7.2 | 7.1 | 6.8 | 6.6 | 6.7 | 6.5 | 7.6042
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.6 | 25.6 | 25.5 | 25.6 | 24.9 | 25.3 | 25.6 | 25.4 | 25.8 | 26.6 | 26.2 | 25.9 | 26 | 26.1 | 26.3 | 26.4 | 26.3 | 26 | 25.3 | 24.8 | 24.6 | 24.2 | 24.4 | 24.2 | 25.525
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.1 | 30.9 | 30.4 | 30 | 29.2 | 29.9 | 30.2 | 29.9 | 30.4 | 31.3 | 31.3 | 31.1 | 31.3 | 31.5 | 31.4 | 31.7 | 31.6 | 30.7 | 29.8 | 29.1 | 28.6 | 28.2 | 28.4 | 28.3 | 30.2625
| Condenser Delta "T" | ºC |  | 5.5 | 5.3 | 4.9 | 4.4 | 4.3 | 4.6 | 4.6 | 4.5 | 4.6 | 4.7 | 5.1 | 5.2 | 5.3 | 5.4 | 5.1 | 5.3 | 5.3 | 4.7 | 4.5 | 4.3 | 4 | 4 | 4 | 4.1 | 4.7375
| Evaporator pressure (Kpag) | kpag |  | 252.3 | 246.1 | 247.5 | 255.8 | 253.7 | 251 | 248.9 | 251 | 252.3 | 256.5 | 254.4 | 250.3 | 249.6 | 248.9 | 251 | 248.9 | 248.2 | 258.6 | 262.7 | 262 | 262 | 262.7 | 262 | 262.7 | 254.1292
| Condenser pressure (kpag) | kpag |  | 723.9 | 719.8 | 705.3 | 694.3 | 680.5 | 692.2 | 702.6 | 696.4 | 706.7 | 723.9 | 724.6 | 723.9 | 728.8 | 732.2 | 733.6 | 739.1 | 737 | 712.2 | 690.9 | 676.4 | 664.7 | 654.3 | 659.1 | 658.4 | 703.3667
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2793.5516 | 2665.1124 | 2504.5635 | 2311.9048 | 2311.9048 | 2311.9048 | 2440.3439 | 2440.3439 | 2440.3439 | 2376.1243 | 2504.5635 | 2633.0026 | 2633.0026 | 2697.2222 | 2633.0026 | 2697.2222 | 2665.1124 | 2408.2341 | 2311.9048 | 2279.795 | 2183.4656 | 2119.246 | 2151.3558 | 2087.1362 | 58600.3638
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1300 | 1300 | 1300 | 1500 | 1400 | 1300 | 1500 | 1300 | 1600 | 1600 | 1500 | 1400 | 1600 | 1500 | 1700 | 1300 | 1300 | 1200 | 1200 | 1200 | 1300 | 1100 | 33400
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53695 | 0.56283 | 0.51905 | 0.56231 | 0.56231 | 0.64882 | 0.57369 | 0.53271 | 0.61467 | 0.54711 | 0.63883 | 0.60767 | 0.56969 | 0.51905 | 0.60767 | 0.55613 | 0.63787 | 0.53981 | 0.56231 | 0.52636 | 0.54959 | 0.56624 | 0.60427 | 0.52704 | 0.56971
17 | Average iKW/TR |  |  | Hours 7: 0.56971 | 0.56971
18 | COP of chiller |  |  | 6.5481 | 6.247 | 6.7739 | 6.2528 | 6.2528 | 5.4191 | 6.1287 | 6.6002 | 5.7202 | 6.4265 | 5.5038 | 5.786 | 6.1718 | 6.7739 | 5.786 | 6.3223 | 5.5121 | 6.5133 | 6.2528 | 6.6798 | 6.3976 | 6.2094 | 5.8186 | 6.6712 | 6.1987
19 | EER of Chiller |  |  | 22.3486 | 21.3211 | 23.1193 | 21.3409 | 21.3409 | 18.4954 | 20.9174 | 22.5265 | 19.5229 | 21.9337 | 18.7844 | 19.7477 | 21.0642 | 23.1193 | 19.7477 | 21.578 | 18.8127 | 22.2301 | 21.3409 | 22.7982 | 21.8349 | 21.1927 | 19.8588 | 22.769 | 21.156
20 | LMTD of Condenser | ºC |  | 3.4482 | 3.2621 | 3.1366 | 2.8563 | 2.5784 | 3.0411 | 2.9196 | 2.8881 | 2.7961 | 3.0731 | 3.0756 | 3.2309 | 3.2621 | 3.2932 | 3.1996 | 3.3852 | 3.3852 | 3.0731 | 2.8881 | 2.8244 | 2.6077 | 2.7279 | 2.7279 | 2.7602 | 3.0184
21 | LMTD of Evaporator | ºC |  | 2.9873 | 3.0776 | 2.7764 | 2.6332 | 2.2368 | 2.6332 | 2.7289 | 2.7289 | 2.7289 | 2.8568 | 2.7764 | 2.8707 | 2.8707 | 2.9175 | 3.0533 | 3.1019 | 3.0776 | 2.8816 | 2.4453 | 2.4222 | 2.3526 | 2.3059 | 2.3293 | 2.2825 | 2.7115

## 12-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 12/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.1 | 1.9 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 1.9 | 2.1 | 2.2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2 | 2.3 | 2 | 2 | 2.1 | 2.1 | 1.9 | 2 | 2.0833
2 | Small temperature difference of evaporator | ºC |  | 2.1 | 1.4 | 0.8 | 0.7 | 0.6 | 0.8 | 0.7 | 0.8 | 0.6 | 0.7 | 0.6 | 0.7 | 0.7 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.72917
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13 | 13.2 | 13.3 | 13.1 | 12.9 | 13.1 | 13.1 | 13.4 | 13.6 | 13.8 | 13.9 | 14.1 | 14.1 | 15.2 | 14.7 | 14.7 | 14.5 | 14.3 | 13.6 | 13.3 | 13.5 | 13.6 | 13.6 | 13.5 | 13.7125
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.6 | 5.6 | 5.5 | 5.6 | 5.6 | 5.6 | 5.6 | 5.7 | 5.8 | 6.1 | 6.1 | 6.1 | 7 | 6.5 | 6.4 | 6.3 | 6.3 | 6 | 6.4 | 6.6 | 6.5 | 6.5 | 6.6 | 6.1375
| Evaporator Delta "T" |  |  | 6.7 | 6.6 | 7.7 | 7.6 | 7.3 | 7.5 | 7.5 | 7.8 | 7.9 | 8 | 7.8 | 8 | 8 | 8.2 | 8.2 | 8.3 | 8.2 | 8 | 7.6 | 6.9 | 6.9 | 7.1 | 7.1 | 6.9 | 7.575
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.4 | 23.4 | 23.9 | 24.2 | 24.3 | 24.8 | 24.9 | 26 | 25.4 | 25.6 | 26.4 | 25.8 | 25.5 | 25.4 | 25.3 | 25.7 | 25.9 | 25.9 | 26.1 | 25.4 | 25.4 | 25.3 | 24.7 | 24.5 | 25.1333
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.3 | 28 | 29.3 | 29.3 | 29.3 | 29.9 | 30.3 | 31.3 | 30.9 | 31.3 | 32 | 31.3 | 25.6 | 30.9 | 31.2 | 31.4 | 31.4 | 31.4 | 31.3 | 30.2 | 30.3 | 30.4 | 29.9 | 29.3 | 30.1875
| Condenser Delta "T" | ºC |  | 4.9 | 4.6 | 5.4 | 5.1 | 5 | 5.1 | 5.4 | 5.3 | 5.5 | 5.7 | 5.6 | 5.5 | 0.1 | 5.5 | 5.9 | 5.7 | 5.5 | 5.5 | 5.2 | 4.8 | 4.9 | 5.1 | 5.2 | 4.8 | 5.0542
| Evaporator pressure (Kpag) | kpag |  | 254.4 | 253 | 246.8 | 246.8 | 246.1 | 246.1 | 246.8 | 248.2 | 248.2 | 251 | 253 | 253 | 385.4 | 266.8 | 259.2 | 258.6 | 257.9 | 255.8 | 254.4 | 259.2 | 255.1 | 258.6 | 253 | 255.8 | 258.8833
| Condenser pressure (kpag) | kpag |  | 670.9 | 667.4 | 699.1 | 703.3 | 702.6 | 714.3 | 721.2 | 748.1 | 740.5 | 741.9 | 766.7 | 751.5 | 384.7 | 737 | 738.4 | 744.6 | 749.5 | 750.1 | 746 | 714.3 | 720.5 | 721.2 | 710.2 | 698.4 | 710.1
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2151.3558 | 2119.246 | 2472.4537 | 2440.3439 | 2344.0146 | 2408.2341 | 2408.2341 | 2504.5635 | 2536.6733 | 2568.7831 | 2504.5635 | 2568.7831 | 2568.7831 | 2633.0026 | 2633.0026 | 2665.1124 | 2633.0026 | 2568.7831 | 2440.3439 | 2215.5754 | 2215.5754 | 2279.795 | 2279.795 | 2215.5754 | 58375.5952
15 | Power Consumption of Chiller | KWH |  | 1000 | 1400 | 1300 | 1300 | 1300 | 1400 | 1300 | 1500 | 1400 | 1500 | 1300 | 1200 | 1200 | 1400 | 1300 | 1400 | 1500 | 1400 | 1400 | 1200 | 1300 | 1200 | 1200 | 1200 | 31600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.46482 | 0.66061 | 0.52579 | 0.53271 | 0.5546 | 0.58134 | 0.53981 | 0.59891 | 0.5519 | 0.58393 | 0.51905 | 0.46715 | 0.46715 | 0.53171 | 0.49373 | 0.52531 | 0.56969 | 0.54501 | 0.57369 | 0.54162 | 0.58676 | 0.52636 | 0.52636 | 0.54162 | 0.54207
17 | Average iKW/TR |  |  | Hours 7: 0.54207 | 0.54207
18 | COP of chiller |  |  | 7.5642 | 5.3223 | 6.687 | 6.6002 | 6.3397 | 6.0481 | 6.5133 | 5.8707 | 6.3707 | 6.0212 | 6.7739 | 7.5265 | 7.5265 | 6.6126 | 7.1213 | 6.6932 | 6.1718 | 6.4513 | 6.1287 | 6.4916 | 5.9923 | 6.6798 | 6.6798 | 6.4916 | 6.5283
19 | EER of Chiller |  |  | 25.8165 | 18.1651 | 22.8229 | 22.5265 | 21.6373 | 20.6422 | 22.2301 | 20.0367 | 21.7431 | 20.5504 | 23.1193 | 25.6881 | 25.6881 | 22.5688 | 24.3049 | 22.844 | 21.0642 | 22.0183 | 20.9174 | 22.156 | 20.4516 | 22.7982 | 22.7982 | 22.156 | 22.281
20 | LMTD of Condenser | ºC |  | 4.0699 | 3.74 | 4.2421 | 4.1391 | 4.1046 | 4.1391 | 4.2421 | 4.2079 | 4.2761 | 4.1117 | 4.3101 | 4.3903 | 2.1496 | 4.2761 | 4.4112 | 4.4587 | 4.3903 | 4.5037 | 4.0595 | 3.9223 | 4.0699 | 4.1391 | 3.9447 | 3.9223 | 4.0925
21 | LMTD of Evaporator | ºC |  | 4.6761 | 3.7866 | 3.2583 | 3.0733 | 2.832 | 3.206 | 3.0478 | 3.2843 | 2.9801 | 3.1746 | 2.9556 | 3.1746 | 3.1746 | 3.0533 | 2.8707 | 3.0776 | 3.0533 | 3.0046 | 2.7289 | 2.5607 | 2.7319 | 2.7821 | 2.7821 | 2.7319 | 3.0834
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.2 | 1.4 | 1.3 | 1.3 | 1.3 | 1.2 | 1.3 | 1.2 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.2 | 1.4 | 1.2 | 1.2 | 1.2 | 1.2792
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.4 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4875
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.2 | 13.2 | 13.2 | 13 | 13.1 | 13.2 | 13.4 | 13.6 | 13.8 | 14 | 14.2 | 14.2 | 15.2 | 14.7 | 14.6 | 14.3 | 14.2 | 13.9 | 13.5 | 13.5 | 13.7 | 13.7 | 13.6 | 13.7542
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.7 | 6.6 | 5.7 | 5.6 | 5.4 | 5.8 | 5.7 | 5.7 | 6 | 5.8 | 5.9 | 5.9 | 5.9 | 6.4 | 6.2 | 6.1 | 5.8 | 5.9 | 5.5 | 6.4 | 6.6 | 6.6 | 6.6 | 6.4 | 6.05
| Evaporator Delta "T" |  |  | 6.4 | 6.6 | 7.5 | 7.6 | 7.6 | 7.3 | 7.5 | 7.7 | 7.6 | 8 | 8.1 | 8.3 | 8.3 | 8.8 | 8.5 | 8.5 | 8.5 | 8.3 | 8.4 | 7.1 | 6.9 | 7.1 | 7.1 | 7.2 | 7.7042
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.4 | 24.1 | 24.6 | 24.8 | 25 | 25.6 | 25.6 | 26.7 | 26.2 | 26.3 | 27.2 | 26.8 | 26.4 | 26.1 | 26.1 | 26.5 | 26.6 | 26.6 | 26.5 | 26.1 | 26 | 26.1 | 25.4 | 25.2 | 25.8708
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.3 | 28.1 | 29.3 | 29.6 | 29.6 | 29.9 | 30.1 | 31.6 | 30.9 | 31.3 | 32.3 | 31.8 | 31.6 | 31.4 | 31.3 | 31.6 | 32.1 | 31.8 | 31.8 | 30.4 | 30.2 | 30.4 | 29.9 | 29.5 | 30.6167
| Condenser Delta "T" | ºC |  | 3.9 | 4 | 4.7 | 4.8 | 4.6 | 4.3 | 4.5 | 4.9 | 4.7 | 5 | 5.1 | 5 | 5.2 | 5.3 | 5.2 | 5.1 | 5.5 | 5.2 | 5.3 | 4.3 | 4.2 | 4.3 | 4.5 | 4.3 | 4.7458
| Evaporator pressure (Kpag) | kpag |  | 264.1 | 262.7 | 250.3 | 248.9 | 248.9 | 253 | 251 | 250.3 | 255.1 | 251.7 | 253.7 | 252.3 | 252.3 | 260.6 | 255.8 | 254.4 | 251 | 252.3 | 247.5 | 259.9 | 263.4 | 262.7 | 262.7 | 260.6 | 255.2167
| Condenser pressure (kpag) | kpag |  | 655.7 | 653.6 | 684 | 688.1 | 690.2 | 694.3 | 702.6 | 732.9 | 718.4 | 728.1 | 752.9 | 739.1 | 732.9 | 731.5 | 729.5 | 737 | 745.3 | 740.5 | 743.3 | 705.3 | 700.5 | 705.3 | 692.9 | 685.3 | 712.05
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2055.0265 | 2119.246 | 2408.2341 | 2440.3439 | 2440.3439 | 2344.0146 | 2408.2341 | 2472.4537 | 2440.3439 | 2568.7831 | 2600.8929 | 2665.1124 | 2665.1124 | 2825.6614 | 2729.332 | 2729.332 | 2729.332 | 2665.1124 | 2697.2222 | 2279.795 | 2215.5754 | 2279.795 | 2279.795 | 2311.9048 | 59370.9987
15 | Power Consumption of Chiller | KWH |  | 1200 | 1400 | 1400 | 1300 | 1400 | 1300 | 1400 | 1400 | 1500 | 1500 | 1700 | 1400 | 1600 | 1600 | 1500 | 1500 | 1700 | 1500 | 1600 | 1200 | 1400 | 1300 | 1300 | 1300 | 34400
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58393 | 0.66061 | 0.58134 | 0.53271 | 0.57369 | 0.5546 | 0.58134 | 0.56624 | 0.61467 | 0.58393 | 0.65362 | 0.52531 | 0.60035 | 0.56624 | 0.54959 | 0.54959 | 0.62286 | 0.56283 | 0.5932 | 0.52636 | 0.63189 | 0.57023 | 0.57023 | 0.56231 | 0.5799
17 | Average iKW/TR |  |  | Hours 7: 0.5799 | 0.5799
18 | COP of chiller |  |  | 6.0212 | 5.3223 | 6.0481 | 6.6002 | 6.1287 | 6.3397 | 6.0481 | 6.2094 | 5.7202 | 6.0212 | 5.3793 | 6.6932 | 5.8566 | 6.2094 | 6.3976 | 6.3976 | 5.6449 | 6.247 | 5.9271 | 6.6798 | 5.5643 | 6.166 | 6.166 | 6.2528 | 6.085
19 | EER of Chiller |  |  | 20.5504 | 18.1651 | 20.6422 | 22.5265 | 20.9174 | 21.6373 | 20.6422 | 21.1927 | 19.5229 | 20.5504 | 18.3594 | 22.844 | 19.9885 | 21.1927 | 21.8349 | 21.8349 | 19.266 | 21.3211 | 20.2293 | 22.7982 | 18.9908 | 21.0445 | 21.0445 | 21.3409 | 20.7682
20 | LMTD of Condenser | ºC |  | 2.6954 | 2.7279 | 3.1933 | 3.1049 | 3.0411 | 2.9444 | 2.8881 | 3.1366 | 2.9511 | 3.0446 | 3.0756 | 3.1682 | 3.2309 | 3.2621 | 3.3535 | 3.3218 | 3.4482 | 3.2309 | 3.2621 | 2.8244 | 3.0297 | 2.8244 | 2.8881 | 2.8244 | 3.0613
21 | LMTD of Evaporator | ºC |  | 2.2589 | 2.3059 | 2.5141 | 2.7289 | 2.5369 | 2.4683 | 2.5141 | 2.7527 | 2.9064 | 2.6277 | 3.029 | 3.0776 | 2.8941 | 3.1982 | 3.126 | 2.9408 | 2.9408 | 2.6951 | 3.1019 | 2.7821 | 2.5607 | 2.6091 | 2.4222 | 2.4453 | 2.7265

## 14-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 14/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 2.1; Hours 8: 1.9; Hours 9: 1.9; Hours 10: 2; Hours 11: 1.9; Hours 12: 2.2 | 2
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.7; Hours 8: 0.7; Hours 9: 0.8; Hours 10: 0.6; Hours 11: 0.6; Hours 12: 0.6 | 0.66667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 14.6; Hours 8: 14.6; Hours 9: 14.9; Hours 10: 15.3; Hours 11: 15.3; Hours 12: 15.1 | 14.9667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 7.2; Hours 8: 7.2; Hours 9: 7.6; Hours 10: 7.6; Hours 11: 7.4; Hours 12: 7.2 | 7.3667
| Evaporator Delta "T" |  |  | Hours 7: 8; Hours 8: 8; Hours 9: 8; Hours 10: 8; Hours 11: 8; Hours 12: 6.7 | 7.7833
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 27.8; Hours 8: 27.5; Hours 9: 27.6; Hours 10: 27.2; Hours 11: 25.6; Hours 12: 27.4 | 27.1833
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 32.9; Hours 8: 32.7; Hours 9: 32.9; Hours 10: 32.7; Hours 11: 31.2; Hours 12: 33.1 | 32.5833
| Condenser Delta "T" | ºC |  | Hours 7: 5.7; Hours 8: 5.7; Hours 9: 5.7; Hours 10: 5.7; Hours 11: 5.7; Hours 12: 4.5 | 5.5
| Evaporator pressure (Kpag) | kpag |  | Hours 7: 264.1; Hours 8: 266.1; Hours 9: 270.3; Hours 10: 273.7; Hours 11: 269.6; Hours 12: 268.9 | 268.7833
| Condenser pressure (kpag) | kpag |  | Hours 7: 785.3; Hours 8: 779.1; Hours 9: 781.2; Hours 10: 775.7; Hours 11: 746; Hours 12: 789.4 | 776.1167
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.2; Hours 8: 4.2; Hours 9: 4.2; Hours 10: 4.2; Hours 11: 4.2; Hours 12: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.7; Hours 8: 3.7; Hours 9: 3.7; Hours 10: 3.7; Hours 11: 3.7; Hours 12: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 10: 3; Hours 11: 3; Hours 12: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 10: 971; Hours 11: 971; Hours 12: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2376.1243; Hours 8: 2376.1243; Hours 9: 2344.0146; Hours 10: 2472.4537; Hours 11: 2536.6733; Hours 12: 2536.6733 | 14642.0635
15 | Power Consumption of Chiller | KWH |  | Hours 7: 1300; Hours 8: 1400; Hours 9: 1500; Hours 10: 1300; Hours 11: 1500; Hours 12: 500 | 7500
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.54711; Hours 8: 0.58919; Hours 9: 0.63993; Hours 10: 0.52579; Hours 11: 0.59133; Hours 12: 0.19711 | 0.51508
17 | Average iKW/TR |  |  | Hours 7: 0.51508 | 0.51508
18 | COP of chiller |  |  | Hours 7: 6.4265; Hours 8: 5.9675; Hours 9: 5.4944; Hours 10: 6.687; Hours 11: 5.946; Hours 12: 17.8379 | 8.0599
19 | EER of Chiller |  |  | Hours 7: 21.9337; Hours 8: 20.367; Hours 9: 18.7523; Hours 10: 22.8229; Hours 11: 20.2936; Hours 12: 60.8807 | 27.5083
20 | LMTD of Condenser | ºC |  | Hours 7: 4.1391; Hours 8: 3.9447; Hours 9: 3.9783; Hours 10: 4.1611; Hours 11: 4.0785; Hours 12: 4.4587 | 4.1267
21 | LMTD of Evaporator | ºC |  | Hours 7: 3.0222; Hours 8: 3.0222; Hours 9: 3.1533; Hours 10: 2.931; Hours 11: 2.9801; Hours 12: 2.9801 | 3.0148
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 14: 0.7; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8 | 0.78
2 | Small temperature difference of evaporator | ºC |  | Hours 14: 0.5; Hours 15: 0.6; Hours 16: 0.6; Hours 17: 0.6; Hours 18: 0.4 | 0.54
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 13: 15.3; Hours 14: 15.7; Hours 15: 14.4; Hours 16: 13.3; Hours 17: 12.3; Hours 18: 12.2 | 13.8667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 13: 7.4; Hours 14: 8; Hours 15: 7; Hours 16: 6.2; Hours 17: 5.4; Hours 18: 5.4 | 6.5667
| Evaporator Delta "T" |  |  | Hours 13: 7.9; Hours 14: 7.7; Hours 15: 7.4; Hours 16: 7.1; Hours 17: 6.9; Hours 18: 6.8 | 7.3
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 13: 27; Hours 14: 27.9; Hours 15: 28; Hours 16: 27.4; Hours 17: 26.5; Hours 18: 26.1 | 27.15
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 13: 31.9; Hours 14: 32.8; Hours 15: 32.7; Hours 16: 32.1; Hours 17: 31; Hours 18: 26.5 | 31.1667
| Condenser Delta "T" | ºC |  | Hours 13: 4.9; Hours 14: 4.9; Hours 15: 4.7; Hours 16: 4.7; Hours 17: 4.5; Hours 18: 0.4 | 4.0167
| Evaporator pressure (Kpag) | kpag |  | Hours 13: 268.9; Hours 14: 275.1; Hours 15: 264.1; Hours 16: 252.3; Hours 17: 244.1; Hours 18: 244.1 | 258.1
| Condenser pressure (kpag) | kpag |  | Hours 13: 726.7; Hours 14: 748.1; Hours 15: 743.9; Hours 16: 726.7; Hours 17: 701.9; Hours 18: 701.9 | 724.8667
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 13: 4.2; Hours 14: 4.2; Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2; Hours 18: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 13: 3.7; Hours 14: 3.7; Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7; Hours 18: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 14: 2536.6733; Hours 15: 2472.4537; Hours 16: 2376.1243; Hours 17: 2279.795; Hours 18: 2215.5754 | 11880.6217
15 | Power Consumption of Chiller | KWH |  | Hours 7: 0; Hours 8: 0; Hours 9: 0; Hours 10: 0; Hours 11: 0; Hours 12: 0; Hours 13: 600; Hours 14: 1600; Hours 15: 1400; Hours 16: 1400; Hours 17: 1400; Hours 18: 800 | 7200
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 14: 0.63075; Hours 15: 0.56624; Hours 16: 0.58919; Hours 17: 0.61409; Hours 18: 0.36108 | 0.55227
17 | Average iKW/TR |  |  | Hours 7: 0.55227 | 0.55227
18 | COP of chiller |  |  | Hours 14: 5.5743; Hours 15: 6.2094; Hours 16: 5.9675; Hours 17: 5.7255; Hours 18: 9.7375 | 6.6428
19 | EER of Chiller |  |  | Hours 14: 19.0252; Hours 15: 21.1927; Hours 16: 20.367; Hours 17: 19.5413; Hours 18: 33.2339 | 22.672
20 | LMTD of Condenser | ºC |  | Hours 14: 2.3564; Hours 15: 2.4379; Hours 16: 2.4379; Hours 17: 2.3799; Hours 18: 0.98652 | 2.1197
21 | LMTD of Evaporator | ºC |  | Hours 14: 2.7527; Hours 15: 2.8568; Hours 16: 2.7821; Hours 17: 2.7319; Hours 18: 2.3526 | 2.6952
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [9 empty] | 0.9 | 0.7 | 0.8 | 0.6 | 0.6 | 0.7 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.7 | 0.74375
2 | Small temperature difference of evaporator | ºC | [9 empty] | 0.6 | 0.4 | 0.6 | 0.5 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.6 | 0.6 | 0.3 | 0.48125
3 | Entering Chilled Water Temp. (tchwe) | ºC | [9 empty] | 14.4 | 13.5 | 12.4 | 12.1 | 13.1 | 13.4 | 13.5 | 13.6 | 13.6 | 13.4 | 13.3 | 13.6 | 13.7 | 13.7 | 13.7 | 13.7 | 13.4187
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [9 empty] | 6.6 | 5.9 | 5.4 | 5.5 | 5.7 | 5.4 | 5.6 | 5.7 | 5.7 | 5.6 | 6 | 6.1 | 6.2 | 6.1 | 6.2 | 6.1 | 5.8625
| Evaporator Delta "T" | [10 empty] | 7.8 | 7.6 | 7 | 6.6 | 7.4 | 8 | 7.9 | 7.9 | 7.9 | 7.8 | 7.3 | 7.5 | 7.5 | 7.6 | 7.5 | 7.6 | 7.5562
5 | Entering Condenser Water Temp. (tcwe) | ºC | [9 empty] | 28.3 | 27.8 | 26.9 | 25.3 | 24.3 | 24.7 | 25.3 | 25.6 | 25.8 | 26.5 | 26.9 | 27.2 | 27.1 | 26.8 | 26.5 | 26.2 | 26.325
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [9 empty] | 32.9 | 32.1 | 30.8 | 28.9 | 28.4 | 29.2 | 29.8 | 30.1 | 30.3 | 31 | 31.2 | 31.4 | 31.3 | 31.1 | 30.8 | 30.4 | 30.6062
| Condenser Delta "T" | ºC | [9 empty] | 4.6 | 4.3 | 3.9 | 3.6 | 4.1 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.3 | 4.2 | 4.2 | 4.3 | 4.3 | 4.2 | 4.2812
| Evaporator pressure (Kpag) | kpag | [9 empty] | 261.3 | 251.7 | 248.2 | 248.9 | 251 | 247.5 | 248.9 | 250.3 | 249.6 | 248.9 | 254.4 | 255.8 | 257.2 | 256.5 | 256.5 | 255.1 | 252.6125
| Condenser pressure (kpag) | kpag | [9 empty] | 750.8 | 732.9 | 701.2 | 655.7 | 650.2 | 665.3 | 684 | 686.7 | 690.2 | 709.5 | 710.8 | 714.3 | 713.6 | 709.5 | 705.3 | 693.6 | 698.35
7 | Chilled water inlet pressure | (Kg/Cm2) | [9 empty] | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) | [9 empty] | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) | [9 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [9 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [9 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [9 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [9 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [9 empty] | 2504.5635 | 2440.3439 | 2247.6852 | 2119.246 | 2376.1243 | 2568.7831 | 2536.6733 | 2536.6733 | 2536.6733 | 2504.5635 | 2344.0146 | 2408.2341 | 2408.2341 | 2440.3439 | 2408.2341 | 2440.3439 | 38820.7341
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1400 | 1500 | 1500 | 1300 | 1300 | 1400 | 1400 | 1600 | 1400 | 1500 | 1500 | 1400 | 1400 | 1500 | 1300 | 1500 | 1500 | 24900
16 | Specific power consumption of Chiller | (iKW/TR) | [9 empty] | 0.59891 | 0.61467 | 0.57837 | 0.61343 | 0.58919 | 0.54501 | 0.63075 | 0.5519 | 0.59133 | 0.59891 | 0.59727 | 0.58134 | 0.62286 | 0.53271 | 0.62286 | 0.61467 | 0.59276
17 | Average iKW/TR |  |  | Hours 7: 0.59276 | 0.59276
18 | COP of chiller | [10 empty] | 5.8707 | 5.7202 | 6.0791 | 5.7317 | 5.9675 | 6.4513 | 5.5743 | 6.3707 | 5.946 | 5.8707 | 5.8868 | 6.0481 | 5.6449 | 6.6002 | 5.6449 | 5.7202 | 5.9455
19 | EER of Chiller | [10 empty] | 20.0367 | 19.5229 | 20.748 | 19.5624 | 20.367 | 22.0183 | 19.0252 | 21.7431 | 20.2936 | 20.0367 | 20.0917 | 20.6422 | 19.266 | 22.5265 | 19.266 | 19.5229 | 20.2918
20 | LMTD of Condenser | ºC | [9 empty] | 2.5413 | 2.1871 | 2.2025 | 1.85 | 1.9918 | 2.244 | 2.244 | 2.3799 | 2.3799 | 2.3799 | 2.3213 | 2.2918 | 2.1584 | 2.1871 | 2.3213 | 2.1584 | 2.2399
21 | LMTD of Evaporator | ºC | [9 empty] | 2.9556 | 2.5369 | 2.757 | 2.4875 | 2.4912 | 2.6277 | 2.8 | 2.8 | 2.8 | 2.7764 | 2.4683 | 2.7051 | 2.5141 | 2.9064 | 2.8816 | 2.3236 | 2.677
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.7 | 1.7 | 1.8 | 1.7 | 1.7 | 1.8 | 1.7 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.7 | 1.7 | 1.8 | 1.7 | 1.8 | 1.7 | 1.9 | 1.8 | 1.7 | 1.8 | 1.7 | 1.725
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.5 | 0.4 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.6 | 0.4 | 0.5 | 0.4 | 0.5 | 0.6 | 0.5 | 0.7 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.4 | 0.525
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.7 | 14.8 | 15.1 | 15.3 | 15.5 | 15.3 | 15.5 | 15.9 | 14.6 | 13.7 | 12.6 | 12.2 | 13.3 | 13.6 | 13.7 | 13.9 | 13.8 | 13.6 | 13.6 | 13.7 | 13.8 | 13.8 | 13.8 | 13.8 | 14.15
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7 | 7 | 7.2 | 7.5 | 7.1 | 7.2 | 7.3 | 7.8 | 6.9 | 6.4 | 5.8 | 5.4 | 5.7 | 5.8 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.2 | 6.2 | 6.2 | 6.2 | 6.1 | 6.4792
| Evaporator Delta "T" |  |  | 7.7 | 7.8 | 7.9 | 7.8 | 8.4 | 8.1 | 8.2 | 8.1 | 7.7 | 7.3 | 6.8 | 6.8 | 7.6 | 7.8 | 7.6 | 7.8 | 7.7 | 7.5 | 7.5 | 7.5 | 7.6 | 7.6 | 7.6 | 7.7 | 7.6708
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 28.2 | 27.9 | 28.1 | 27.7 | 26.1 | 28.1 | 27.3 | 28.2 | 28.3 | 27.7 | 26.9 | 25.2 | 24.3 | 24.6 | 25.3 | 25.4 | 25.7 | 26.5 | 26.9 | 27.2 | 27.1 | 26.8 | 26.6 | 26.2 | 26.7625
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 32.7 | 32.6 | 32.7 | 32.4 | 31.1 | 32.8 | 32.3 | 33.2 | 32.9 | 32.1 | 30.9 | 29.2 | 28.7 | 29.2 | 29.9 | 30.2 | 30.3 | 31 | 31.4 | 31.6 | 31.6 | 31.4 | 31.1 | 30.7 | 31.3333
| Condenser Delta "T" | ºC |  | 4.5 | 4.7 | 4.6 | 4.7 | 5 | 4.7 | 5 | 5 | 4.6 | 4.4 | 4 | 4 | 4.4 | 4.6 | 4.6 | 4.8 | 4.6 | 4.5 | 4.5 | 4.4 | 4.5 | 4.6 | 4.5 | 4.5 | 4.5708
| Evaporator pressure (Kpag) | kpag |  | 267.5 | 266.1 | 271 | 273 | 266.8 | 270.3 | 269.6 | 276.5 | 264.1 | 260.6 | 251.7 | 248.2 | 249.6 | 251.7 | 254.4 | 254.4 | 255.1 | 257.2 | 255.8 | 257.9 | 257.2 | 257.9 | 256.5 | 254.4 | 260.3125
| Condenser pressure (kpag) | kpag |  | 772.9 | 770.1 | 772.2 | 765.3 | 738.4 | 777 | 763.9 | 783.9 | 777 | 751.5 | 726 | 684.6 | 681.9 | 691.5 | 706.7 | 713.6 | 714.3 | 730.2 | 739.8 | 743.3 | 744.6 | 738.4 | 735.7 | 726.7 | 739.5625
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2472.4537 | 2504.5635 | 2536.6733 | 2504.5635 | 2697.2222 | 2600.8929 | 2633.0026 | 2600.8929 | 2472.4537 | 2344.0146 | 2183.4656 | 2183.4656 | 2440.3439 | 2504.5635 | 2440.3439 | 2504.5635 | 2472.4537 | 2408.2341 | 2408.2341 | 2408.2341 | 2440.3439 | 2440.3439 | 2440.3439 | 2472.4537 | 59114.1204
15 | Power Consumption of Chiller | KWH |  | 1600 | 1400 | 1600 | 1500 | 1500 | 1600 | 1500 | 1600 | 1400 | 1500 | 1300 | 1300 | 1400 | 1400 | 1400 | 1600 | 1300 | 1400 | 1500 | 1500 | 1500 | 1500 | 1400 | 1400 | 35100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.64713 | 0.55898 | 0.63075 | 0.59891 | 0.55613 | 0.61517 | 0.56969 | 0.61517 | 0.56624 | 0.63993 | 0.59538 | 0.59538 | 0.57369 | 0.55898 | 0.57369 | 0.63883 | 0.52579 | 0.58134 | 0.62286 | 0.62286 | 0.61467 | 0.61467 | 0.57369 | 0.56624 | 0.59401
17 | Average iKW/TR |  |  | Hours 7: 0.59401 | 0.59401
18 | COP of chiller |  |  | 5.4332 | 6.29 | 5.5743 | 5.8707 | 6.3223 | 5.7155 | 6.1718 | 5.7155 | 6.2094 | 5.4944 | 5.9054 | 5.9054 | 6.1287 | 6.29 | 6.1287 | 5.5038 | 6.687 | 6.0481 | 5.6449 | 5.6449 | 5.7202 | 5.7202 | 6.1287 | 6.2094 | 5.9359
19 | EER of Chiller |  |  | 18.5436 | 21.4679 | 19.0252 | 20.0367 | 21.578 | 19.5069 | 21.0642 | 19.5069 | 21.1927 | 18.7523 | 20.1552 | 20.1552 | 20.9174 | 21.4679 | 20.9174 | 18.7844 | 22.8229 | 20.6422 | 19.266 | 19.266 | 19.5229 | 19.5229 | 20.9174 | 21.1927 | 20.2594
20 | LMTD of Condenser | ºC |  | 3.5921 | 3.5454 | 3.5117 | 3.6604 | 3.6457 | 3.5454 | 3.7618 | 3.6457 | 3.6263 | 3.3289 | 3.1929 | 3.1929 | 3.3289 | 3.5117 | 3.5117 | 3.6943 | 3.5117 | 3.5921 | 3.4778 | 3.6707 | 3.5921 | 3.5117 | 3.5921 | 3.4778 | 3.5301
21 | LMTD of Evaporator | ºC |  | 2.7527 | 2.7764 | 2.6051 | 2.9556 | 3.1019 | 3.029 | 2.8707 | 2.8472 | 2.931 | 2.4683 | 2.5363 | 2.3526 | 2.7289 | 2.9556 | 2.7289 | 3.1241 | 2.931 | 2.8816 | 2.7051 | 2.7051 | 2.7289 | 2.9064 | 2.7289 | 2.5597 | 2.788
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## 13-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 13/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.9 | 1.9 | 2 | 2 | 2 | 2.1 | 2.2 | 2 | 1.9 | 1.9 | 2.2 | 1.7 | 1.8 | 1.8 | 2 | 2 | 2.1 | 2 | 1.9 | 1.9 | 1.8 | 2 | 2.1 | 2.1 | 1.9708
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 1.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.5 | 0.3 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.7 | 0.7 | 0.8 | 0.7375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.4 | 13.4 | 13.4 | 13.3 | 13.4 | 13.4 | 13.5 | 13.7 | 14.2 | 14.4 | 14.4 | 15.2 | 15.7 | 15.8 | 15.3 | 14.3 | 13.4 | 13.7 | 14.4 | 14.7 | 14.6 | 14.6 | 14.6 | 14.6 | 14.225
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 5.8 | 5.6 | 5.6 | 5.6 | 5.7 | 5.8 | 6 | 6.1 | 6.6 | 7.1 | 7.5 | 8.1 | 8.5 | 8.1 | 6.9 | 6.4 | 6.5 | 7 | 7.4 | 7.2 | 7.2 | 7.2 | 7.1 | 6.7333
| Evaporator Delta "T" |  |  | 6.8 | 7.6 | 7.8 | 7.7 | 7.8 | 7.7 | 7.7 | 7.7 | 8.1 | 7.8 | 7.3 | 7.7 | 7.6 | 7.3 | 7.2 | 7.4 | 7 | 7.2 | 7.4 | 7.3 | 7.4 | 7.4 | 7.4 | 7.5 | 7.4917
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.8 | 25.1 | 24.8 | 24.9 | 26.1 | 25.9 | 25.6 | 26.4 | 26.2 | 27.4 | 28 | 28.6 | 27.9 | 28 | 29.2 | 29.4 | 29.4 | 28.2 | 27.8 | 27.9 | 27.6 | 27.7 | 27.8 | 27.6 | 27.1792
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.6 | 30.4 | 30.1 | 30.3 | 31.3 | 31.3 | 30.9 | 31.7 | 31.8 | 32.4 | 33.6 | 33.9 | 33.3 | 33.4 | 34.7 | 34.6 | 34.6 | 33.4 | 33.2 | 33.1 | 33 | 32.8 | 33.1 | 32.8 | 32.4708
| Condenser Delta "T" | ºC |  | 4.8 | 5.3 | 5.3 | 5.4 | 5.2 | 5.4 | 5.3 | 5.3 | 5.6 | 5 | 5.6 | 5.3 | 5.4 | 5.4 | 5.5 | 5.2 | 5.2 | 5.2 | 5.4 | 5.2 | 5.4 | 5.1 | 5.3 | 5.2 | 5.2917
| Evaporator pressure (Kpag) | kpag |  | 254.4 | 251 | 247.5 | 248.2 | 248.2 | 249.6 | 250.3 | 253.7 | 256.5 | 260.6 | 269.6 | 271 | 277.9 | 278.5 | 275.1 | 265.4 | 257.2 | 253 | 261.3 | 265.4 | 263.4 | 266.8 | 264.1 | 266.1 | 260.6167
| Condenser pressure (kpag) | kpag |  | 703.3 | 723.3 | 719.1 | 721.9 | 745.3 | 742.6 | 737 | 755 | 748.1 | 781.2 | 792.9 | 810.1 | 795 | 792.9 | 826.7 | 821.9 | 821.2 | 797 | 792.2 | 786 | 786.7 | 781.9 | 787.4 | 781.9 | 772.9417
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2183.4656 | 2440.3439 | 2504.5635 | 2472.4537 | 2504.5635 | 2472.4537 | 2472.4537 | 2472.4537 | 2600.8929 | 2504.5635 | 2344.0146 | 2472.4537 | 2440.3439 | 2344.0146 | 2311.9048 | 2376.1243 | 2247.6852 | 2311.9048 | 2376.1243 | 2344.0146 | 2376.1243 | 2376.1243 | 2376.1243 | 2408.2341 | 57733.3995
15 | Power Consumption of Chiller | KWH |  | 1400 | 1300 | 1300 | 1400 | 1500 | 1400 | 1400 | 1500 | 1300 | 1400 | 1600 | 1300 | 1500 | 1300 | 1500 | 1500 | 1300 | 1400 | 1300 | 1400 | 1500 | 1300 | 1400 | 1500 | 33700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.64118 | 0.53271 | 0.51905 | 0.56624 | 0.59891 | 0.56624 | 0.56624 | 0.60668 | 0.49983 | 0.55898 | 0.68259 | 0.52579 | 0.61467 | 0.5546 | 0.64882 | 0.63128 | 0.57837 | 0.60556 | 0.54711 | 0.59727 | 0.63128 | 0.54711 | 0.58919 | 0.62286 | 0.58469
17 | Average iKW/TR |  |  | Hours 7: 0.58469 | 0.58469
18 | COP of chiller |  |  | 5.4836 | 6.6002 | 6.7739 | 6.2094 | 5.8707 | 6.2094 | 6.2094 | 5.7954 | 7.0344 | 6.29 | 5.151 | 6.687 | 5.7202 | 6.3397 | 5.4191 | 5.5696 | 6.0791 | 5.8062 | 6.4265 | 5.8868 | 5.5696 | 6.4265 | 5.9675 | 5.6449 | 6.0488
19 | EER of Chiller |  |  | 18.7156 | 22.5265 | 23.1193 | 21.1927 | 20.0367 | 21.1927 | 21.1927 | 19.7798 | 24.0085 | 21.4679 | 17.5803 | 22.8229 | 19.5229 | 21.6373 | 18.4954 | 19.0092 | 20.748 | 19.8165 | 21.9337 | 20.0917 | 19.0092 | 21.9337 | 20.367 | 19.266 | 20.6444
20 | LMTD of Condenser | ºC |  | 3.8088 | 3.9783 | 4.0935 | 4.1274 | 4.0595 | 4.2421 | 4.3214 | 4.0935 | 4.0785 | 3.877 | 4.4245 | 3.7448 | 3.8953 | 3.8953 | 4.1611 | 4.0595 | 4.1736 | 4.0595 | 4.0118 | 3.9447 | 3.8953 | 4.0254 | 4.2079 | 4.1736 | 4.0563
21 | LMTD of Evaporator | ºC |  | 3.1678 | 4.3448 | 2.9556 | 3.0987 | 2.9556 | 2.931 | 2.931 | 2.931 | 3.1998 | 2.9556 | 2.832 | 2.7527 | 2.3236 | 2.9966 | 2.9709 | 3.1797 | 3.2225 | 3.2769 | 3.3309 | 3.3039 | 3.1797 | 3.0222 | 3.0222 | 3.206 | 3.0871
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 21: 1.6; Hours 22: 1.6; Hours 23: 1.6; Hours 0: 1.6; Hours 1: 1.6; Hours 2: 1.6; Hours 3: 1.6; Hours 4: 1.6; Hours 5: 1.8; Hours 6: 1.8 | 1.64
2 | Small temperature difference of evaporator | ºC |  | Hours 21: 0.4; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.4; Hours 1: 0.4; Hours 2: 0.4; Hours 3: 0.4; Hours 4: 0.6; Hours 5: 0.5; Hours 6: 0.5 | 0.46
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 21: 15.6; Hours 22: 14.4; Hours 23: 13.6; Hours 0: 13.8; Hours 1: 14.4; Hours 2: 14.7; Hours 3: 14.8; Hours 4: 14.8; Hours 5: 14.7; Hours 6: 14.7 | 14.55
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 21: 8.1; Hours 22: 7.2; Hours 23: 6.6; Hours 0: 6.5; Hours 1: 6.8; Hours 2: 7; Hours 3: 6.9; Hours 4: 6.9; Hours 5: 7.1; Hours 6: 6.9 | 7
| Evaporator Delta "T" |  |  | Hours 21: 7.5; Hours 22: 7.2; Hours 23: 7; Hours 0: 7.3; Hours 1: 7.6; Hours 2: 7.7; Hours 3: 7.9; Hours 4: 7.9; Hours 5: 7.6; Hours 6: 7.8 | 7.55
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 21: 29.9; Hours 22: 29.9; Hours 23: 29.9; Hours 0: 28.6; Hours 1: 28.4; Hours 2: 28.3; Hours 3: 28; Hours 4: 28.1; Hours 5: 28.2; Hours 6: 28.1 | 28.74
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 21: 34.4; Hours 22: 34.2; Hours 23: 34.2; Hours 0: 33; Hours 1: 32.9; Hours 2: 32.9; Hours 3: 32.8; Hours 4: 32.8; Hours 5: 32.7; Hours 6: 32.8 | 33.27
| Condenser Delta "T" | ºC |  | Hours 21: 4.5; Hours 22: 4.3; Hours 23: 4.3; Hours 0: 4.4; Hours 1: 4.5; Hours 2: 4.6; Hours 3: 4.8; Hours 4: 4.7; Hours 5: 4.5; Hours 6: 4.7 | 4.53
| Evaporator pressure (Kpag) | kpag |  | Hours 21: 282.7; Hours 22: 269.6; Hours 23: 259.2; Hours 0: 259.2; Hours 1: 262.7; Hours 2: 266.1; Hours 3: 266.1; Hours 4: 266.8; Hours 5: 264.8; Hours 6: 268.2 | 266.54
| Condenser pressure (kpag) | kpag |  | Hours 21: 810.1; Hours 22: 806.7; Hours 23: 809.4; Hours 0: 777.7; Hours 1: 779.1; Hours 2: 779.1; Hours 3: 772.2; Hours 4: 774.3; Hours 5: 775; Hours 6: 769.5 | 785.31
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 21: 4.2; Hours 22: 4.2; Hours 23: 4.2; Hours 0: 4.2; Hours 1: 4.2; Hours 2: 4.2; Hours 3: 4.2; Hours 4: 4.2; Hours 5: 4.2; Hours 6: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 21: 3.7; Hours 22: 3.7; Hours 23: 3.7; Hours 0: 3.7; Hours 1: 3.7; Hours 2: 3.7; Hours 3: 3.7; Hours 4: 3.7; Hours 5: 3.7; Hours 6: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8; Hours 5: 3.8; Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 21: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3; Hours 3: 3; Hours 4: 3; Hours 5: 3; Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5; Hours 3: 0.5; Hours 4: 0.5; Hours 5: 0.5; Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8; Hours 3: 0.8; Hours 4: 0.8; Hours 5: 0.8; Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 21: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971; Hours 3: 971; Hours 4: 971; Hours 5: 971; Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 21: 2408.2341; Hours 22: 2311.9048; Hours 23: 2247.6852; Hours 0: 2344.0146; Hours 1: 2440.3439; Hours 2: 2472.4537; Hours 3: 2536.6733; Hours 4: 2536.6733; Hours 5: 2440.3439; Hours 6: 2504.5635 | 24242.8902
15 | Power Consumption of Chiller | KWH |  | Hours 20: 1500; Hours 21: 1400; Hours 22: 1500; Hours 23: 1500; Hours 0: 1500; Hours 1: 1600; Hours 2: 1400; Hours 3: 1600; Hours 4: 1500; Hours 5: 1500; Hours 6: 1500 | 16500
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 21: 0.58134; Hours 22: 0.64882; Hours 23: 0.66735; Hours 0: 0.63993; Hours 1: 0.65565; Hours 2: 0.56624; Hours 3: 0.63075; Hours 4: 0.59133; Hours 5: 0.61467; Hours 6: 0.59891 | 0.6195
17 | Average iKW/TR |  |  | Hours 7: 0.6195 | 0.6195
18 | COP of chiller |  |  | Hours 21: 6.0481; Hours 22: 5.4191; Hours 23: 5.2686; Hours 0: 5.4944; Hours 1: 5.3627; Hours 2: 6.2094; Hours 3: 5.5743; Hours 4: 5.946; Hours 5: 5.7202; Hours 6: 5.8707 | 5.6913
19 | EER of Chiller |  |  | Hours 21: 20.6422; Hours 22: 18.4954; Hours 23: 17.9816; Hours 0: 18.7523; Hours 1: 18.3027; Hours 2: 21.1927; Hours 3: 19.0252; Hours 4: 20.2936; Hours 5: 19.5229; Hours 6: 20.0367 | 19.4245
20 | LMTD of Condenser | ºC |  | Hours 21: 3.3625; Hours 22: 3.2951; Hours 23: 3.2951; Hours 0: 3.3289; Hours 1: 3.3625; Hours 2: 3.396; Hours 3: 3.4625; Hours 4: 3.4293; Hours 5: 3.5921; Hours 6: 3.6604 | 3.4184
21 | LMTD of Evaporator | ºC |  | Hours 21: 2.5141; Hours 22: 2.6332; Hours 23: 2.5849; Hours 0: 2.4683; Hours 1: 2.5369; Hours 2: 2.5597; Hours 3: 2.6051; Hours 4: 2.9801; Hours 5: 2.7289; Hours 6: 2.7764 | 2.6388
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.6 | 1.2 | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.3 | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.5 | 1.4 | 1.3 | [7 empty] | 1.3588
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.5 | 0.5 | [7 empty] | 0.47647
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.6 | 13.8 | 14.2 | 14.6 | 14.9 | 15.4 | 15.8 | 16.1 | 15.4 | 14.4 | 13.7 | [7 empty] | 14.2882
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 5.7 | 5.6 | 5.5 | 5.8 | 5.6 | 5.6 | 6.4 | 6.7 | 6.7 | 6.8 | 7.8 | 7.7 | 8.1 | 7.6 | 6.9 | 6.3 | [7 empty] | 6.5529
| Evaporator Delta "T" |  |  | 6.9 | 7.8 | 7.9 | 8 | 7.7 | 7.9 | 8 | 7.4 | 7.5 | 7.9 | 8.1 | 7.6 | 8.1 | 8 | 7.8 | 7.5 | 7.4 | [7 empty] | 7.7353
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.3 | 25.7 | 25.4 | 25.6 | 26.4 | 26.3 | 26.3 | 26.9 | 26.8 | 27.7 | 28.4 | 28.8 | 28.3 | 28.3 | 29.8 | 29.7 | 29.7 | [7 empty] | 27.3765
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.7 | 30.6 | 30.4 | 30.6 | 31.3 | 31.2 | 31.3 | 31.7 | 31.5 | 32.8 | 33.9 | 33.9 | 33.7 | 33.9 | 34.9 | 34.7 | 34.7 | [7 empty] | 32.4
| Condenser Delta "T" | ºC |  | 4.4 | 4.9 | 5 | 5 | 4.9 | 4.9 | 5 | 4.8 | 4.7 | 5.1 | 5.5 | 5.1 | 5.4 | 5.6 | 5.1 | 5 | 5 | [7 empty] | 5.0235
| Evaporator pressure (Kpag) | kpag |  | 262 | 251 | 249.6 | 248.2 | 252.3 | 250.3 | 250.3 | 259.9 | 261.3 | 263.4 | 262 | 275.1 | 275.8 | 276.5 | 277.9 | 266.8 | 257.9 | [7 empty] | 261.1941
| Condenser pressure (kpag) | kpag |  | 689.5 | 712.9 | 706 | 712.9 | 729.5 | 728.8 | 727.4 | 736.4 | 730.8 | 762.6 | 793.6 | 791.5 | 788.1 | 788.8 | 817 | 811.5 | 810.8 | [7 empty] | 755.1824
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | [7 empty] | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | [7 empty] | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2215.5754 | 2504.5635 | 2536.6733 | 2568.7831 | 2472.4537 | 2536.6733 | 2568.7831 | 2376.1243 | 2408.2341 | 2536.6733 | 2600.8929 | 2440.3439 | 2600.8929 | 2568.7831 | 2504.5635 | 2408.2341 | 2376.1243 | [7 empty] | 42224.3717
15 | Power Consumption of Chiller | KWH |  | 1400 | 1300 | 1500 | 1500 | 1400 | 1500 | 1500 | 1400 | 1600 | 1500 | 1600 | 1400 | 1600 | 1500 | 1500 | 1500 | 100 | [7 empty] | 23800
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.63189 | 0.51905 | 0.59133 | 0.58393 | 0.56624 | 0.59133 | 0.58393 | 0.58919 | 0.66439 | 0.59133 | 0.61517 | 0.57369 | 0.61517 | 0.58393 | 0.59891 | 0.62286 | 0.042085 | [7 empty] | 0.56261
17 | Average iKW/TR |  |  | Hours 7: 0.56261 | 0.56261
18 | COP of chiller |  |  | 5.5643 | 6.7739 | 5.946 | 6.0212 | 6.2094 | 5.946 | 6.0212 | 5.9675 | 5.2921 | 5.946 | 5.7155 | 6.1287 | 5.7155 | 6.0212 | 5.8707 | 5.6449 | 83.5445 | [7 empty] | 10.4899
19 | EER of Chiller |  |  | 18.9908 | 23.1193 | 20.2936 | 20.5504 | 21.1927 | 20.2936 | 20.5504 | 20.367 | 18.0619 | 20.2936 | 19.5069 | 20.9174 | 19.5069 | 20.5504 | 20.0367 | 19.266 | 285.1375 | [7 empty] | 35.8021
20 | LMTD of Condenser | ºC |  | 2.8563 | 3.4955 | 3.0446 | 3.2899 | 3.2578 | 3.2578 | 3.1682 | 3.1049 | 3.0731 | 3.3218 | 3.4482 | 3.3218 | 3.2932 | 3.355 | 3.4422 | 3.2899 | 3.1682 | [7 empty] | 3.2464
21 | LMTD of Evaporator | ºC |  | 2.3759 | 2.3666 | 2.8 | 2.8236 | 2.7527 | 2.8 | 2.8236 | 2.6811 | 2.5141 | 2.6051 | 2.6502 | 2.7289 | 2.8472 | 3.0046 | 2.9556 | 2.7051 | 2.6811 | [7 empty] | 2.7127

## 15-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 15/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | Hours 11: 0; Hours 12: 0; Hours 13: 0; Hours 14: 0; Hours 15: 0; Hours 16: 0; Hours 17: 0; Hours 18: 0; Hours 19: 0; Hours 20: 0; Hours 21: 0; Hours 22: 0; Hours 23: 0; Hours 0: 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | Hours 11: 0; Hours 12: 0; Hours 13: 0; Hours 14: 0; Hours 15: 0; Hours 16: 0; Hours 17: 0; Hours 18: 0; Hours 19: 0; Hours 20: 0; Hours 21: 0; Hours 22: 0; Hours 23: 0; Hours 0: 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 11: 4.2; Hours 12: 4.2; Hours 13: 4.2; Hours 14: 4.2; Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2; Hours 18: 4.2; Hours 19: 4.2; Hours 20: 4.2; Hours 21: 4.2; Hours 22: 4.2; Hours 23: 4.2; Hours 0: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 11: 3.7; Hours 12: 3.7; Hours 13: 3.7; Hours 14: 3.7; Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7; Hours 18: 3.7; Hours 19: 3.7; Hours 20: 3.7; Hours 21: 3.7; Hours 22: 3.7; Hours 23: 3.7; Hours 0: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 11: 0; Hours 12: 0; Hours 13: 0; Hours 14: 0; Hours 15: 0; Hours 16: 0; Hours 17: 0; Hours 18: 0; Hours 19: 0; Hours 20: 0; Hours 21: 0; Hours 22: 0; Hours 23: 0; Hours 0: 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 11: #DIV/0!; Hours 12: #DIV/0!; Hours 13: #DIV/0!; Hours 14: #DIV/0!; Hours 15: #DIV/0!; Hours 16: #DIV/0!; Hours 17: #DIV/0!; Hours 18: #DIV/0!; Hours 19: #DIV/0!; Hours 20: #DIV/0!; Hours 21: #DIV/0!; Hours 22: #DIV/0!; Hours 23: #DIV/0!; Hours 0: #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | Hours 11: #DIV/0!; Hours 12: #DIV/0!; Hours 13: #DIV/0!; Hours 14: #DIV/0!; Hours 15: #DIV/0!; Hours 16: #DIV/0!; Hours 17: #DIV/0!; Hours 18: #DIV/0!; Hours 19: #DIV/0!; Hours 20: #DIV/0!; Hours 21: #DIV/0!; Hours 22: #DIV/0!; Hours 23: #DIV/0!; Hours 0: #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | Hours 11: #DIV/0!; Hours 12: #DIV/0!; Hours 13: #DIV/0!; Hours 14: #DIV/0!; Hours 15: #DIV/0!; Hours 16: #DIV/0!; Hours 17: #DIV/0!; Hours 18: #DIV/0!; Hours 19: #DIV/0!; Hours 20: #DIV/0!; Hours 21: #DIV/0!; Hours 22: #DIV/0!; Hours 23: #DIV/0!; Hours 0: #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | Hours 11: #DIV/0!; Hours 12: #DIV/0!; Hours 13: #DIV/0!; Hours 14: #DIV/0!; Hours 15: #DIV/0!; Hours 16: #DIV/0!; Hours 17: #DIV/0!; Hours 18: #DIV/0!; Hours 19: #DIV/0!; Hours 20: #DIV/0!; Hours 21: #DIV/0!; Hours 22: #DIV/0!; Hours 23: #DIV/0!; Hours 0: #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | Hours 11: #DIV/0!; Hours 12: #DIV/0!; Hours 13: #DIV/0!; Hours 14: #DIV/0!; Hours 15: #DIV/0!; Hours 16: #DIV/0!; Hours 17: #DIV/0!; Hours 18: #DIV/0!; Hours 19: #DIV/0!; Hours 20: #DIV/0!; Hours 21: #DIV/0!; Hours 22: #DIV/0!; Hours 23: #DIV/0!; Hours 0: #DIV/0! | #DIV/0!
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.9 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.8 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.9 | 0.7 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.75
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.53333
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.6 | 13.4 | 13.7 | 13.5 | 13.2 | 13 | 13.6 | 14.1 | 14.4 | 14.7 | 14.4 | 14.5 | 14.3 | 14.3 | 14.4 | 14.2 | 13.3 | 12.9 | 13.1 | 13.2 | 13.3 | 13.2 | 13.1 | 12.9 | 13.6792
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.7 | 5.7 | 5.6 | 5.5 | 5.6 | 5.6 | 5.7 | 6 | 6.3 | 6.4 | 5.8 | 5.9 | 6 | 6.2 | 5.9 | 5.7 | 5.6 | 5.9 | 6.1 | 6.2 | 6.1 | 6.1 | 6.1 | 5.5 | 5.8833
| Evaporator Delta "T" |  |  | 7.9 | 7.7 | 8.1 | 8 | 7.6 | 7.4 | 7.9 | 8.1 | 8.1 | 8.3 | 8.6 | 8.6 | 8.3 | 8.1 | 8.5 | 8.5 | 7.7 | 7 | 7 | 7 | 7.2 | 7.1 | 7 | 7.4 | 7.7958
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.4 | 25.3 | 24.6 | 23.6 | 23.6 | 26.5 | 26.8 | 26.8 | 26.7 | 26.8 | 24.9 | 25.2 | 25.5 | 26.1 | 24.9 | 23.8 | 24.2 | 25.2 | 25.4 | 25.3 | 24.9 | 24.4 | 23.6 | 23.2 | 25.1125
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.8 | 29.6 | 29.2 | 28 | 27.9 | 30.7 | 31.2 | 31.4 | 31.3 | 31.5 | 29.7 | 30.1 | 30.2 | 30.8 | 29.8 | 28.7 | 28.5 | 29 | 29.3 | 29.3 | 29.1 | 28.3 | 27.4 | 27.3 | 29.5042
| Condenser Delta "T" | ºC |  | 4.4 | 4.3 | 4.6 | 4.4 | 4.3 | 4.2 | 4.4 | 4.6 | 4.6 | 4.7 | 4.8 | 4.9 | 4.7 | 4.7 | 4.9 | 4.9 | 4.3 | 3.8 | 3.9 | 4 | 4.2 | 3.9 | 3.8 | 4.1 | 4.3917
| Evaporator pressure (Kpag) | kpag |  | 251 | 251 | 247.5 | 246.8 | 248.9 | 248.9 | 251 | 253.7 | 257.2 | 258.6 | 251.7 | 253.7 | 253.7 | 254.4 | 252.3 | 248.2 | 248.2 | 255.1 | 255.8 | 256.5 | 255.8 | 257.2 | 256.5 | 248.9 | 252.6083
| Condenser pressure (kpag) | kpag |  | 681.2 | 678.4 | 667.4 | 643.3 | 639.8 | 698.4 | 712.2 | 717.1 | 715.7 | 719.1 | 677.1 | 686.7 | 690.9 | 704 | 682.6 | 655.7 | 652.2 | 662.6 | 668.8 | 668.8 | 660.5 | 646 | 627.4 | 625.4 | 674.2208
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2472.4537 | 2600.8929 | 2568.7831 | 2440.3439 | 2376.1243 | 2536.6733 | 2600.8929 | 2600.8929 | 2665.1124 | 2761.4418 | 2761.4418 | 2665.1124 | 2600.8929 | 2729.332 | 2729.332 | 2472.4537 | 2247.6852 | 2247.6852 | 2247.6852 | 2311.9048 | 2279.795 | 2247.6852 | 2376.1243 | 60077.414
15 | Power Consumption of Chiller | KWH |  | 1300 | 1500 | 1400 | 1400 | 1400 | 1500 | 1400 | 1500 | 1600 | 1500 | 1500 | 1700 | 1500 | 1500 | 1500 | 1500 | 1300 | 1200 | 1400 | 1300 | 1300 | 1300 | 1200 | 1300 | 34000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.51248 | 0.60668 | 0.53828 | 0.54501 | 0.57369 | 0.63128 | 0.5519 | 0.57673 | 0.61517 | 0.56283 | 0.54319 | 0.61562 | 0.56283 | 0.57673 | 0.54959 | 0.54959 | 0.52579 | 0.53388 | 0.62286 | 0.57837 | 0.56231 | 0.57023 | 0.53388 | 0.54711 | 0.56608
17 | Average iKW/TR |  |  | Hours 7: 0.56608 | 0.56608
18 | COP of chiller |  |  | 6.8607 | 5.7954 | 6.532 | 6.4513 | 6.1287 | 5.5696 | 6.3707 | 6.0965 | 5.7155 | 6.247 | 6.4728 | 5.7113 | 6.247 | 6.0965 | 6.3976 | 6.3976 | 6.687 | 6.5857 | 5.6449 | 6.0791 | 6.2528 | 6.166 | 6.5857 | 6.4265 | 6.2299
19 | EER of Chiller |  |  | 23.4157 | 19.7798 | 22.2936 | 22.0183 | 20.9174 | 19.0092 | 21.7431 | 20.8073 | 19.5069 | 21.3211 | 22.0917 | 19.4927 | 21.3211 | 20.8073 | 21.8349 | 21.8349 | 22.8229 | 22.4771 | 19.266 | 20.748 | 21.3409 | 21.0445 | 22.4771 | 21.9337 | 21.2627
20 | LMTD of Condenser | ºC |  | 2.4816 | 2.1871 | 2.2723 | 2.2156 | 2.3213 | 2.1584 | 2.3507 | 2.2723 | 2.409 | 2.4379 | 2.4667 | 2.4954 | 2.4379 | 2.3005 | 2.6299 | 2.3564 | 2.3213 | 2.1724 | 2.0715 | 2.1006 | 2.1584 | 2.0715 | 1.9072 | 2.1295 | 2.2802
21 | LMTD of Evaporator | ºC |  | 2.9801 | 2.931 | 2.8472 | 3.0046 | 2.9064 | 2.6811 | 2.9801 | 3.029 | 3.1998 | 3.0776 | 3.1501 | 3.1501 | 3.0776 | 2.8472 | 3.126 | 3.126 | 2.931 | 2.3991 | 2.3991 | 2.3991 | 2.4453 | 2.4222 | 2.3991 | 2.4912 | 2.8333
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.8 | 1.7 | 1.9 | 1.8 | 1.8 | 1.7 | 1.8 | 1.8 | 1.8 | 1.8 | 2 | 1.9 | 1.9 | 1.8 | 1.9 | 2 | 1.9 | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.7 | 1.8083
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.6 | 0.4 | 0.8 | 0.7 | 0.6 | 0.6 | 0.7 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.4 | 0.5 | 0.6 | 0.6 | 0.8 | 0.7 | 0.6
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.8 | 13.7 | 13.9 | 13.7 | 13.4 | 13.3 | 13.8 | 14.2 | 14.6 | 14.8 | 14.6 | 14.6 | 14.5 | 14.5 | 14.5 | 14.3 | 13.5 | 13.2 | 13.3 | 13.4 | 13.4 | 13.4 | 13.3 | 13.1 | 13.8667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6 | 6.1 | 6.1 | 5.8 | 5.6 | 5.9 | 5.9 | 6.2 | 6.4 | 6.6 | 6.1 | 6.2 | 6.1 | 6.2 | 6.1 | 5.7 | 5.3 | 5.9 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 5.7 | 6.0167
| Evaporator Delta "T" |  |  | 7.8 | 7.6 | 7.8 | 7.9 | 7.8 | 7.4 | 7.9 | 8 | 8.2 | 8.2 | 8.5 | 8.4 | 8.4 | 8.3 | 8.4 | 8.6 | 8.2 | 7.3 | 7.2 | 7.3 | 7.3 | 7.3 | 7.2 | 7.4 | 7.85
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.2 | 25.2 | 24.5 | 23.4 | 23.6 | 26.4 | 26.8 | 26.9 | 26.7 | 26.8 | 24.8 | 25.2 | 25.5 | 26.2 | 24.9 | 23.8 | 24.1 | 25.1 | 25.3 | 25.3 | 24.9 | 24.3 | 23.6 | 23.1 | 25.0667
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30 | 29.8 | 29.2 | 28.2 | 28.2 | 30.8 | 31.4 | 31.7 | 31.6 | 31.7 | 29.9 | 30.3 | 30.5 | 31.1 | 30.1 | 28.9 | 29.1 | 29.3 | 29.6 | 29.6 | 29.3 | 28.6 | 27.8 | 27.6 | 29.7625
| Condenser Delta "T" | ºC |  | 4.8 | 4.6 | 4.7 | 4.8 | 4.6 | 4.4 | 4.6 | 4.8 | 4.9 | 4.9 | 5.1 | 5.1 | 5 | 4.9 | 5.2 | 5.1 | 5 | 4.2 | 4.3 | 4.3 | 4.4 | 4.3 | 4.2 | 4.5 | 4.6958
| Evaporator pressure (Kpag) | kpag |  | 254.4 | 253.7 | 254.4 | 249.6 | 250.3 | 252.3 | 255.8 | 255.8 | 258.6 | 260.6 | 253.7 | 253.7 | 254.4 | 255.8 | 253.7 | 248.9 | 244.8 | 253 | 255.1 | 256.5 | 255.8 | 254.4 | 253 | 247.5 | 253.575
| Condenser pressure (kpag) | kpag |  | 708.1 | 706.7 | 691.5 | 668.8 | 668.8 | 724.6 | 737.7 | 748.8 | 749.5 | 752.2 | 712.2 | 719.1 | 721.9 | 736.4 | 715 | 690.9 | 689.5 | 692.9 | 697.7 | 699.1 | 690.9 | 675.7 | 658.4 | 655 | 704.6417
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2504.5635 | 2440.3439 | 2504.5635 | 2536.6733 | 2504.5635 | 2376.1243 | 2536.6733 | 2568.7831 | 2633.0026 | 2633.0026 | 2729.332 | 2697.2222 | 2697.2222 | 2665.1124 | 2697.2222 | 2761.4418 | 2633.0026 | 2344.0146 | 2311.9048 | 2344.0146 | 2344.0146 | 2344.0146 | 2311.9048 | 2376.1243 | 60494.8413
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1300 | 1300 | 1500 | 1500 | 1600 | 1500 | 1600 | 1500 | 1700 | 1500 | 1600 | 1500 | 1500 | 1500 | 1400 | 1500 | 1300 | 1400 | 1300 | 1300 | 1300 | 1300 | 34900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.59891 | 0.61467 | 0.51905 | 0.51248 | 0.59891 | 0.63128 | 0.63075 | 0.58393 | 0.60767 | 0.56969 | 0.62286 | 0.55613 | 0.5932 | 0.56283 | 0.55613 | 0.54319 | 0.53171 | 0.63993 | 0.56231 | 0.59727 | 0.5546 | 0.5546 | 0.56231 | 0.54711 | 0.57715
17 | Average iKW/TR |  |  | Hours 7: 0.57715 | 0.57715
18 | COP of chiller |  |  | 5.8707 | 5.7202 | 6.7739 | 6.8607 | 5.8707 | 5.5696 | 5.5743 | 6.0212 | 5.786 | 6.1718 | 5.6449 | 6.3223 | 5.9271 | 6.247 | 6.3223 | 6.4728 | 6.6126 | 5.4944 | 6.2528 | 5.8868 | 6.3397 | 6.3397 | 6.2528 | 6.4265 | 6.115
19 | EER of Chiller |  |  | 20.0367 | 19.5229 | 23.1193 | 23.4157 | 20.0367 | 19.0092 | 19.0252 | 20.5504 | 19.7477 | 21.0642 | 19.266 | 21.578 | 20.2293 | 21.3211 | 21.578 | 22.0917 | 22.5688 | 18.7523 | 21.3409 | 20.0917 | 21.6373 | 21.6373 | 21.3409 | 21.9337 | 20.8706
20 | LMTD of Condenser | ºC |  | 3.6943 | 3.6263 | 3.5454 | 3.8088 | 3.6263 | 3.5577 | 3.5117 | 3.6943 | 3.7282 | 3.7282 | 3.7954 | 4.0254 | 3.877 | 3.8429 | 3.8288 | 3.9109 | 3.9912 | 3.6007 | 3.4096 | 3.4096 | 3.4438 | 3.4096 | 3.4885 | 3.4778 | 3.668
21 | LMTD of Evaporator | ºC |  | 2.9556 | 2.9064 | 2.9556 | 2.6051 | 3.2843 | 3.0222 | 2.9801 | 3.0046 | 3.2249 | 3.0533 | 2.9408 | 3.1019 | 3.1019 | 3.0776 | 3.1019 | 3.1501 | 3.0533 | 2.6572 | 2.4453 | 2.6572 | 2.832 | 2.832 | 3.1269 | 3.0222 | 2.9622
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## 16-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 16/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 6: 1.8 | 1.8
2 | Small temperature difference of evaporator | ºC |  | Hours 6: 0.4 | 0.4
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 6: 13.1 | 13.1
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 6: 5.6 | 5.6
| Evaporator Delta "T" |  |  | Hours 6: 7.5 | 7.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 6: 24.8 | 24.8
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 6: 29.9 | 29.9
| Condenser Delta "T" | ºC |  | Hours 6: 5.1 | 5.1
| Evaporator pressure (Kpag) | kpag |  | Hours 6: 248.2 | 248.2
| Condenser pressure (kpag) | kpag |  | Hours 6: 706.7 | 706.7
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 6: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 6: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 6: 2408.2341 | 2408.2341
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1300 | 1800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 6: 0.53981 | 0.53981
17 | Average iKW/TR |  |  | Hours 7: 0.53981 | 0.53981
18 | COP of chiller |  |  | Hours 6: 6.5133 | 6.5133
19 | EER of Chiller |  |  | Hours 6: 22.2301 | 22.2301
20 | LMTD of Condenser | ºC |  | Hours 6: 3.7954 | 3.7954
21 | LMTD of Evaporator | ºC |  | Hours 6: 2.5141 | 2.5141
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC
2 | Small temperature difference of evaporator | ºC
3 | Entering Chilled Water Temp. (tchwe) | ºC
4 | Leaving Chilled Water Temp. (tchwl) | ºC
Evaporator Delta "T"
5 | Entering Condenser Water Temp. (tcwe) | ºC
6 | Leaving Condenser Water Temp. (tcwl) | ºC
| Condenser Delta "T" | ºC
| Evaporator pressure (Kpag) | kpag
| Condenser pressure (kpag) | kpag
7 | Chilled water inlet pressure | (Kg/Cm2)
8 | Chilled water outlet pressure | (Kg/Cm2)
9 | Condenser water inlet pressure | (Kg/Cm2)
10 | Condenser water outlet pressure | (Kg/Cm2)
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2)
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2)
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.)
14 | TR Genrated by Chiller | TR
15 | Power Consumption of Chiller | KWH
16 | Specific power consumption of Chiller | (iKW/TR)
17 | Average iKW/TR |  |  | Hours 7: #DIV/0!
18 | COP of chiller
19 | EER of Chiller
20 | LMTD of Condenser | ºC
21 | LMTD of Evaporator | ºC
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.6 | 0.8 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.9 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.75417
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.49583
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 12.4 | 12.6 | 12.7 | 12.8 | 12.7 | 12.9 | 13.4 | 13.8 | 14.1 | 14.4 | 14.6 | 14.8 | 14.7 | 14.5 | 14.2 | 13.9 | 13.4 | 13.1 | 13 | 13.2 | 13.1 | 13.1 | 13 | 13 | 13.475
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.5 | 5.6 | 5.5 | 5.6 | 5.5 | 5.5 | 5.9 | 6.2 | 6.4 | 6.3 | 6.4 | 6.2 | 6.1 | 5.9 | 5.8 | 5.4 | 5.4 | 5.7 | 5.6 | 5.4 | 5.6 | 5.7 | 5.7 | 5.7667
| Evaporator Delta "T" |  |  | 6.9 | 7.1 | 7.1 | 7.3 | 7.1 | 7.4 | 7.9 | 7.9 | 7.9 | 8 | 8.3 | 8.4 | 8.5 | 8.4 | 8.3 | 8.1 | 8 | 7.7 | 7.3 | 7.6 | 7.7 | 7.5 | 7.3 | 7.3 | 7.7083
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.2 | 23.4 | 23.3 | 23.6 | 24.3 | 25.6 | 26.5 | 26.7 | 26.7 | 26.8 | 26.3 | 26 | 25.3 | 25.1 | 25.4 | 25.1 | 24.7 | 25.4 | 26.4 | 26.3 | 25.9 | 25.8 | 25.5 | 25.1 | 25.35
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.2 | 27.3 | 27.2 | 27.7 | 28.2 | 29.8 | 30.9 | 31.1 | 31.2 | 31.3 | 30.9 | 30.8 | 30.1 | 29.8 | 30 | 29.7 | 29.2 | 29.6 | 30.6 | 30.6 | 30.4 | 30.1 | 29.6 | 29.2 | 29.6875
| Condenser Delta "T" | ºC |  | 4 | 3.9 | 3.9 | 4.1 | 3.9 | 4.2 | 4.4 | 4.4 | 4.5 | 4.5 | 4.6 | 4.8 | 4.8 | 4.7 | 4.6 | 4.6 | 4.5 | 4.2 | 4.2 | 4.3 | 4.5 | 4.3 | 4.1 | 4.1 | 4.3375
| Evaporator pressure (Kpag) | kpag |  | 249.6 | 249.6 | 250.3 | 248.2 | 251 | 249.6 | 248.2 | 253 | 255.1 | 258.6 | 257.9 | 258.6 | 255.8 | 253.7 | 251.7 | 251 | 246.8 | 246.8 | 250.3 | 249.6 | 246.8 | 247.5 | 249.6 | 251 | 251.2625
| Condenser pressure (kpag) | kpag |  | 622.6 | 625.4 | 624.7 | 636.4 | 646.7 | 682.6 | 707.4 | 711.5 | 714.3 | 716.4 | 709.5 | 703.3 | 690.9 | 684 | 688.8 | 679.1 | 667.4 | 675.7 | 697.1 | 699.1 | 694.3 | 690.2 | 677.1 | 666 | 679.6042
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2215.5754 | 2279.795 | 2279.795 | 2344.0146 | 2279.795 | 2376.1243 | 2536.6733 | 2536.6733 | 2536.6733 | 2568.7831 | 2665.1124 | 2697.2222 | 2729.332 | 2697.2222 | 2665.1124 | 2600.8929 | 2568.7831 | 2472.4537 | 2344.0146 | 2440.3439 | 2472.4537 | 2408.2341 | 2344.0146 | 2344.0146 | 59403.1085
15 | Power Consumption of Chiller | KWH |  | 1200 | 1300 | 1300 | 1300 | 1300 | 1500 | 1400 | 1500 | 1600 | 1400 | 1500 | 1600 | 1600 | 1500 | 1500 | 1500 | 1400 | 1400 | 1400 | 1500 | 1300 | 1500 | 1400 | 1300 | 34200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.54162 | 0.57023 | 0.57023 | 0.5546 | 0.57023 | 0.63128 | 0.5519 | 0.59133 | 0.63075 | 0.54501 | 0.56283 | 0.5932 | 0.58622 | 0.55613 | 0.56283 | 0.57673 | 0.54501 | 0.56624 | 0.59727 | 0.61467 | 0.52579 | 0.62286 | 0.59727 | 0.5546 | 0.57578
17 | Average iKW/TR |  |  | Hours 7: 0.57578 | 0.57578
18 | COP of chiller |  |  | 6.4916 | 6.166 | 6.166 | 6.3397 | 6.166 | 5.5696 | 6.3707 | 5.946 | 5.5743 | 6.4513 | 6.247 | 5.9271 | 5.9977 | 6.3223 | 6.247 | 6.0965 | 6.4513 | 6.2094 | 5.8868 | 5.7202 | 6.687 | 5.6449 | 5.8868 | 6.3397 | 6.121
19 | EER of Chiller |  |  | 22.156 | 21.0445 | 21.0445 | 21.6373 | 21.0445 | 19.0092 | 21.7431 | 20.2936 | 19.0252 | 22.0183 | 21.3211 | 20.2293 | 20.4702 | 21.578 | 21.3211 | 20.8073 | 22.0183 | 21.1927 | 20.0917 | 19.5229 | 22.8229 | 19.266 | 20.0917 | 21.6373 | 20.8911
20 | LMTD of Condenser | ºC |  | 2.2324 | 2.2025 | 2.0715 | 2.1295 | 1.9356 | 2.2918 | 2.2156 | 2.3507 | 2.3799 | 2.3799 | 2.2723 | 2.3285 | 2.4667 | 2.4379 | 2.5413 | 2.409 | 2.3799 | 2.1584 | 2.1584 | 2.1871 | 2.244 | 2.1871 | 2.2622 | 2.2622 | 2.2702
21 | LMTD of Evaporator | ºC |  | 2.3759 | 2.4222 | 2.4222 | 2.4683 | 2.6091 | 2.4912 | 2.8 | 2.9801 | 2.9801 | 3.0046 | 3.0776 | 3.1019 | 3.126 | 3.1019 | 3.0776 | 2.8472 | 3.0046 | 2.7527 | 2.4683 | 2.5369 | 2.5597 | 2.7051 | 2.4683 | 2.4683 | 2.7437
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.8 | 1.7 | 1.8 | 1.7 | 1.7 | 1.8 | 1.8 | 2 | 1.9 | 1.8 | 2 | 1.9 | 1.9 | 1.9 | 1.8 | 1.9 | 1.8 | 1.8 | 1.8 | 1.9 | 1.8 | 1.8 |  | 1.8304
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.58696
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 12.6 | 12.7 | 12.8 | 12.8 | 12.8 | 13.1 | 13.5 | 14 | 14.2 | 14.6 | 14.8 | 14.9 | 14.9 | 14.6 | 14.4 | 14.1 | 13.6 | 13.2 | 13.2 | 13.3 | 13.3 | 13.3 | 13.1 |  | 13.6435
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.4 | 5.7 | 5.7 | 5.7 | 5.6 | 5.7 | 5.8 | 5.9 | 6.2 | 6.3 | 6.4 | 6.4 | 6.3 | 6.1 | 6 | 5.8 | 5.4 | 5.3 | 5.4 | 5.6 | 5.6 | 5.4 | 5.4 |  | 5.787
| Evaporator Delta "T" |  |  | 7.2 | 7 | 7.1 | 7.1 | 7.2 | 7.4 | 7.7 | 8.1 | 8 | 8.3 | 8.4 | 8.5 | 8.6 | 8.5 | 8.4 | 8.3 | 8.2 | 7.9 | 7.8 | 7.7 | 7.7 | 7.9 | 7.7 |  | 7.8565
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.2 | 23.4 | 23.2 | 23.6 | 24.2 | 25.7 | 26.4 | 26.7 | 26.7 | 26.8 | 26.3 | 25.9 | 25.3 | 25.1 | 25.3 | 25.1 | 24.6 | 25.3 | 26.3 | 26.3 | 26 | 25.9 | 25.4 |  | 25.3348
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.5 | 27.6 | 27.6 | 27.8 | 28.6 | 30.1 | 31.2 | 31.4 | 31.5 | 31.7 | 31.3 | 31.1 | 30.4 | 30.2 | 30.3 | 30.1 | 29.5 | 29.9 | 31.1 | 30.9 | 30.7 | 30.5 | 30.1 |  | 30.0478
| Condenser Delta "T" | ºC |  | 4.3 | 4.2 | 4.4 | 4.2 | 4.4 | 4.4 | 4.8 | 4.7 | 4.8 | 4.9 | 5 | 5.2 | 5.1 | 5.1 | 5 | 5 | 4.9 | 4.6 | 4.8 | 4.6 | 4.7 | 4.6 | 4.7 |  | 4.713
| Evaporator pressure (Kpag) | kpag |  | 247.5 | 248.9 | 248.2 | 248.9 | 248.2 | 250.3 | 251.7 | 253 | 255.8 | 259.2 | 257.9 | 259.2 | 257.2 | 254.4 | 252.3 | 251 | 247.5 | 246.8 | 247.5 | 248.2 | 248.9 | 248.2 | 247.5 |  | 251.2304
| Condenser pressure (kpag) | kpag |  | 652.9 | 653.6 | 653.6 | 661.2 | 678.4 | 710.2 | 737 | 745.3 | 746.7 | 750.1 | 743.9 | 736.4 | 721.2 | 717.7 | 721.2 | 712.2 | 699.8 | 708.1 | 730.8 | 732.2 | 724.6 | 721.2 | 709.5 |  | 711.6435
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  | 971
14 | TR Genrated by Chiller | TR |  | 2311.9048 | 2247.6852 | 2279.795 | 2279.795 | 2311.9048 | 2376.1243 | 2472.4537 | 2600.8929 | 2568.7831 | 2665.1124 | 2697.2222 | 2729.332 | 2761.4418 | 2729.332 | 2697.2222 | 2665.1124 | 2633.0026 | 2536.6733 | 2504.5635 | 2472.4537 | 2472.4537 | 2536.6733 | 2472.4537 |  | 58022.3876
15 | Power Consumption of Chiller | KWH |  | 1300 | 1400 | 1200 | 1300 | 1500 | 1400 | 1500 | 1600 | 1400 | 1700 | 1600 | 1600 | 1500 | 1600 | 1400 | 1600 | 1400 | 1600 | 1400 | 1500 | 1600 | 1400 | 900 | 0 | 33400
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.56231 | 0.62286 | 0.52636 | 0.57023 | 0.64882 | 0.58919 | 0.60668 | 0.61517 | 0.54501 | 0.63787 | 0.5932 | 0.58622 | 0.54319 | 0.58622 | 0.51905 | 0.60035 | 0.53171 | 0.63075 | 0.55898 | 0.60668 | 0.64713 | 0.5519 | 0.36401 |  | 0.57582
17 | Average iKW/TR |  |  | Hours 7: 0.57582 | 0.57582
18 | COP of chiller |  |  | 6.2528 | 5.6449 | 6.6798 | 6.166 | 5.4191 | 5.9675 | 5.7954 | 5.7155 | 6.4513 | 5.5121 | 5.9271 | 5.9977 | 6.4728 | 5.9977 | 6.7739 | 5.8566 | 6.6126 | 5.5743 | 6.29 | 5.7954 | 5.4332 | 6.3707 | 9.6591 |  | 6.1898
19 | EER of Chiller |  |  | 21.3409 | 19.266 | 22.7982 | 21.0445 | 18.4954 | 20.367 | 19.7798 | 19.5069 | 22.0183 | 18.8127 | 20.2293 | 20.4702 | 22.0917 | 20.4702 | 23.1193 | 19.9885 | 22.5688 | 19.0252 | 21.4679 | 19.7798 | 18.5436 | 21.7431 | 32.9663 |  | 21.1258
20 | LMTD of Condenser | ºC |  | 3.5231 | 3.4885 | 3.4438 | 3.4885 | 3.4438 | 3.4438 | 3.6943 | 3.6604 | 3.9223 | 3.8429 | 3.7618 | 4.0595 | 3.9109 | 3.9109 | 3.877 | 3.7618 | 3.8429 | 3.6263 | 3.6943 | 3.6263 | 3.7744 | 3.6263 | 3.6604 |  | 3.6993
21 | LMTD of Evaporator | ºC |  | 2.8071 | 2.757 | 2.7821 | 2.9451 | 2.9709 | 2.6811 | 2.7527 | 2.8472 | 3.0046 | 3.0776 | 3.2749 | 3.2998 | 3.1501 | 3.126 | 3.2749 | 3.0776 | 3.0533 | 2.9801 | 2.7764 | 2.7527 | 2.7527 | 2.8 | 2.7527 |  | 2.9433
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC
2 | Small temperature difference of evaporator | ºC
3 | Entering Chilled Water Temp. (tchwe) | ºC
4 | Leaving Chilled Water Temp. (tchwl) | ºC
Evaporator Delta "T"
5 | Entering Condenser Water Temp. (tcwe) | ºC
6 | Leaving Condenser Water Temp. (tcwl) | ºC
| Condenser Delta "T" | ºC
| Evaporator pressure (Kpag) | kpag
| Condenser pressure (kpag) | kpag
7 | Chilled water inlet pressure | (Kg/Cm2)
8 | Chilled water outlet pressure | (Kg/Cm2)
9 | Condenser water inlet pressure | (Kg/Cm2)
10 | Condenser water outlet pressure | (Kg/Cm2)
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2)
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2)
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.)
14 | TR Genrated by Chiller | TR
15 | Power Consumption of Chiller | KWH
16 | Specific power consumption of Chiller | (iKW/TR)
17 | Average iKW/TR |  |  | Hours 7: #DIV/0!
18 | COP of chiller
19 | EER of Chiller
20 | LMTD of Condenser | ºC
21 | LMTD of Evaporator | ºC
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC
2 | Small temperature difference of evaporator | ºC
3 | Entering Chilled Water Temp. (tchwe) | ºC
4 | Leaving Chilled Water Temp. (tchwl) | ºC
Evaporator Delta "T"
5 | Entering Condenser Water Temp. (tcwe) | ºC
6 | Leaving Condenser Water Temp. (tcwl) | ºC
| Condenser Delta "T" | ºC
| Evaporator pressure (Kpag) | kpag
| Condenser pressure (kpag) | kpag
7 | Chilled water inlet pressure | (Kg/Cm2)
8 | Chilled water outlet pressure | (Kg/Cm2)
9 | Condenser water inlet pressure | (Kg/Cm2)
10 | Condenser water outlet pressure | (Kg/Cm2)
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2)
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2)
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.)
14 | TR Genrated by Chiller | TR
15 | Power Consumption of Chiller | KWH
16 | Specific power consumption of Chiller | (iKW/TR)
17 | Average iKW/TR |  |  | Hours 7: #DIV/0!
18 | COP of chiller
19 | EER of Chiller
20 | LMTD of Condenser | ºC
21 | LMTD of Evaporator | ºC

## 17-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 17/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.7 | 1.7 | 1.8 | 1.6 | 2 | 1.9 | 1.9 | 2 | 1.8 | 1.9 | 2.1 | 2.2 | 2.2 | 2.1 | 1.9 | 1.9 | 2.1 | 1.7 | 1.8 | 1.7 | 1.7 | 1.6 |  |  | 1.8773
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.6 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.9 | 1.1 | 0.8 |  |  | 0.67273
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.2 | 12.9 | 12.8 | 12.9 | 13.1 | 13.3 | 13.4 | 13.7 | 13.9 | 14.1 | 14 | 14 | 13.8 | 13.5 | 13.6 | 13.5 | 13.3 | 13.2 | 13.1 | 13.4 | 13.5 | 13.4 |  |  | 12.7
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.6 | 5.4 | 5.5 | 5.6 | 5.7 | 5.7 | 5.6 | 5.9 | 5.6 | 5.6 | 5.6 | 5.6 | 5.5 | 5.6 | 5.5 | 5.4 | 5.4 | 6.6 | 6.7 | 6.6 | 5.6 |  |  | 13.3
| Evaporator Delta "T" |  |  | 7.7 | 7.3 | 7.4 | 7.4 | 7.5 | 7.6 | 7.7 | 8.1 | 8 | 8.5 | 8.4 | 8.4 | 8.2 | 8 | 8 | 8 | 7.9 | 7.8 | 6.5 | 6.7 | 6.9 | 7.8 |  |  | 7.7182
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.8 | 24.2 | 23.8 | 23.3 | 25.1 | 25.7 | 26 | 24.9 | 25.2 | 24 | 24 | 24 | 24.4 | 24.8 | 25.2 | 25.4 | 25.7 | 25.7 | 25.4 | 25.1 | 25.1 | 25.2 |  |  | 21.8
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.1 | 29.4 | 29.2 | 28.6 | 30.2 | 30.9 | 31.4 | 30.7 | 30.8 | 29.9 | 29.9 | 29.8 | 30.1 | 30.4 | 30.8 | 31.3 | 31.1 | 31.2 | 30 | 30.1 | 29.9 | 30.6 |  |  | 21.8
| Condenser Delta "T" | ºC |  | 5.3 | 5.2 | 5.4 | 5.3 | 5.1 | 5.2 | 5.4 | 5.8 | 5.6 | 5.9 | 5.9 | 5.8 | 5.7 | 5.6 | 5.6 | 5.9 | 5.4 | 5.5 | 4.6 | 5 | 4.8 | 5.4 |  |  | 5.4273
| Evaporator pressure (Kpag) | kpag |  | 244.1 | 248.2 | 246.8 | 246.1 | 245.5 | 246.8 | 249.6 | 248.9 | 252.3 | 246.8 | 246.8 | 248.9 | 247.5 | 247.5 | 247.5 | 245.5 | 246.8 | 246.8 | 245.5 | 248.2 | 257.9 | 248.2 |  |  | 247.8273
| Condenser pressure (kpag) | kpag |  | 719.8 | 696.4 | 688.8 | 677.1 | 721.2 | 735.7 | 747.4 | 729.5 | 731.5 | 716.4 | 713.6 | 712.9 | 716.4 | 719.8 | 728.8 | 740.5 | 738.4 | 736.4 | 709.5 | 706 | 702.6 | 721.9 |  |  | 718.6636
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  |  | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  |  | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  | 971
14 | TR Genrated by Chiller | TR |  | 2472.4537 | 2344.0146 | 2376.1243 | 2376.1243 | 2408.2341 | 2440.3439 | 2472.4537 | 2600.8929 | 2568.7831 | 2729.332 | 2697.2222 | 2697.2222 | 2633.0026 | 2568.7831 | 2568.7831 | 2568.7831 | 2536.6733 | 2504.5635 | 2087.1362 | 2151.3558 | 2215.5754 | 2504.5635 |  |  | 54522.4206
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1500 | 1500 | 1500 | 1400 | 1400 | 1400 | 1400 | 1500 | 1400 | 1400 | 1300 | 1400 | 1100 | 1200 | 1400 | 1300 | 800 |  | 30700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.52579 | 0.5546 | 0.54711 | 0.54711 | 0.53981 | 0.53271 | 0.60668 | 0.57673 | 0.58393 | 0.51295 | 0.51905 | 0.51905 | 0.53171 | 0.58393 | 0.54501 | 0.54501 | 0.51248 | 0.55898 | 0.52704 | 0.55779 | 0.63189 | 0.51905 |  |  | 0.54902
17 | Average iKW/TR |  |  | Hours 7: 0.54902 | 0.54902
18 | COP of chiller |  |  | 6.687 | 6.3397 | 6.4265 | 6.4265 | 6.5133 | 6.6002 | 5.7954 | 6.0965 | 6.0212 | 6.8545 | 6.7739 | 6.7739 | 6.6126 | 6.0212 | 6.4513 | 6.4513 | 6.8607 | 6.29 | 6.6712 | 6.3035 | 5.5643 | 6.7739 |  |  | 6.4231
19 | EER of Chiller |  |  | 22.8229 | 21.6373 | 21.9337 | 21.9337 | 22.2301 | 22.5265 | 19.7798 | 20.8073 | 20.5504 | 23.3945 | 23.1193 | 23.1193 | 22.5688 | 20.5504 | 22.0183 | 22.0183 | 23.4157 | 21.4679 | 22.769 | 21.5138 | 18.9908 | 23.1193 |  |  | 21.9221
20 | LMTD of Condenser | ºC |  | 3.7448 | 3.7119 | 3.8953 | 3.6264 | 4.0254 | 3.9447 | 4.0118 | 4.2616 | 3.9613 | 4.1777 | 4.4112 | 4.4927 | 4.4587 | 4.3101 | 4.0785 | 4.1777 | 4.2421 | 3.8103 | 3.6263 | 3.6457 | 3.579 | 3.6588 |  |  | 3.9933
21 | LMTD of Evaporator | ºC |  | 2.5597 | 2.4683 | 2.8568 | 2.8568 | 3.206 | 2.9064 | 3.0987 | 3.029 | 3.0046 | 3.2998 | 3.2749 | 3.4393 | 3.2249 | 3.1746 | 3.0046 | 3.1746 | 2.9801 | 2.9556 | 2.6306 | 3.1404 | 3.4776 | 3.2843 |  |  | 3.0476
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.8 | 1 | 0.8 | 0.7 | 0.8 | 0.8 | 0.7 | 0.9 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.7 | 0.8 | 0.7 | 0.77917
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.50417
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 12.9 | 12.7 | 13.1 | 13 | 13.1 | 13.5 | 13.6 | 13.8 | 14 | 13.9 | 13.8 | 13.8 | 13.5 | 13.5 | 13.5 | 13.2 | 13.1 | 13 | 13.3 | 13.4 | 13.3 | 13.1 | 12.7 | 13.3292
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.7 | 5.5 | 5.5 | 5.5 | 5.6 | 5.7 | 5.6 | 5.6 | 5.7 | 5.6 | 5.6 | 5.5 | 5.6 | 5.5 | 5.6 | 5.5 | 5.6 | 5.5 | 6.3 | 6.6 | 6.6 | 5.7 | 5.5 | 6.3 | 5.725
| Evaporator Delta "T" |  |  | 7.4 | 7.4 | 7.2 | 7.6 | 7.4 | 7.4 | 7.9 | 8 | 8.1 | 8.4 | 8.3 | 8.3 | 8.2 | 8 | 7.9 | 8 | 7.6 | 7.6 | 6.7 | 6.7 | 6.8 | 7.6 | 7.6 | 6.4 | 7.6042
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.2 | 24.7 | 24.4 | 23.8 | 25.4 | 26 | 26.5 | 25.6 | 25.6 | 24.6 | 24.6 | 24.6 | 24.8 | 25.3 | 25.6 | 26 | 26.3 | 26.3 | 25.8 | 25.4 | 25.4 | 25.6 | 25.4 | 25 | 25.3292
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.4 | 28.8 | 28.3 | 27.8 | 29.6 | 30.2 | 30.9 | 29.9 | 30.2 | 29.2 | 29.1 | 29.1 | 29.4 | 29.7 | 29.9 | 30.4 | 30.5 | 30.7 | 29.4 | 29.1 | 29.3 | 29.8 | 29.8 | 28.7 | 29.55
| Condenser Delta "T" | ºC |  | 4.2 | 4.1 | 3.9 | 4 | 4.2 | 4.2 | 4.4 | 4.3 | 4.6 | 4.6 | 4.5 | 4.5 | 4.6 | 4.4 | 4.3 | 4.4 | 4.2 | 4.4 | 3.6 | 3.7 | 3.9 | 4.2 | 4.4 | 3.7 | 4.2208
| Evaporator pressure (Kpag) | kpag |  | 250.3 | 249.6 | 248.9 | 248.2 | 251.7 | 250.3 | 250.3 | 249.6 | 251 | 248.9 | 248.9 | 246.8 | 248.9 | 247.5 | 248.2 | 249.6 | 248.9 | 247.5 | 261.3 | 263.4 | 262 | 251 | 247.5 | 260.6 | 251.2875
| Condenser pressure (kpag) | kpag |  | 673.6 | 657.8 | 650.2 | 639.1 | 672.2 | 691.5 | 705.3 | 685.3 | 690.2 | 668.8 | 667.4 | 670.2 | 674.3 | 679.8 | 686.7 | 695.7 | 695.7 | 697.1 | 668.8 | 663.3 | 667.4 | 681.9 | 677.8 | 652.2 | 675.5125
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2376.1243 | 2376.1243 | 2311.9048 | 2440.3439 | 2376.1243 | 2376.1243 | 2536.6733 | 2568.7831 | 2600.8929 | 2697.2222 | 2665.1124 | 2665.1124 | 2633.0026 | 2568.7831 | 2536.6733 | 2568.7831 | 2440.3439 | 2440.3439 | 2151.3558 | 2151.3558 | 2183.4656 | 2440.3439 | 2440.3439 | 2055.0265 | 58600.3638
15 | Power Consumption of Chiller | KWH |  | 1400 | 1300 | 1300 | 1300 | 1300 | 1500 | 1400 | 1600 | 1500 | 1400 | 1600 | 1300 | 1600 | 1500 | 1400 | 1500 | 1400 | 1300 | 1300 | 1200 | 1400 | 1300 | 1400 | 1100 | 33300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58919 | 0.54711 | 0.56231 | 0.53271 | 0.54711 | 0.63128 | 0.5519 | 0.62286 | 0.57673 | 0.51905 | 0.60035 | 0.6 | 0.60767 | 0.58393 | 0.5519 | 0.58393 | 0.57369 | 0.53271 | 0.60427 | 0.55779 | 0.64118 | 0.53271 | 0.57369 | 0.53527 | 0.57331
17 | Average iKW/TR |  |  | Hours 7: 0.57331 | 0.57331
18 | COP of chiller |  |  | 5.9675 | 6.4265 | 6.2528 | 6.6002 | 6.4265 | 5.5696 | 6.3707 | 5.6449 | 6.0965 | 6.7739 | 5.8566 | 5.86 | 5.786 | 6.0212 | 6.3707 | 6.0212 | 6.1287 | 6.6002 | 5.8186 | 6.3035 | 5.4836 | 6.6002 | 6.1287 | 6.5686 | 6.1532
19 | EER of Chiller |  |  | 20.367 | 21.9337 | 21.3409 | 22.5265 | 21.9337 | 19.0092 | 21.7431 | 19.266 | 20.8073 | 23.1193 | 19.9885 | 20.0002 | 19.7477 | 20.5504 | 21.7431 | 20.5504 | 20.9174 | 22.5265 | 19.8588 | 21.5138 | 18.7156 | 22.5265 | 20.9174 | 22.4187 | 21.0009
20 | LMTD of Condenser | ºC |  | 2.2918 | 2.2622 | 2.2025 | 2.2324 | 2.2918 | 2.1584 | 2.3507 | 2.5784 | 2.409 | 2.2723 | 2.3799 | 2.3799 | 2.2723 | 2.4816 | 2.1871 | 2.3507 | 2.2918 | 2.3507 | 1.9832 | 2.0128 | 2.2025 | 2.1584 | 2.3507 | 2.0128 | 2.2693
21 | LMTD of Evaporator | ºC |  | 2.6811 | 2.4912 | 2.6332 | 2.5369 | 2.4912 | 2.4912 | 2.6051 | 3.0046 | 3.029 | 3.1019 | 3.2499 | 3.0776 | 3.0533 | 3.0046 | 2.9801 | 3.0046 | 2.5369 | 2.7289 | 2.512 | 2.3293 | 2.3526 | 2.5369 | 2.5369 | 2.6051 | 2.7323
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 6: 1.6 | 1.6
2 | Small temperature difference of evaporator | ºC |  | Hours 6: 0.4 | 0.4
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 6: 13.3 | 14.9
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 6: 6.6 | 6.3
| Evaporator Delta "T" |  |  | Hours 6: 6.7 | 6.7
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 6: 24.9 | 21.8
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 6: 28.8 | 27.2
| Condenser Delta "T" | ºC |  | Hours 6: 3.9 | 3.9
| Evaporator pressure (Kpag) | kpag |  | Hours 6: 261.3 | 252.3
| Condenser pressure (kpag) | kpag |  | Hours 6: 678.4 | 641.9
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 6: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 6: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 6: 2151.3558 | 2151.3558
15 | Power Consumption of Chiller | KWH |  | Hours 5: 500; Hours 6: 1300 | 1800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 6: 0.60427 | 0.60427
17 | Average iKW/TR |  |  | Hours 7: 0.60427 | 0.60427
18 | COP of chiller |  |  | Hours 6: 5.8186 | 5.8186
19 | EER of Chiller |  |  | Hours 6: 19.8588 | 19.8588
20 | LMTD of Condenser | ºC |  | Hours 6: 3.1585 | 3.1585
21 | LMTD of Evaporator | ºC |  | Hours 6: 2.3293 | 2.3293
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## 18-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 18/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 6: 1.8 | 1.8
2 | Small temperature difference of evaporator | ºC |  | Hours 6: 0.4 | 0.4
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 6: 12.7 | 12.7
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 6: 6.6 | 6.6
| Evaporator Delta "T" |  |  | Hours 6: 6.1 | 6.1
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 6: 24.6 | 24.6
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 6: 28.9 | 28.9
| Condenser Delta "T" | ºC |  | Hours 6: 4.3 | 4.3
| Evaporator pressure (Kpag) | kpag |  | Hours 6: 263.4 | 263.4
| Condenser pressure (kpag) | kpag |  | Hours 6: 675.7 | 675.7
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 6: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 6: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 6: 1958.6971 | 1958.6971
15 | Power Consumption of Chiller | KWH |  | Hours 5: 300; Hours 6: 1200 | 1500
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 6: 0.61265 | 0.61265
17 | Average iKW/TR |  |  | Hours 7: 0.61265 | 0.61265
18 | COP of chiller |  |  | Hours 6: 5.739 | 5.739
19 | EER of Chiller |  |  | Hours 6: 19.5871 | 19.5871
20 | LMTD of Condenser | ºC |  | Hours 6: 3.5231 | 3.5231
21 | LMTD of Evaporator | ºC |  | Hours 6: 2.1879 | 2.1879
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [9 empty] | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) | [9 empty] | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) | [9 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [9 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [9 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [9 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [9 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller | [10 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller | [10 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.7 | 0.7 | 0.7 | 0.8 | 0.6 | 0.6 | 0.8 | 0.7 | 0.7 | 0.7 | 0.6 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  | 0.7087
2 | Small temperature difference of evaporator | ºC |  | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 |  | 0.5
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.2 | 13.4 | 13.3 | 13.1 | 12.8 | 13 | 13.5 | 13.6 | 13.7 | 13.8 | 13.6 | 13.6 | 13.6 | 13.6 | 13.6 | 13.5 | 13.6 | 13.6 | 13.6 | 13.2 | 12.9 | 12.9 | 12.8 |  | 13.3696
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 5.7 | 5.5 | 5.6 | 6.3 | 6.2 | 5.7 | 5.6 | 5.6 | 5.6 | 5.6 | 5.4 | 5.6 | 5.6 | 5.4 | 5.4 | 5.6 | 5.6 | 5.6 | 5.6 | 5.4 | 5.4 | 5.4 |  | 5.6522
| Evaporator Delta "T" |  |  | 6.6 | 7.7 | 7.8 | 7.5 | 6.5 | 6.8 | 7.8 | 8 | 8.1 | 8.2 | 8 | 8.2 | 8 | 8 | 8.2 | 8.1 | 8 | 8 | 8 | 7.6 | 7.5 | 7.5 | 7.4 |  | 7.7174
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.9 | 24.8 | 22.9 | 22.1 | 22.9 | 24.8 | 26 | 25.6 | 25.1 | 24.8 | 24.4 | 24.9 | 25.2 | 25.2 | 25.6 | 25.6 | 25.7 | 25.7 | 25.8 | 25.7 | 25.8 | 25.7 | 25.4 |  | 24.9826
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.5 | 29 | 27.2 | 26.3 | 26.3 | 28.6 | 30.4 | 30.1 | 29.7 | 29.7 | 28.9 | 29.4 | 29.6 | 29.7 | 30.2 | 30.1 | 30.2 | 30.3 | 30.4 | 29.9 | 30.1 | 29.8 | 29.7 |  | 29.3087
| Condenser Delta "T" | ºC |  | 3.6 | 4.2 | 4.3 | 4.2 | 3.4 | 3.8 | 4.4 | 4.5 | 4.6 | 4.9 | 4.5 | 4.5 | 4.4 | 4.5 | 4.6 | 4.5 | 4.5 | 4.6 | 4.6 | 4.2 | 4.3 | 4.1 | 4.3 |  | 4.3261
| Evaporator pressure (Kpag) | kpag |  | 262 | 250.3 | 248.2 | 249.6 | 260.6 | 255.1 | 251 | 248.2 | 248.2 | 249.6 | 248.2 | 247.5 | 247.5 | 248.9 | 248.2 | 247.5 | 248.9 | 247.5 | 248.9 | 248.9 | 246.8 | 248.2 | 248.2 |  | 249.913
| Condenser pressure (kpag) | kpag |  | 651.6 | 661.9 | 624 | 606 | 604.7 | 655 | 695.7 | 687.4 | 677.8 | 678.4 | 661.9 | 670.9 | 679.8 | 677.1 | 689.5 | 688.8 | 688.8 | 690.9 | 693.6 | 684 | 686 | 680.5 | 677.8 |  | 670.0913
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  | 971
14 | TR Genrated by Chiller | TR |  | 2119.246 | 2472.4537 | 2504.5635 | 2408.2341 | 2087.1362 | 2183.4656 | 2504.5635 | 2568.7831 | 2600.8929 | 2633.0026 | 2568.7831 | 2633.0026 | 2568.7831 | 2568.7831 | 2633.0026 | 2600.8929 | 2568.7831 | 2568.7831 | 2568.7831 | 2440.3439 | 2408.2341 | 2408.2341 | 2376.1243 |  | 56994.8743
15 | Power Consumption of Chiller | KWH |  | 1400 | 1300 | 1300 | 1100 | 1200 | 1500 | 1400 | 1500 | 1500 | 1400 | 1500 | 1400 | 1600 | 1400 | 1600 | 1400 | 1500 | 1500 | 1400 | 1400 | 1400 | 1400 | 1000 |  | 32100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.66061 | 0.52579 | 0.51905 | 0.45677 | 0.57495 | 0.68698 | 0.55898 | 0.58393 | 0.57673 | 0.53171 | 0.58393 | 0.53171 | 0.62286 | 0.54501 | 0.60767 | 0.53828 | 0.58393 | 0.58393 | 0.54501 | 0.57369 | 0.58134 | 0.58134 | 0.42085 |  | 0.56413
17 | Average iKW/TR |  |  | Hours 7: 0.56413 | 0.56413
18 | COP of chiller |  |  | 5.3223 | 6.687 | 6.7739 | 7.6976 | 6.1153 | 5.118 | 6.29 | 6.0212 | 6.0965 | 6.6126 | 6.0212 | 6.6126 | 5.6449 | 6.4513 | 5.786 | 6.532 | 6.0212 | 6.0212 | 6.4513 | 6.1287 | 6.0481 | 6.0481 | 8.3545 |  | 6.2981
19 | EER of Chiller |  |  | 18.1651 | 22.8229 | 23.1193 | 26.2719 | 20.8716 | 17.4679 | 21.4679 | 20.5504 | 20.8073 | 22.5688 | 20.5504 | 22.5688 | 19.266 | 22.0183 | 19.7477 | 22.2936 | 20.5504 | 20.5504 | 22.0183 | 20.9174 | 20.6422 | 20.6422 | 28.5137 |  | 21.4953
20 | LMTD of Condenser | ºC |  | 1.9832 | 2.1584 | 2.1871 | 2.2918 | 1.7922 | 1.9072 | 2.3507 | 2.244 | 2.2723 | 2.3564 | 2.1027 | 2.3799 | 2.3507 | 2.244 | 2.2723 | 2.3799 | 2.3799 | 2.1301 | 2.2723 | 2.1584 | 2.1871 | 2.1295 | 2.1871 |  | 2.2051
21 | LMTD of Evaporator | ºC |  | 2.1049 | 2.3451 | 2.5824 | 2.5141 | 2.463 | 2.1491 | 2.5824 | 2.8236 | 2.8472 | 3.0533 | 3.0046 | 3.0533 | 2.8236 | 3.0046 | 3.0533 | 3.029 | 3.0046 | 3.0046 | 3.0046 | 2.9064 | 2.7051 | 2.7051 | 2.4912 |  | 2.7502
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.6 | 1.6 | 1.8 | 1.8 | 1.8 | 1.6 | 1.8 | 1.8 | 1.8 | 1.8 | 1.7 | 1.8 | 1.7 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.7 | 1.7 | 1.7 | 1.7 | 1.75
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.5 | 0.4 | 0.6 | 0.6 | 0.7 | 0.6 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.4 | 0.4 | 0.4 | 0.5 | 0.47917
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.3 | 13.5 | 13.5 | 13.3 | 12.9 | 13.1 | 13.7 | 13.6 | 13.8 | 13.9 | 13.7 | 13.7 | 13.7 | 13.8 | 13.7 | 13.7 | 13.7 | 13.7 | 13.8 | 13.3 | 13.2 | 13.1 | 13.1 | 12.9 | 13.4875
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 5.7 | 5.6 | 5.5 | 6.4 | 6.5 | 5.8 | 5.7 | 5.7 | 5.7 | 5.6 | 5.7 | 5.6 | 5.6 | 5.6 | 5.6 | 5.7 | 5.7 | 5.8 | 5.6 | 5.4 | 5.4 | 5.4 | 6.4 | 5.7625
| Evaporator Delta "T" |  |  | 6.7 | 7.8 | 7.9 | 7.8 | 6.5 | 6.6 | 7.9 | 7.9 | 8.1 | 8.2 | 8.1 | 8 | 8.1 | 8.2 | 8.1 | 8.1 | 8 | 8 | 8 | 7.7 | 7.8 | 7.7 | 7.7 | 6.5 | 7.725
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.9 | 24.8 | 22.8 | 22 | 22.8 | 24.8 | 26.1 | 25.6 | 25.1 | 24.9 | 24.4 | 24.8 | 25.1 | 25.1 | 25.6 | 25.6 | 25.7 | 25.7 | 25.8 | 25.7 | 25.8 | 25.7 | 25.5 | 25.1 | 24.975
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.8 | 29.4 | 27.4 | 26.7 | 26.7 | 28.6 | 30.7 | 30.4 | 29.9 | 29.8 | 29.3 | 29.7 | 30.1 | 30.1 | 30.5 | 30.4 | 30.5 | 30.5 | 30.6 | 30.4 | 30.4 | 30.2 | 30.1 | 28.8 | 29.5833
| Condenser Delta "T" | ºC |  | 3.9 | 4.6 | 4.6 | 4.7 | 3.9 | 3.8 | 4.6 | 4.8 | 4.8 | 4.9 | 4.9 | 4.9 | 5 | 5 | 4.9 | 4.8 | 4.8 | 4.8 | 4.8 | 4.7 | 4.6 | 4.5 | 4.6 | 3.7 | 4.6083
| Evaporator pressure (Kpag) | kpag |  | 261.3 | 250.3 | 247.5 | 246.1 | 257.9 | 255.8 | 251.7 | 250.3 | 250.3 | 250.3 | 249.6 | 249.6 | 248.9 | 248.2 | 248.9 | 249.6 | 250.3 | 250.3 | 251.7 | 248.9 | 248.2 | 248.2 | 248.2 | 259.9 | 250.9167
| Condenser pressure (kpag) | kpag |  | 678.4 | 692.9 | 652.9 | 637.1 | 629.5 | 672.9 | 724.6 | 716.4 | 706.7 | 708.1 | 690.2 | 699.8 | 710.2 | 710.2 | 719.8 | 717.1 | 718.4 | 719.8 | 721.9 | 714.3 | 715 | 709.5 | 706.7 | 675.7 | 697.8375
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2151.3558 | 2504.5635 | 2536.6733 | 2504.5635 | 2087.1362 | 2119.246 | 2536.6733 | 2536.6733 | 2600.8929 | 2633.0026 | 2600.8929 | 2568.7831 | 2600.8929 | 2633.0026 | 2600.8929 | 2600.8929 | 2568.7831 | 2568.7831 | 2568.7831 | 2472.4537 | 2504.5635 | 2472.4537 | 2472.4537 | 2087.1362 | 59531.5476
15 | Power Consumption of Chiller | KWH |  | 1300 | 1500 | 1300 | 1200 | 1300 | 1400 | 1400 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1600 | 1400 | 1600 | 1400 | 1500 | 1500 | 1400 | 1500 | 1300 | 1200 | 34300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.60427 | 0.59891 | 0.51248 | 0.47913 | 0.62286 | 0.66061 | 0.5519 | 0.59133 | 0.57673 | 0.56969 | 0.57673 | 0.58393 | 0.57673 | 0.56969 | 0.61517 | 0.53828 | 0.62286 | 0.54501 | 0.58393 | 0.60668 | 0.55898 | 0.60668 | 0.52579 | 0.57495 | 0.57722
17 | Average iKW/TR |  |  | Hours 7: 0.57722 | 0.57722
18 | COP of chiller |  |  | 5.8186 | 5.8707 | 6.8607 | 7.3384 | 5.6449 | 5.3223 | 6.3707 | 5.946 | 6.0965 | 6.1718 | 6.0965 | 6.0212 | 6.0965 | 6.1718 | 5.7155 | 6.532 | 5.6449 | 6.4513 | 6.0212 | 5.7954 | 6.29 | 5.7954 | 6.687 | 6.1153 | 6.1198
19 | EER of Chiller |  |  | 19.8588 | 20.0367 | 23.4157 | 25.0459 | 19.266 | 18.1651 | 21.7431 | 20.2936 | 20.8073 | 21.0642 | 20.8073 | 20.5504 | 20.8073 | 21.0642 | 19.5069 | 22.2936 | 19.266 | 22.0183 | 20.5504 | 19.7798 | 21.4679 | 19.7798 | 22.8229 | 20.8716 | 20.8868
20 | LMTD of Condenser | ºC |  | 3.1585 | 3.396 | 3.6263 | 3.6604 | 3.3834 | 3.124 | 3.6263 | 3.6943 | 3.6943 | 3.7282 | 3.6124 | 3.7282 | 3.6457 | 3.7618 | 3.7282 | 3.6943 | 3.6943 | 3.6943 | 3.6943 | 3.6604 | 3.5117 | 3.4778 | 3.5117 | 3.2013 | 3.5712
21 | LMTD of Evaporator | ºC |  | 2.3293 | 2.7764 | 2.6051 | 2.9556 | 2.6306 | 2.815 | 2.9801 | 2.6051 | 2.6502 | 3.0533 | 3.029 | 3.0046 | 2.6502 | 2.6727 | 2.6502 | 2.6502 | 2.6277 | 2.6277 | 2.6277 | 2.931 | 2.5824 | 2.5597 | 2.5597 | 2.463 | 2.7099
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  | 4.2 | 4.2 | 4.2 |  |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | [6 empty] | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  | 3.7 | 3.7 | 3.7 |  |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | [6 empty] | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  | 3.8 | 3.8 | 3.8 |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [6 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  | 3 | 3 | 3 |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [6 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  | 0.5 | 0.5 | 0.5 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [6 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  | 0.8 | 0.8 | 0.8 |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [6 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  | 971 | 971 | 971 |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [6 empty] | 971
14 | TR Genrated by Chiller | TR |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0!
19 | EER of Chiller |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0!
20 | LMTD of Condenser | ºC |  |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC |  |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0!

## 19-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 19/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.5 | 1.7 | 1.7 | 1.6 | 1.8 | 1.6 | 1.8 | 1.6 | 1.6 | 1.7 | 1.8 | 1.7 | 1.7 | 1.8 | 1.6 | 1.8 | 1.4 | 1.6 | 1.6 | 1.4 | 1.6 | 1.4 | 1.5 | 1.5 | 1.625
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 1.1 | 0.7 | 0.8 | 0.8 | 0.6 | 0.6 | 0.8 | 0.8 | 0.5 | 0.6 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 1.4 | 1.6 | 1.2 | 1.1 | 0.76667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.4 | 13.4 | 13.2 | 13.1 | 12.9 | 13.7 | 13.6 | 13.7 | 14.1 | 14.2 | 14.2 | 13.8 | 13.7 | 13.6 | 13.4 | 13.5 | 13.6 | 13.4 | 13.3 | 13.1 | 13.3 | 13.3 | 13.2 | 13.2 | 13.4958
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.9 | 5.5 | 5.6 | 5.6 | 5.4 | 5.9 | 6.2 | 6.4 | 5.8 | 5.8 | 5.7 | 5.5 | 5.5 | 5.5 | 5.6 | 5.5 | 5.5 | 5.5 | 5.4 | 6.7 | 6.6 | 6.5 | 6.6 | 6.5 | 5.8625
| Evaporator Delta "T" |  |  | 7.5 | 7.9 | 7.6 | 7.5 | 7.5 | 7.8 | 7.4 | 7.3 | 8.3 | 8.4 | 8.5 | 8.3 | 8.2 | 8.1 | 7.8 | 8 | 8.1 | 7.9 | 7.9 | 6.4 | 6.7 | 6.8 | 6.6 | 6.7 | 7.6333
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.6 | 23.8 | 23.3 | 23.5 | 24.4 | 25.7 | 25.9 | 25.8 | 25.9 | 25.4 | 24.8 | 23.6 | 23.3 | 24.4 | 24.4 | 24.5 | 24.7 | 25 | 25 | 24.8 | 24.3 | 23.9 | 23.3 | 23.6 | 24.4958
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.9 | 29.5 | 28.6 | 28.8 | 29.3 | 31 | 31.1 | 31.1 | 31.4 | 31.1 | 30.8 | 29.4 | 29 | 29.8 | 29.7 | 29.9 | 30.1 | 30.4 | 30.3 | 29.2 | 29.1 | 28.7 | 27.9 | 28.2 | 29.7625
| Condenser Delta "T" | ºC |  | 5.3 | 5.7 | 5.3 | 5.3 | 4.9 | 5.3 | 5.2 | 5.3 | 5.5 | 5.7 | 6 | 5.8 | 5.7 | 5.4 | 5.3 | 5.4 | 5.4 | 5.4 | 5.3 | 4.4 | 4.8 | 4.8 | 4.6 | 4.6 | 5.2667
| Evaporator pressure (Kpag) | kpag |  | 245.5 | 245.5 | 242.7 | 244.8 | 247.5 | 252.3 | 254.4 | 255.1 | 251.7 | 251 | 247.5 | 245.5 | 246.8 | 246.8 | 248.2 | 246.8 | 246.8 | 247.5 | 246.8 | 250.3 | 249.6 | 255.8 | 256.5 | 255.8 | 249.2167
| Condenser pressure (kpag) | kpag |  | 706.7 | 696.4 | 680.5 | 679.1 | 694.3 | 728.8 | 729.5 | 725.3 | 742.6 | 732.2 | 727.4 | 696.4 | 683.3 | 702.6 | 702.6 | 704.6 | 707.4 | 712.2 | 710.2 | 685.3 | 679.1 | 669.5 | 656.4 | 657.8 | 700.425
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2536.6733 | 2440.3439 | 2408.2341 | 2408.2341 | 2504.5635 | 2376.1243 | 2344.0146 | 2665.1124 | 2697.2222 | 2729.332 | 2665.1124 | 2633.0026 | 2600.8929 | 2504.5635 | 2568.7831 | 2600.8929 | 2536.6733 | 2536.6733 | 2055.0265 | 2151.3558 | 2183.4656 | 2119.246 | 2151.3558 | 58825.1323
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1300 | 1200 | 1400 | 1400 | 1200 | 1600 | 1400 | 1400 | 1500 | 1500 | 1200 | 1400 | 1400 | 1400 | 1300 | 1500 | 1200 | 1200 | 1100 | 1100 | 1100 | 1200 | 31600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53981 | 0.51248 | 0.53271 | 0.49829 | 0.58134 | 0.55898 | 0.50502 | 0.68259 | 0.52531 | 0.51905 | 0.54959 | 0.56283 | 0.45575 | 0.53828 | 0.55898 | 0.54501 | 0.49983 | 0.59133 | 0.47306 | 0.58393 | 0.51131 | 0.50379 | 0.51905 | 0.55779 | 0.53775
17 | Average iKW/TR |  |  | Hours 7: 0.53775 | 0.53775
18 | COP of chiller |  |  | 6.5133 | 6.8607 | 6.6002 | 7.0561 | 6.0481 | 6.29 | 6.962 | 5.151 | 6.6932 | 6.7739 | 6.3976 | 6.247 | 7.7147 | 6.532 | 6.29 | 6.4513 | 7.0344 | 5.946 | 7.4325 | 6.0212 | 6.8765 | 6.9792 | 6.7739 | 6.3035 | 6.5812
19 | EER of Chiller |  |  | 22.2301 | 23.4157 | 22.5265 | 24.0826 | 20.6422 | 21.4679 | 23.7615 | 17.5803 | 22.844 | 23.1193 | 21.8349 | 21.3211 | 26.3303 | 22.2936 | 21.4679 | 22.0183 | 24.0085 | 20.2936 | 25.367 | 20.5504 | 23.4695 | 23.8198 | 23.1193 | 21.5138 | 22.4616
20 | LMTD of Condenser | ºC |  | 3.5065 | 3.8753 | 3.7448 | 3.6264 | 3.7282 | 3.6264 | 3.8288 | 3.6264 | 3.691 | 3.8753 | 4.0918 | 3.9076 | 3.8753 | 3.8953 | 3.6264 | 3.8953 | 3.4167 | 3.6588 | 3.6264 | 3.0956 | 3.4625 | 3.2256 | 3.2791 | 3.2791 | 3.6444
21 | LMTD of Evaporator | ºC |  | 2.5141 | 3.7585 | 3.0733 | 3.206 | 3.206 | 2.9556 | 2.8568 | 3.1533 | 3.4136 | 2.9175 | 3.126 | 3.2499 | 3.2249 | 3.029 | 2.9556 | 3.0046 | 3.029 | 2.9801 | 2.8 | 2.4384 | 3.8168 | 4.1008 | 3.526 | 3.4204 | 3.1565
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.5; Hours 8: 1.6; Hours 9: 1.7; Hours 10: 1.7 | 1.625
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.4; Hours 8: 0.5; Hours 9: 0.4; Hours 10: 0.6 | 0.475
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 13.4; Hours 8: 13.5; Hours 9: 13.3; Hours 10: 13.2 | 13.35
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 5.9; Hours 8: 5.6; Hours 9: 5.6; Hours 10: 5.6 | 5.675
| Evaporator Delta "T" |  |  | Hours 7: 7.5; Hours 8: 7.9; Hours 9: 7.7; Hours 10: 7.6 | 7.675
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 25.1; Hours 8: 24.4; Hours 9: 23.7; Hours 10: 23.9 | 24.275
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 29.4; Hours 8: 29.2; Hours 9: 28.3; Hours 10: 28.3 | 28.8
| Condenser Delta "T" | ºC |  | Hours 7: 4.3; Hours 8: 4.8; Hours 9: 4.6; Hours 10: 4.4 | 4.525
| Evaporator pressure (Kpag) | kpag |  | Hours 7: 252.3; Hours 8: 248.9; Hours 9: 248.9; Hours 10: 248.2 | 249.575
| Condenser pressure (kpag) | kpag |  | Hours 7: 692.9; Hours 8: 688.8; Hours 9: 668.1; Hours 10: 669.5 | 679.825
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.2; Hours 8: 4.2; Hours 9: 4.2; Hours 10: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.7; Hours 8: 3.7; Hours 9: 3.7; Hours 10: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 10: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 10: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2408.2341; Hours 8: 2536.6733; Hours 9: 2472.4537; Hours 10: 2440.3439 | 9857.705
15 | Power Consumption of Chiller | KWH |  | Hours 7: 1500; Hours 8: 1400; Hours 9: 1300; Hours 10: 1400 | 5600
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.62286; Hours 8: 0.5519; Hours 9: 0.52579; Hours 10: 0.57369 | 0.56856
17 | Average iKW/TR |  |  | Hours 7: 0.56856 | 0.56856
18 | COP of chiller |  |  | Hours 7: 5.6449; Hours 8: 6.3707; Hours 9: 6.687; Hours 10: 6.1287 | 6.2078
19 | EER of Chiller |  |  | Hours 7: 19.266; Hours 8: 21.7431; Hours 9: 22.8229; Hours 10: 20.9174 | 21.1874
20 | LMTD of Condenser | ºC |  | Hours 7: 3.1795; Hours 8: 3.4625; Hours 9: 3.5117; Hours 10: 3.4438 | 3.3994
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.5141; Hours 8: 2.8; Hours 9: 2.5597; Hours 10: 2.9064 | 2.6951
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | [5 empty] | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | [5 empty] | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [5 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [5 empty] | 971
14 | TR Genrated by Chiller | TR |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | #DIV/0!
19 | EER of Chiller | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | #DIV/0!
20 | LMTD of Condenser | ºC |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [6 empty] | 1.3 | 1.3 | 1.3 | 1.3 | 1.4 | 1.2 | 1.2 | 1.4 | 1.3 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.1 | 1.2 | 1.3 | 1.3 | 1.2895
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.52105
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 13.7 | 13.6 | 13.8 | 14.1 | 14.2 | 14.2 | 14 | 13.7 | 13.6 | 13.4 | 13.5 | 13.5 | 13.5 | 13.2 | 13.1 | 13.2 | 13.3 | 13.2 | 13.2 | 13.5789
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 5.8 | 5.6 | 5.7 | 5.8 | 5.9 | 5.9 | 5.6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.5 | 6.2 | 6.4 | 6.4 | 6.6 | 6.6 | 5.8526
| Evaporator Delta "T" | [7 empty] | 7.9 | 8 | 8.1 | 8.3 | 8.3 | 8.3 | 8.4 | 8.2 | 8.1 | 7.9 | 8 | 7.9 | 7.9 | 7.7 | 6.9 | 6.8 | 6.9 | 6.6 | 6.6 | 7.7263
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 25.7 | 26.1 | 25.9 | 25.9 | 25.6 | 25.2 | 23.8 | 23.5 | 24.5 | 24.6 | 24.7 | 24.8 | 25.1 | 25.2 | 24.9 | 24.4 | 24.2 | 23.6 | 23.7 | 24.8105
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 30.9 | 31.5 | 31.5 | 31.4 | 31.2 | 30.8 | 29.5 | 29.1 | 29.9 | 30.1 | 30.2 | 30.2 | 30.4 | 30.4 | 29.6 | 28.9 | 28.8 | 28.2 | 28.1 | 30.0368
| Condenser Delta "T" | ºC | [6 empty] | 5.2 | 5.4 | 5.6 | 5.5 | 5.6 | 5.6 | 5.7 | 5.6 | 5.4 | 5.5 | 5.5 | 5.4 | 5.3 | 5.2 | 4.7 | 4.5 | 4.6 | 4.6 | 4.4 | 5.2263
| Evaporator pressure (Kpag) | kpag | [6 empty] | 251.7 | 250.3 | 251 | 252.3 | 252.3 | 253.7 | 249.6 | 247.5 | 247.5 | 247.5 | 247.5 | 250.3 | 250.3 | 248.9 | 258.6 | 262 | 261.3 | 262.7 | 263.4 | 253.0737
| Condenser pressure (kpag) | kpag | [6 empty] | 725.3 | 734.3 | 732.2 | 733.6 | 727.4 | 716.4 | 686.7 | 679.1 | 698.4 | 700.5 | 701.9 | 701.2 | 707.4 | 706 | 685.3 | 673.6 | 668.8 | 653.6 | 654.3 | 699.2632
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 2536.6733 | 2568.7831 | 2600.8929 | 2665.1124 | 2665.1124 | 2665.1124 | 2697.2222 | 2633.0026 | 2600.8929 | 2536.6733 | 2568.7831 | 2536.6733 | 2536.6733 | 2472.4537 | 2215.5754 | 2183.4656 | 2215.5754 | 2119.246 | 2119.246 | 47137.1693
15 | Power Consumption of Chiller | KWH | [5 empty] | 1200 | 1500 | 1500 | 1400 | 1600 | 1600 | 1500 | 1500 | 1300 | 1600 | 1500 | 1400 | 1400 | 1400 | 1400 | 1200 | 1300 | 1200 | 1100 | 1300 | 27900
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.59133 | 0.58393 | 0.53828 | 0.60035 | 0.60035 | 0.56283 | 0.55613 | 0.49373 | 0.61517 | 0.59133 | 0.54501 | 0.5519 | 0.5519 | 0.56624 | 0.54162 | 0.59538 | 0.54162 | 0.51905 | 0.61343 | 0.56629
17 | Average iKW/TR |  |  | Hours 7: 0.56629 | 0.56629
18 | COP of chiller | [7 empty] | 5.946 | 6.0212 | 6.532 | 5.8566 | 5.8566 | 6.247 | 6.3223 | 7.1213 | 5.7155 | 5.946 | 6.4513 | 6.3707 | 6.3707 | 6.2094 | 6.4916 | 5.9054 | 6.4916 | 6.7739 | 5.7317 | 6.2295
19 | EER of Chiller | [7 empty] | 20.2936 | 20.5504 | 22.2936 | 19.9885 | 19.9885 | 21.3211 | 21.578 | 24.3049 | 19.5069 | 20.2936 | 22.0183 | 21.7431 | 21.7431 | 21.1927 | 22.156 | 20.1552 | 22.156 | 23.1193 | 19.5624 | 21.2613
20 | LMTD of Condenser | ºC | [6 empty] | 3.2309 | 3.2932 | 3.355 | 3.3241 | 3.4795 | 3.2284 | 3.2586 | 3.4795 | 3.2932 | 3.4482 | 3.3241 | 3.2932 | 3.2621 | 3.2309 | 3.0731 | 2.7651 | 2.9196 | 3.0411 | 2.9768 | 3.2251
21 | LMTD of Evaporator | ºC | [6 empty] | 2.9801 | 3.0046 | 3.029 | 3.0776 | 3.0776 | 3.0776 | 3.1019 | 3.0533 | 3.029 | 2.9801 | 3.0046 | 2.9801 | 2.6051 | 2.5597 | 2.3759 | 2.1491 | 2.3759 | 2.3059 | 2.3059 | 2.7933

## 20-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 20/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.3 | 1.4 | 1.4 | 1.3 | 1.5 | 1.5 | 1.5 | 1 | 1.5 | 1.7 | 1.4 | 1.6 | 1.5 | 1.5 | 1.5 | 1.4 | 1.6 | 1.6 | 1.5 | 1.6 | 1.3 | 1.3 | 1.4 |  | 1.4478
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.8 | 1.2 | 0.7 | 1 | 0.8 | 1 | 2.8 | 1.3 | 0.6 | 0.5 | 0.6 | 0.5 | 0.7 | 0.6 | 0.7 | 0.7 | 0.6 | 0.6 | 1.6 | 0.7 | 0.7 | 1.1 |  | 0.89565
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.3 | 13.1 | 13.6 | 13.6 | 13.4 | 13.4 | 13.6 | 13.8 | 13.6 | 13.5 | 13.4 | 13.4 | 13.4 | 13.4 | 13.3 | 13.2 | 13.3 | 13.3 | 13.1 | 13.5 | 13.5 | 13.5 | 13.4 |  | 13.4174
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.5 | 6.7 | 6.5 | 6.5 | 6.4 | 6.4 | 9.1 | 6.4 | 5.4 | 5.6 | 5.5 | 5.6 | 5.6 | 5.4 | 5.6 | 5.6 | 5.7 | 5.4 | 6.4 | 6.4 | 6.6 | 6.7 | 6.7 |  | 6.2043
| Evaporator Delta "T" |  |  | 6.8 | 6.4 | 7.1 | 7.1 | 7 | 7 | 4.5 | 7.4 | 8.2 | 7.9 | 7.9 | 7.8 | 7.8 | 8 | 7.7 | 7.6 | 7.6 | 7.9 | 6.7 | 7.1 | 6.9 | 6.8 | 6.7 |  | 7.213
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.6 | 23.6 | 22.6 | 22 | 21.9 | 24.3 | 20.8 | 22.1 | 23.7 | 23.4 | 23.3 | 23.7 | 23.6 | 23.2 | 22.9 | 23.1 | 24.4 | 23.9 | 24.6 | 24.9 | 24.9 | 24.6 | 23.9 |  | 23.4348
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.3 | 28.3 | 27.4 | 26.9 | 26.9 | 29.6 | 24.4 | 27.3 | 29.3 | 28.7 | 28.6 | 29.1 | 28.8 | 28.6 | 28.2 | 28.2 | 29.6 | 29.3 | 29.1 | 29.7 | 29.8 | 29.3 | 28.7 |  | 28.4391
| Condenser Delta "T" | ºC |  | 4.7 | 4.7 | 4.8 | 4.9 | 5 | 5.3 | 3.6 | 5.2 | 5.6 | 5.3 | 5.3 | 5.4 | 5.2 | 5.4 | 5.3 | 5.1 | 5.2 | 5.4 | 4.5 | 4.8 | 4.9 | 4.7 | 4.8 |  | 5.0043
| Evaporator pressure (Kpag) | kpag |  | 251.7 | 251 | 257.2 | 255.8 | 255.1 | 254.4 | 264.1 | 254.4 | 244.8 | 248.2 | 246.8 | 248.9 | 248.2 | 244.8 | 246.1 | 246.8 | 249.6 | 246.8 | 258.6 | 257.9 | 255.1 | 253.7 | 254.4 |  | 251.9304
| Condenser pressure (kpag) | kpag |  | 662.6 | 661.9 | 644.7 | 634.3 | 635.7 | 689.5 | 576.4 | 637.8 | 691.5 | 674.3 | 671.5 | 684.6 | 681.9 | 676.4 | 666.7 | 663.3 | 692.2 | 685.3 | 677.8 | 693.6 | 693.6 | 686.7 | 670.2 |  | 667.5
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  | 971
14 | TR Genrated by Chiller | TR |  | 2183.4656 | 2055.0265 | 2279.795 | 2279.795 | 2247.6852 | 2247.6852 | 1444.9405 | 2376.1243 | 2633.0026 | 2536.6733 | 2536.6733 | 2504.5635 | 2504.5635 | 2568.7831 | 2472.4537 | 2440.3439 | 2440.3439 | 2536.6733 | 2151.3558 | 2279.795 | 2215.5754 | 2183.4656 | 2151.3558 |  | 53270.1389
15 | Power Consumption of Chiller | KWH |  | 1100 | 1200 | 1200 | 1100 | 1100 | 800 | 1200 | 1300 | 1300 | 1300 | 1400 | 1300 | 1300 | 1300 | 1400 | 1200 | 1300 | 1300 | 1200 | 1200 | 1200 | 1100 | 1000 | 0 | 27800
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.50379 | 0.58393 | 0.52636 | 0.4825 | 0.48939 | 0.35592 | 0.83048 | 0.54711 | 0.49373 | 0.51248 | 0.5519 | 0.51905 | 0.51905 | 0.50608 | 0.56624 | 0.49173 | 0.53271 | 0.51248 | 0.55779 | 0.52636 | 0.54162 | 0.50379 | 0.46482 |  | 0.52693
17 | Average iKW/TR |  |  | Hours 7: 0.52693 | 0.52693
18 | COP of chiller |  |  | 6.9792 | 6.0212 | 6.6798 | 7.2871 | 7.1844 | 9.8786 | 4.2337 | 6.4265 | 7.1213 | 6.8607 | 6.3707 | 6.7739 | 6.7739 | 6.9476 | 6.2094 | 7.1502 | 6.6002 | 6.8607 | 6.3035 | 6.6798 | 6.4916 | 6.9792 | 7.5642 |  | 6.799
19 | EER of Chiller |  |  | 23.8198 | 20.5504 | 22.7982 | 24.8707 | 24.5204 | 33.7156 | 14.4495 | 21.9337 | 24.3049 | 23.4157 | 21.7431 | 23.1193 | 23.1193 | 23.7121 | 21.1927 | 24.4037 | 22.5265 | 23.4157 | 21.5138 | 22.7982 | 22.156 | 23.8198 | 25.8165 |  | 23.205
20 | LMTD of Condenser | ºC |  | 3.0731 | 3.1933 | 3.2256 | 3.1366 | 3.4099 | 3.5065 | 2.9417 | 2.85 | 3.6021 | 3.7448 | 3.3852 | 3.6588 | 3.4744 | 3.5385 | 3.5065 | 3.3218 | 3.5938 | 3.6588 | 3.2461 | 3.4625 | 3.1366 | 3.0731 | 3.2256 |  | 3.3463
21 | LMTD of Evaporator | ºC |  | 3.0205 | 2.9128 | 3.6713 | 2.9451 | 3.3663 | 3.0739 | 2.6397 | 5.7242 | 4.1228 | 2.9801 | 2.8 | 2.9556 | 2.7764 | 3.1746 | 2.931 | 3.0733 | 3.0733 | 2.9801 | 2.6814 | 4.1929 | 2.8933 | 2.8673 | 3.4204 |  | 3.2294
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 6: 0.72 | 0.72
2 | Small temperature difference of evaporator | ºC |  | Hours 6: 0.5 | 0.5
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 6: 13.1 | 13.1
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 6: 6.8 | 6.8
| Evaporator Delta "T" |  |  | Hours 6: 6.3 | 6.3
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 6: 24.1 | 24.1
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 6: 27.2 | 27.2
| Condenser Delta "T" | ºC |  | Hours 6: 3.1 | 3.1
| Evaporator pressure (Kpag) | kpag |  | Hours 6: 266.8 | 266.8
| Condenser pressure (kpag) | kpag |  | Hours 6: 625.4 | 625.4
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 6: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 6: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 6: 2022.9167 | 2022.9167
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1100 | 1200
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 6: 0.54377 | 0.54377
17 | Average iKW/TR |  |  | Hours 7: 0.54377 | 0.54377
18 | COP of chiller |  |  | Hours 6: 6.466 | 6.466
19 | EER of Chiller |  |  | Hours 6: 22.0684 | 22.0684
20 | LMTD of Condenser | ºC |  | Hours 6: 1.8577 | 1.8577
21 | LMTD of Evaporator | ºC |  | Hours 6: 2.4137 | 2.4137
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.3 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.3 | 1.6 | 1.5 | 1.3 | 1.3 | 1.4 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 1.3 | 1.2 | 1.2 | 1.3 | 1.3083
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.5 | 0.8 | 0.7 | 0.6 | 0.4 | 0.6 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.50417
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.2 | 13.3 | 13.7 | 13.7 | 13.5 | 13.5 | 13.6 | 13.8 | 13.7 | 13.4 | 13.4 | 13.6 | 13.6 | 13.4 | 13.3 | 13.2 | 13.3 | 13.4 | 13.2 | 13.6 | 13.6 | 13.4 | 13.3 | 13.2 | 13.4542
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 6.6 | 6.7 | 6.4 | 6.5 | 6.6 | 5.6 | 5.5 | 5.6 | 5.4 | 5.5 | 5.5 | 5.6 | 5.6 | 5.5 | 5.5 | 5.6 | 5.5 | 6.4 | 6.6 | 6.5 | 6.5 | 6.4 | 6.7 | 6.0375
| Evaporator Delta "T" |  |  | 6.6 | 6.7 | 7 | 7.3 | 7 | 6.9 | 8 | 8.3 | 8.1 | 8 | 7.9 | 8.1 | 8 | 7.8 | 7.8 | 7.7 | 7.7 | 7.9 | 6.8 | 7 | 7.1 | 6.9 | 6.9 | 6.5 | 7.4167
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.8 | 23.7 | 22.8 | 22.1 | 22.3 | 24.7 | 21.2 | 22.2 | 23.8 | 23.6 | 23.4 | 23.9 | 23.9 | 23.4 | 23.2 | 23.3 | 24.6 | 24.2 | 24.7 | 25 | 25.1 | 24.7 | 24.1 | 23.8 | 23.6458
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.3 | 28.2 | 27.6 | 27.1 | 27 | 29.3 | 26.7 | 27.8 | 29.3 | 29 | 28.8 | 29.2 | 29.3 | 28.7 | 28.4 | 28.3 | 29.8 | 29.5 | 29.2 | 29.6 | 29.8 | 29.6 | 28.9 | 28.2 | 28.65
| Condenser Delta "T" | ºC |  | 4.5 | 4.5 | 4.8 | 5 | 4.7 | 4.6 | 5.5 | 5.6 | 5.5 | 5.4 | 5.4 | 5.3 | 5.4 | 5.3 | 5.2 | 5 | 5.2 | 5.3 | 4.5 | 4.6 | 4.7 | 4.9 | 4.8 | 4.4 | 5.0042
| Evaporator pressure (Kpag) | kpag |  | 262.7 | 263.4 | 262.7 | 258.6 | 259.9 | 262 | 243.4 | 246.1 | 249.6 | 248.2 | 247.5 | 248.9 | 249.6 | 248.9 | 247.5 | 248.2 | 249.6 | 248.9 | 259.2 | 262.7 | 262 | 261.3 | 259.2 | 264.1 | 254.7583
| Condenser pressure (kpag) | kpag |  | 658.4 | 655 | 641.9 | 632.2 | 631.6 | 684 | 630.2 | 649.5 | 684 | 675.7 | 670.2 | 684 | 681.2 | 670.9 | 665.3 | 662.6 | 692.2 | 685.3 | 679.1 | 690.2 | 691.5 | 685.3 | 672.2 | 655.7 | 667.8417
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2119.246 | 2151.3558 | 2247.6852 | 2344.0146 | 2247.6852 | 2215.5754 | 2568.7831 | 2665.1124 | 2600.8929 | 2568.7831 | 2536.6733 | 2600.8929 | 2568.7831 | 2504.5635 | 2504.5635 | 2472.4537 | 2472.4537 | 2536.6733 | 2183.4656 | 2247.6852 | 2279.795 | 2215.5754 | 2215.5754 | 2087.1362 | 57155.4233
15 | Power Consumption of Chiller | KWH |  | 1100 | 1200 | 1200 | 1200 | 1300 | 1400 | 1300 | 1500 | 1300 | 1500 | 1300 | 1500 | 1400 | 1400 | 1400 | 1300 | 1500 | 1300 | 1200 | 1200 | 1400 | 1300 | 1200 | 1300 | 31700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.51905 | 0.55779 | 0.53388 | 0.51194 | 0.57837 | 0.63189 | 0.50608 | 0.56283 | 0.49983 | 0.58393 | 0.51248 | 0.57673 | 0.54501 | 0.55898 | 0.55898 | 0.52579 | 0.60668 | 0.51248 | 0.54959 | 0.53388 | 0.61409 | 0.58676 | 0.54162 | 0.62286 | 0.55548
17 | Average iKW/TR |  |  | Hours 7: 0.55548 | 0.55548
18 | COP of chiller |  |  | 6.7739 | 6.3035 | 6.5857 | 6.868 | 6.0791 | 5.5643 | 6.9476 | 6.247 | 7.0344 | 6.0212 | 6.8607 | 6.0965 | 6.4513 | 6.29 | 6.29 | 6.687 | 5.7954 | 6.8607 | 6.3976 | 6.5857 | 5.7255 | 5.9923 | 6.4916 | 5.6449 | 6.3581
19 | EER of Chiller |  |  | 23.1193 | 21.5138 | 22.4771 | 23.4404 | 20.748 | 18.9908 | 23.7121 | 21.3211 | 24.0085 | 20.5504 | 23.4157 | 20.8073 | 22.0183 | 21.4679 | 21.4679 | 22.8229 | 19.7798 | 23.4157 | 21.8349 | 22.4771 | 19.5413 | 20.4516 | 22.156 | 19.266 | 21.7001
20 | LMTD of Condenser | ºC |  | 3.009 | 2.8881 | 2.9824 | 3.1682 | 3.0731 | 3.0411 | 3.3241 | 3.7232 | 3.5704 | 3.2932 | 3.2932 | 3.3852 | 3.4167 | 3.2621 | 3.2309 | 3.1682 | 3.2309 | 3.2621 | 3.009 | 2.9196 | 3.0731 | 3.0136 | 2.9824 | 2.9768 | 3.179
21 | LMTD of Evaporator | ºC |  | 2.3059 | 2.3293 | 2.3991 | 2.832 | 2.757 | 2.7319 | 2.8236 | 3.4136 | 3.1998 | 3.0046 | 2.6051 | 3.029 | 2.6277 | 2.7764 | 2.9556 | 2.931 | 2.931 | 2.8 | 2.5363 | 2.1931 | 2.4222 | 2.3759 | 2.3759 | 2.0827 | 2.685

## 21-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 21/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.6 | 0.7 | 0.6 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.8 | 0.6 | 0.7 | 0.6 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.675
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.5 | 0.5 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.5 | 0.4 | 0.5 | 0.6 | 0.6 | 0.45833
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.2 | 13.3 | 13.4 | 13.1 | 13.3 | 13.4 | 13.2 | 13 | 13.5 | 13.6 | 13.7 | 13.8 | 14 | 14.1 | 14.1 | 14.1 | 14.1 | 13.3 | 13.1 | 12.8 | 13.4 | 14.8 | 15.6 | 15.8 | 13.7375
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.5 | 5.7 | 5.4 | 6.5 | 6.6 | 5.6 | 5.5 | 6.6 | 6.5 | 5.5 | 6.4 | 6.5 | 6.6 | 6.5 | 6.6 | 6.4 | 5.9 | 5.6 | 5.4 | 5.4 | 5.7 | 6.1 | 6.6 | 6.9 | 6.125
| Evaporator Delta "T" |  |  | 6.7 | 7.6 | 8 | 6.6 | 6.7 | 7.8 | 7.7 | 6.4 | 7 | 8.1 | 7.3 | 7.3 | 7.4 | 7.6 | 7.5 | 7.7 | 8.2 | 7.7 | 7.7 | 7.4 | 7.7 | 8.7 | 9 | 8.9 | 7.6125
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.1 | 24.1 | 23.6 | 22.6 | 22.3 | 22.8 | 22.8 | 22 | 22.2 | 22.2 | 22.9 | 23.4 | 23.6 | 24 | 24.6 | 25.1 | 25.3 | 25.7 | 25.5 | 25.3 | 25.1 | 25.3 | 25.4 | 25.4 | 23.9708
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.8 | 28.3 | 28 | 26.1 | 25.8 | 27.1 | 27 | 25.4 | 25.9 | 26.6 | 26.7 | 27.4 | 27.7 | 28.3 | 28.7 | 29.2 | 30.1 | 30 | 29.7 | 29.4 | 29.5 | 30.2 | 30.6 | 30.4 | 28.1625
| Condenser Delta "T" | ºC |  | 3.7 | 4.2 | 4.4 | 3.5 | 3.5 | 4.3 | 4.2 | 3.4 | 3.7 | 4.4 | 3.8 | 4 | 4.1 | 4.3 | 4.1 | 4.1 | 4.8 | 4.3 | 4.2 | 4.1 | 4.4 | 4.9 | 5.2 | 5 | 4.1917
| Evaporator pressure (Kpag) | kpag |  | 262 | 250.3 | 247.5 | 262 | 264.1 | 250.3 | 247.5 | 262 | 262 | 248.9 | 261.3 | 262.7 | 262.7 | 262 | 263.4 | 259.9 | 252.3 | 248.9 | 248.2 | 248.2 | 250.3 | 255.1 | 259.2 | 266.8 | 256.5667
| Condenser pressure (kpag) | kpag |  | 634.3 | 647.4 | 640.5 | 598.5 | 593.6 | 621.2 | 619.1 | 583.3 | 595 | 611.6 | 613.6 | 626 | 632.2 | 642.6 | 655 | 668.1 | 684.6 | 683.3 | 676.4 | 669.5 | 671.5 | 690.2 | 698.4 | 692.2 | 643.6708
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2151.3558 | 2440.3439 | 2568.7831 | 2119.246 | 2151.3558 | 2504.5635 | 2472.4537 | 2055.0265 | 2247.6852 | 2600.8929 | 2344.0146 | 2344.0146 | 2376.1243 | 2440.3439 | 2408.2341 | 2472.4537 | 2633.0026 | 2472.4537 | 2472.4537 | 2376.1243 | 2472.4537 | 2793.5516 | 2889.881 | 2857.7712 | 58664.5833
15 | Power Consumption of Chiller | KWH |  | 1300 | 1400 | 1200 | 1100 | 1300 | 1300 | 1100 | 1200 | 1200 | 1200 | 1200 | 1300 | 1300 | 1400 | 1300 | 1300 | 1600 | 1300 | 1500 | 1300 | 1400 | 1700 | 1600 | 1500 | 32000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.60427 | 0.57369 | 0.46715 | 0.51905 | 0.60427 | 0.51905 | 0.4449 | 0.58393 | 0.53388 | 0.46138 | 0.51194 | 0.5546 | 0.54711 | 0.57369 | 0.53981 | 0.52579 | 0.60767 | 0.52579 | 0.60668 | 0.54711 | 0.56624 | 0.60854 | 0.55366 | 0.52488 | 0.54605
17 | Average iKW/TR |  |  | Hours 7: 0.54605 | 0.54605
18 | COP of chiller |  |  | 5.8186 | 6.1287 | 7.5265 | 6.7739 | 5.8186 | 6.7739 | 7.9029 | 6.0212 | 6.5857 | 7.6206 | 6.868 | 6.3397 | 6.4265 | 6.1287 | 6.5133 | 6.687 | 5.786 | 6.687 | 5.7954 | 6.4265 | 6.2094 | 5.7777 | 6.3505 | 6.6986 | 6.486
19 | EER of Chiller |  |  | 19.8588 | 20.9174 | 25.6881 | 23.1193 | 19.8588 | 23.1193 | 26.9725 | 20.5504 | 22.4771 | 26.0092 | 23.4404 | 21.6373 | 21.9337 | 20.9174 | 22.2301 | 22.8229 | 19.7477 | 22.8229 | 19.7798 | 21.9337 | 21.1927 | 19.7194 | 21.6743 | 22.8624 | 22.1369
20 | LMTD of Condenser | ºC |  | 2.0128 | 2.1584 | 2.2156 | 1.9534 | 1.8212 | 2.1871 | 2.0198 | 1.9234 | 1.8787 | 2.2156 | 1.9072 | 2.1006 | 2.1295 | 2.1871 | 2.2622 | 1.9918 | 2.3285 | 2.0476 | 2.1584 | 2.1295 | 2.0752 | 2.3564 | 2.4395 | 2.3842 | 2.1202
21 | LMTD of Evaporator | ºC |  | 2.3293 | 2.5369 | 2.8236 | 2.4875 | 2.1271 | 2.5824 | 2.5597 | 2.2589 | 2.1931 | 3.029 | 2.4683 | 2.4683 | 2.4912 | 2.7289 | 2.5141 | 2.5597 | 2.8707 | 2.931 | 2.931 | 2.6811 | 2.5597 | 2.9873 | 3.2461 | 3.2222 | 2.6495
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.3 | 1.4 | 1.3 | 1.1 | 1.3 | 1.5 | 1.3 | 1.3 | 1.3 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 1.3 | 1.4 |  |  |  |  | 1.4 | 1.31
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.5 | 0.5 | 0.6 | 0.5 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.5 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 |  |  |  |  | 0.6 | 0.58
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.4 | 13.4 | 13.5 | 13.2 | 13.4 | 13.5 | 13.4 | 13.1 | 13.6 | 13.8 | 13.8 | 13.9 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 13.4 | 13.1 |  |  |  |  | 16 | 13.775
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 5.6 | 5.6 | 6.4 | 6.6 | 5.7 | 5.4 | 6.4 | 6.6 | 6.5 | 6.6 | 6.5 | 6.7 | 6.4 | 6.4 | 6.4 | 5.7 | 5.4 | 5.4 |  |  |  |  | 7.3 | 6.21
| Evaporator Delta "T" |  |  | 6.8 | 7.8 | 7.9 | 6.8 | 6.8 | 7.8 | 8 | 6.7 | 7 | 7.3 | 7.2 | 7.4 | 7.5 | 7.8 | 7.8 | 7.8 | 8.5 | 8 | 7.7 |  |  |  |  | 8.7 | 7.565
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.7 | 23.8 | 23.5 | 22.4 | 22 | 22.4 | 22.6 | 21.7 | 21.9 | 21.9 | 22.5 | 23.1 | 23.4 | 23.7 | 24.3 | 24.8 | 25.1 | 25.3 | 25.1 |  |  |  |  | 25.2 | 23.42
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.4 | 29.1 | 28.9 | 27.1 | 26.6 | 27.8 | 28 | 26.2 | 26.7 | 26.9 | 27.4 | 28.1 | 28.4 | 28.9 | 29.6 | 30.1 | 30.9 | 30.9 | 30.6 |  |  |  |  | 31.1 | 28.585
| Condenser Delta "T" | ºC |  | 4.7 | 5.3 | 5.4 | 4.7 | 4.6 | 5.4 | 5.4 | 4.5 | 4.8 | 5 | 4.9 | 5 | 5 | 5.2 | 5.3 | 5.3 | 5.8 | 5.6 | 5.5 |  |  |  |  | 5.9 | 5.165
| Evaporator pressure (Kpag) | kpag |  | 262.7 | 250.3 | 248.9 | 259.2 | 259.9 | 248.2 | 246.1 | 259.2 | 258.6 | 257.9 | 260.6 | 259.9 | 262 | 259.2 | 259.9 | 260.6 | 251 | 246.8 | 246.8 |  |  |  |  | 270.3 | 256.405
| Condenser pressure (kpag) | kpag |  | 661.9 | 679.1 | 672.2 | 629.5 | 624 | 652.2 | 651.6 | 612.9 | 627.4 | 630.2 | 643.3 | 657.8 | 662.6 | 675.7 | 688.1 | 698.4 | 720.5 | 719.8 | 710.2 |  |  |  |  | 723.3 | 667.035
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  |  |  |  | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  |  |  |  | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  |  | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  |  | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  |  | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2183.4656 | 2504.5635 | 2536.6733 | 2183.4656 | 2183.4656 | 2504.5635 | 2568.7831 | 2151.3558 | 2247.6852 | 2344.0146 | 2311.9048 | 2376.1243 | 2408.2341 | 2504.5635 | 2504.5635 | 2504.5635 | 2729.332 | 2568.7831 | 2472.4537 |  |  |  |  | 2793.5516 | 48582.1098
15 | Power Consumption of Chiller | KWH |  | 1200 | 1400 | 1200 | 1200 | 1300 | 1400 | 1200 | 1200 | 1200 | 1200 | 1300 | 1200 | 1500 | 1400 | 1200 | 1700 | 1500 | 1400 | 1400 | 200 | 0 | 0 | 1100 | 1400 | 27800
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.54959 | 0.55898 | 0.47306 | 0.54959 | 0.59538 | 0.55898 | 0.46715 | 0.55779 | 0.53388 | 0.51194 | 0.56231 | 0.50502 | 0.62286 | 0.55898 | 0.47913 | 0.67876 | 0.54959 | 0.54501 | 0.56624 |  |  |  |  | 0.50115 | 0.54627
17 | Average iKW/TR |  |  | Hours 7: 0.54627 | 0.54627
18 | COP of chiller |  |  | 6.3976 | 6.29 | 7.4325 | 6.3976 | 5.9054 | 6.29 | 7.5265 | 6.3035 | 6.5857 | 6.868 | 6.2528 | 6.962 | 5.6449 | 6.29 | 7.3384 | 5.18 | 6.3976 | 6.4513 | 6.2094 |  |  |  |  | 7.0158 | 6.487
19 | EER of Chiller |  |  | 21.8349 | 21.4679 | 25.367 | 21.8349 | 20.1552 | 21.4679 | 25.6881 | 21.5138 | 22.4771 | 23.4404 | 21.3409 | 23.7615 | 19.266 | 21.4679 | 25.0459 | 17.6794 | 21.8349 | 22.0183 | 21.1927 |  |  |  |  | 23.9449 | 22.14
20 | LMTD of Condenser | ºC |  | 2.9511 | 3.2621 | 3.4167 | 3.0731 | 2.7961 | 3.2932 | 3.5385 | 3.009 | 3.1049 | 3.1682 | 3.2578 | 3.1682 | 3.1682 | 3.2309 | 3.2621 | 3.2621 | 3.2887 | 3.355 | 3.4482 |  |  |  |  | 3.5727 | 3.2314
21 | LMTD of Evaporator | ºC |  | 2.3526 | 2.7764 | 2.8 | 2.7067 | 2.5363 | 3.1241 | 3.1746 | 2.8412 | 2.757 | 2.9966 | 2.9709 | 2.6811 | 2.8816 | 2.9556 | 2.7764 | 2.7764 | 2.9408 | 3.0046 | 2.931 |  |  |  |  | 3.1742 | 2.8579

## 22-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 22/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.7 | 0.7 | 0.6 | 0.6 | 0.8 | 0.8 | 0.7 | 0.7 | 0.6 | 0.8 | 0.6 | 0.7 | 0.7 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.68333
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.525
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.4 | 13.9 | 13.8 | 13.7 | 13.8 | 13.7 | 13.9 | 14.1 | 14.3 | 14.7 | 14.6 | 14.6 | 14.6 | 14.7 | 14.7 | 14.7 | 14.3 | 14 | 13.7 | 13.7 | 13.6 | 13.5 | 13.3 | 13.3 | 14.0667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.4 | 6.5 | 6.4 | 6.5 | 6.6 | 6.5 | 6.6 | 6.6 | 6.1 | 6.2 | 5.8 | 5.9 | 6.2 | 6.3 | 6.2 | 6.2 | 5.9 | 5.8 | 5.6 | 5.6 | 5.5 | 5.5 | 5.6 | 5.5 | 6.0833
| Evaporator Delta "T" |  |  | 8 | 7.4 | 7.4 | 7.2 | 7.2 | 7.2 | 7.3 | 7.5 | 8.2 | 8.5 | 8.8 | 8.7 | 8.4 | 8.4 | 8.5 | 8.5 | 8.4 | 8.2 | 8.1 | 8.1 | 8.1 | 8 | 7.7 | 7.8 | 7.9833
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.8 | 24.9 | 24.2 | 23.3 | 22.9 | 24 | 24.5 | 25 | 25.7 | 26.1 | 25.2 | 25.7 | 26.4 | 26.6 | 26.6 | 26.6 | 26.6 | 26.7 | 26.8 | 26.9 | 26.8 | 26.6 | 26.6 | 26.7 | 25.675
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.4 | 28.9 | 28.1 | 27.1 | 26.8 | 27.9 | 28.4 | 29.1 | 30.2 | 30.6 | 30.1 | 30.6 | 31.2 | 31.1 | 31.3 | 31.4 | 31.3 | 31.2 | 31.4 | 31.5 | 31.2 | 31.1 | 31 | 31 | 30.0792
| Condenser Delta "T" | ºC |  | 4.6 | 4 | 3.9 | 3.8 | 3.9 | 3.9 | 3.9 | 4.1 | 4.5 | 4.5 | 4.9 | 4.9 | 4.8 | 4.5 | 4.7 | 4.8 | 4.7 | 4.5 | 4.6 | 4.6 | 4.4 | 4.5 | 4.4 | 4.3 | 4.4042
| Evaporator pressure (Kpag) | kpag |  | 259.9 | 262 | 260.6 | 262 | 262.7 | 261.3 | 262.7 | 261.3 | 255.8 | 257.2 | 251.7 | 252.3 | 256.5 | 257.9 | 255.1 | 253.7 | 252.3 | 251 | 249.6 | 248.2 | 248.2 | 248.9 | 248.9 | 248.2 | 255.3333
| Condenser pressure (kpag) | kpag |  | 668.8 | 659.8 | 639.8 | 619.8 | 615.7 | 636.4 | 647.4 | 663.3 | 688.1 | 700.5 | 684.6 | 696.4 | 709.5 | 711.5 | 715.7 | 717.1 | 714.3 | 712.9 | 715 | 716.4 | 711.5 | 706.7 | 705.3 | 709.5 | 686.0833
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2376.1243 | 2376.1243 | 2311.9048 | 2311.9048 | 2311.9048 | 2344.0146 | 2408.2341 | 2633.0026 | 2729.332 | 2825.6614 | 2793.5516 | 2697.2222 | 2697.2222 | 2729.332 | 2729.332 | 2697.2222 | 2633.0026 | 2600.8929 | 2600.8929 | 2600.8929 | 2568.7831 | 2472.4537 | 2504.5635 | 61522.3545
15 | Power Consumption of Chiller | KWH |  | 1300 | 1400 | 1200 | 1200 | 1300 | 1300 | 1300 | 1400 | 1500 | 1600 | 1600 | 1500 | 1600 | 1600 | 1600 | 1400 | 1700 | 1500 | 1600 | 1500 | 1600 | 1400 | 1500 | 1400 | 35000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.50608 | 0.58919 | 0.50502 | 0.51905 | 0.56231 | 0.56231 | 0.5546 | 0.58134 | 0.56969 | 0.58622 | 0.56624 | 0.53695 | 0.5932 | 0.5932 | 0.58622 | 0.51295 | 0.63028 | 0.56969 | 0.61517 | 0.57673 | 0.61517 | 0.54501 | 0.60668 | 0.55898 | 0.56843
17 | Average iKW/TR |  |  | Hours 7: 0.56843 | 0.56843
18 | COP of chiller |  |  | 6.9476 | 5.9675 | 6.962 | 6.7739 | 6.2528 | 6.2528 | 6.3397 | 6.0481 | 6.1718 | 5.9977 | 6.2094 | 6.5481 | 5.9271 | 5.9271 | 5.9977 | 6.8545 | 5.5785 | 6.1718 | 5.7155 | 6.0965 | 5.7155 | 6.4513 | 5.7954 | 6.29 | 6.208
19 | EER of Chiller |  |  | 23.7121 | 20.367 | 23.7615 | 23.1193 | 21.3409 | 21.3409 | 21.6373 | 20.6422 | 21.0642 | 20.4702 | 21.1927 | 22.3486 | 20.2293 | 20.2293 | 20.4702 | 23.3945 | 19.0394 | 21.0642 | 19.5069 | 20.8073 | 19.5069 | 22.0183 | 19.7798 | 21.4679 | 21.1879
20 | LMTD of Condenser | ºC |  | 2.2723 | 2.1006 | 1.9356 | 1.9072 | 2.2025 | 2.2025 | 2.0715 | 2.1295 | 2.1027 | 2.3799 | 2.2116 | 2.3564 | 2.3285 | 2.3799 | 2.4379 | 2.3285 | 2.3005 | 2.244 | 2.2723 | 2.1301 | 2.0752 | 2.1027 | 2.0752 | 2.0476 | 2.1914
21 | LMTD of Evaporator | ºC |  | 2.8236 | 2.6811 | 2.4912 | 2.4453 | 2.4453 | 2.6332 | 2.4683 | 2.5141 | 2.8707 | 3.126 | 3.1982 | 3.1742 | 3.1019 | 3.1019 | 3.126 | 3.2998 | 3.1019 | 3.0533 | 2.8472 | 2.8472 | 2.8472 | 2.8236 | 2.7527 | 2.9556 | 2.8637
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1400 | 1400
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.3 | 1.2 | 1.3 | 1.2 | 1.4 | 1.1 | 1.1 | 1.1 | 1.4 | 1.2 | 1.2 | 1.3 | 1.2 | 1.3 | 1.3 | 1.2 | 1.1 | 1.2 | 1.3 | 1.2 | 1.2 | 1.3 |  | 1.2304
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.6 | 0.5 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.4 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 |  | 0.5
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.6 | 14 | 13.9 | 13.9 | 13.9 | 13.9 | 14.1 | 14.3 | 14.4 | 14.8 | 14.8 | 14.6 | 14.8 | 14.8 | 14.8 | 14.8 | 14.5 | 14.2 | 13.8 | 13.8 | 13.7 | 13.6 | 13.5 |  | 14.2391
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 6.6 | 6.5 | 6.3 | 6.6 | 6.7 | 6.6 | 6.7 | 6.3 | 6.3 | 6.3 | 6.3 | 6.4 | 6.4 | 6.5 | 6.4 | 6.2 | 5.9 | 5.9 | 5.8 | 5.8 | 5.8 | 5.7 |  | 6.287
| Evaporator Delta "T" |  |  | 8 | 7.4 | 7.4 | 7.6 | 7.3 | 7.2 | 7.5 | 7.6 | 8.1 | 8.5 | 8.5 | 8.3 | 8.4 | 8.4 | 8.3 | 8.4 | 8.3 | 8.3 | 7.9 | 8 | 7.9 | 7.8 | 7.8 |  | 7.9522
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.6 | 24.6 | 23.8 | 22.9 | 22.7 | 23.7 | 24.1 | 24.6 | 25.4 | 25.8 | 24.9 | 25.4 | 26.2 | 26.3 | 26.3 | 26.3 | 26.4 | 26.3 | 26.6 | 26.7 | 26.5 | 26.3 | 26.3 |  | 25.3348
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.1 | 29.6 | 28.8 | 28 | 27.8 | 28.7 | 29.2 | 29.8 | 30.8 | 31.5 | 30.6 | 31.1 | 31.8 | 31.9 | 31.9 | 32.1 | 32.1 | 32 | 31.9 | 32.2 | 31.8 | 31.6 | 31.7 |  | 30.7391
| Condenser Delta "T" | ºC |  | 5.5 | 5 | 5 | 5.1 | 5.1 | 5 | 5.1 | 5.2 | 5.4 | 5.7 | 5.7 | 5.7 | 5.6 | 5.6 | 5.6 | 5.8 | 5.7 | 5.7 | 5.3 | 5.5 | 5.3 | 5.3 | 5.4 |  | 5.4043
| Evaporator pressure (Kpag) | kpag |  | 262 | 262.7 | 261.3 | 258.6 | 259.9 | 262.7 | 261.3 | 265.4 | 257.9 | 257.9 | 257.9 | 259.9 | 259.9 | 259.2 | 259.9 | 259.2 | 253.7 | 253 | 254.4 | 251.7 | 251.7 | 251 | 251.7 |  | 257.9522
| Condenser pressure (kpag) | kpag |  | 699.1 | 688.1 | 669.5 | 652.2 | 646 | 664.7 | 677.1 | 688.1 | 719.1 | 735.7 | 711.5 | 720.5 | 737.7 | 742.6 | 742.6 | 743.3 | 744.6 | 741.9 | 738.4 | 743.9 | 737.7 | 734.3 | 731.5 |  | 713.4826
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2376.1243 | 2376.1243 | 2440.3439 | 2344.0146 | 2311.9048 | 2408.2341 | 2440.3439 | 2600.8929 | 2729.332 | 2729.332 | 2665.1124 | 2697.2222 | 2697.2222 | 2665.1124 | 2697.2222 | 2665.1124 | 2665.1124 | 2536.6733 | 2568.7831 | 2536.6733 | 2504.5635 | 2504.5635 |  | 58728.8029
15 | Power Consumption of Chiller | KWH |  | 1500 | 1300 | 1300 | 1200 | 1300 | 1300 | 1300 | 1600 | 1400 | 1500 | 1600 | 1500 | 1500 | 1500 | 1600 | 1600 | 1600 | 1400 | 1500 | 1600 | 1400 | 1600 | 1300 | 0 | 33400
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58393 | 0.54711 | 0.54711 | 0.49173 | 0.5546 | 0.56231 | 0.53981 | 0.65565 | 0.53828 | 0.54959 | 0.58622 | 0.56283 | 0.55613 | 0.55613 | 0.60035 | 0.5932 | 0.60035 | 0.52531 | 0.59133 | 0.62286 | 0.5519 | 0.63883 | 0.51905 |  | 0.56846
17 | Average iKW/TR |  |  | Hours 7: 0.56846 | 0.56846
18 | COP of chiller |  |  | 6.0212 | 6.4265 | 6.4265 | 7.1502 | 6.3397 | 6.2528 | 6.5133 | 5.3627 | 6.532 | 6.3976 | 5.9977 | 6.247 | 6.3223 | 6.3223 | 5.8566 | 5.9271 | 5.8566 | 6.6932 | 5.946 | 5.6449 | 6.3707 | 5.5038 | 6.7739 |  | 6.2124
19 | EER of Chiller |  |  | 20.5504 | 21.9337 | 21.9337 | 24.4037 | 21.6373 | 21.3409 | 22.2301 | 18.3027 | 22.2936 | 21.8349 | 20.4702 | 21.3211 | 21.578 | 21.578 | 19.9885 | 20.2293 | 19.9885 | 22.844 | 20.2936 | 19.266 | 21.7431 | 18.7844 | 23.1193 |  | 21.2028
20 | LMTD of Condenser | ºC |  | 3.1981 | 3.1682 | 3.0446 | 3.1996 | 3.0756 | 3.2899 | 2.9493 | 2.9795 | 3.0397 | 3.5107 | 3.2586 | 3.2586 | 3.355 | 3.2284 | 3.355 | 3.4163 | 3.2586 | 3.1291 | 3.1371 | 3.3241 | 3.1371 | 3.1371 | 3.2932 |  | 3.2062
21 | LMTD of Evaporator | ºC |  | 2.6277 | 2.4912 | 2.4912 | 2.9064 | 2.6572 | 2.4453 | 2.7051 | 2.7289 | 2.6502 | 2.7399 | 2.9408 | 2.8941 | 3.1019 | 3.1019 | 2.8941 | 3.1019 | 3.0776 | 2.6951 | 2.8 | 2.8236 | 2.8 | 2.9556 | 2.9556 |  | 2.8081

## 23-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 23/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 17: 0.8; Hours 18: 0.6; Hours 0: 0.7 | 0.7
2 | Small temperature difference of evaporator | ºC |  | Hours 17: 0.7; Hours 18: 0.8; Hours 0: 0.9 | 0.8
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 17: 14.9; Hours 18: 13.6; Hours 0: 14.1 | 14.2
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 17: 7.5; Hours 18: 6.5; Hours 0: 6.2 | 6.7333
| Evaporator Delta "T" |  |  | Hours 17: 7.4; Hours 18: 7.1; Hours 0: 7.9 | 7.4667
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 17: 28.5; Hours 18: 28.5; Hours 0: 28.3 | 28.4333
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 17: 33.2; Hours 18: 33.1; Hours 0: 33.3 | 33.2
| Condenser Delta "T" | ºC |  | Hours 17: 4.7; Hours 18: 4.6; Hours 0: 5 | 4.7667
| Evaporator pressure (Kpag) | kpag |  | Hours 17: 271; Hours 18: 256.5; Hours 0: 253 | 260.1667
| Condenser pressure (kpag) | kpag |  | Hours 17: 755; Hours 18: 752.9; Hours 0: 760.5 | 756.1333
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 17: 4.2; Hours 18: 4.2; Hours 0: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 17: 3.7; Hours 18: 3.7; Hours 0: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 17: 3.8; Hours 18: 3.8; Hours 0: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 17: 3; Hours 18: 3; Hours 0: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 17: 0.5; Hours 18: 0.5; Hours 0: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 17: 0.8; Hours 18: 0.8; Hours 0: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 17: 971; Hours 18: 971; Hours 0: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 17: 2376.1243; Hours 18: 2279.795; Hours 0: 2536.6733 | 7192.5926
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1400 | 1400 | 800 | 0 | 0 | 0 | 0 | 1100 | 1000 | 0 | 0 | 0 | 0 | 0 | 5800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 17: 0.58919; Hours 18: 0.61409; Hours 0: 0.43364 | 0.54564
17 | Average iKW/TR |  |  | Hours 7: 0.54564 | 0.54564
18 | COP of chiller |  |  | Hours 17: 5.9675; Hours 18: 5.7255; Hours 0: 8.1081 | 6.6004
19 | EER of Chiller |  |  | Hours 17: 20.367; Hours 18: 19.5413; Hours 0: 27.673 | 22.5271
20 | LMTD of Condenser | ºC |  | Hours 17: 2.4379; Hours 18: 2.1301; Hours 0: 2.3842 | 2.3174
21 | LMTD of Evaporator | ºC |  | Hours 17: 3.0222; Hours 18: 3.1004; Hours 0: 3.4647 | 3.1958
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 | 0.5 | 0.8 | 0.8 | 0.7 | 0.9 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.4 | 0.4 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.4 | 0.5 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.7 | 0.6 | 0.56667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.7 | 13.5 | 14.3 | 14.6 | 14.7 | 14.9 | 15.3 | 15.4 | 15.4 | 15.4 | 15.5 | 14.9 | 13.7 | 13.1 | 14.2 | 14.4 | 14.6 | 14.7 | 14.2 | 12.9 | 13.7 | 13.9 | 13.7 | 13.5 | 14.3417
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.5 | 6.1 | 6.3 | 6.4 | 6.7 | 7 | 7 | 7 | 6.9 | 6.9 | 6.8 | 6.1 | 5.6 | 6.1 | 6.2 | 6.4 | 6.4 | 6.3 | 5.5 | 5.6 | 5.8 | 5.6 | 5.6 | 6.2958
| Evaporator Delta "T" |  |  | 7.4 | 7 | 8.2 | 8.3 | 8.3 | 8.2 | 8.3 | 8.4 | 8.4 | 8.5 | 8.6 | 8.1 | 7.6 | 7.5 | 8.1 | 8.2 | 8.2 | 8.3 | 7.9 | 7.4 | 8.1 | 8.1 | 8.1 | 7.9 | 8.0458
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26.4 | 26.6 | 26.7 | 26.8 | 27.1 | 27.8 | 27.6 | 27.5 | 27.1 | 26.7 | 27.3 | 28.8 | 28.8 | 27.7 | 27.2 | 26.7 | 26.8 | 27.2 | 28.6 | 27.9 | 27.2 | 26.7 | 27.1 | 27 | 27.3042
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.7 | 30.4 | 31.3 | 31.4 | 31.8 | 32.4 | 32.2 | 32.2 | 31.9 | 31.4 | 32.2 | 33.4 | 33.3 | 32 | 31.6 | 31.4 | 31.4 | 31.9 | 33.2 | 32.1 | 31.6 | 31.7 | 31.7 | 31.5 | 31.8625
| Condenser Delta "T" | ºC |  | 4.3 | 3.8 | 4.6 | 4.6 | 4.7 | 4.6 | 4.6 | 4.7 | 4.8 | 4.7 | 4.9 | 4.6 | 4.5 | 4.3 | 4.4 | 4.7 | 4.6 | 4.7 | 4.6 | 4.2 | 4.4 | 5 | 4.6 | 4.5 | 4.5583
| Evaporator pressure (Kpag) | kpag |  | 258.6 | 262 | 253.7 | 257.2 | 257.9 | 262 | 264.8 | 264.8 | 264.8 | 264.8 | 266.1 | 265.4 | 255.1 | 249.6 | 255.8 | 255.1 | 258.6 | 258.6 | 256.5 | 248.2 | 248.9 | 251 | 248.9 | 249.6 | 257.4167
| Condenser pressure (kpag) | kpag |  | 696.4 | 692.2 | 712.2 | 717.7 | 724.6 | 740.5 | 733.6 | 736.4 | 728.1 | 717.1 | 731.5 | 762.6 | 756.4 | 729.5 | 721.2 | 715 | 715 | 727.4 | 759.8 | 730.2 | 723.3 | 721.9 | 721.9 | 718.4 | 726.3708
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2376.1243 | 2247.6852 | 2633.0026 | 2665.1124 | 2665.1124 | 2633.0026 | 2665.1124 | 2697.2222 | 2697.2222 | 2729.332 | 2761.4418 | 2600.8929 | 2440.3439 | 2408.2341 | 2600.8929 | 2633.0026 | 2633.0026 | 2665.1124 | 2536.6733 | 2376.1243 | 2600.8929 | 2600.8929 | 2600.8929 | 2536.6733 | 62004.0013
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1600 | 1600 | 1600 | 1600 | 1600 | 1400 | 1600 | 1600 | 1600 | 1600 | 1500 | 1600 | 1400 | 1600 | 1500 | 1600 | 1600 | 1500 | 1500 | 1500 | 1600 | 1600 | 37100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58919 | 0.62286 | 0.60767 | 0.60035 | 0.60035 | 0.60767 | 0.60035 | 0.51905 | 0.5932 | 0.58622 | 0.57941 | 0.61517 | 0.61467 | 0.66439 | 0.53828 | 0.60767 | 0.56969 | 0.60035 | 0.63075 | 0.63128 | 0.57673 | 0.57673 | 0.61517 | 0.63075 | 0.59908
17 | Average iKW/TR |  |  | Hours 7: 0.59908 | 0.59908
18 | COP of chiller |  |  | 5.9675 | 5.6449 | 5.786 | 5.8566 | 5.8566 | 5.786 | 5.8566 | 6.7739 | 5.9271 | 5.9977 | 6.0683 | 5.7155 | 5.7202 | 5.2921 | 6.532 | 5.786 | 6.1718 | 5.8566 | 5.5743 | 5.5696 | 6.0965 | 6.0965 | 5.7155 | 5.5743 | 5.8842
19 | EER of Chiller |  |  | 20.367 | 19.266 | 19.7477 | 19.9885 | 19.9885 | 19.7477 | 19.9885 | 23.1193 | 20.2293 | 20.4702 | 20.711 | 19.5069 | 19.5229 | 18.0619 | 22.2936 | 19.7477 | 21.0642 | 19.9885 | 19.0252 | 19.0092 | 20.8073 | 20.8073 | 19.5069 | 19.0252 | 20.0829
20 | LMTD of Condenser | ºC |  | 2.1871 | 1.9072 | 2.2723 | 2.2723 | 2.3005 | 2.2723 | 2.2723 | 2.3005 | 2.4667 | 2.1574 | 2.2116 | 2.2723 | 2.244 | 2.0476 | 1.9278 | 2.4379 | 2.409 | 2.3005 | 2.5413 | 2.1584 | 2.2156 | 2.3842 | 2.409 | 2.244 | 2.2588
21 | LMTD of Evaporator | ºC |  | 2.8568 | 2.3991 | 2.6727 | 3.0776 | 3.2499 | 3.0533 | 3.0776 | 3.1019 | 3.1019 | 2.9408 | 3.1501 | 3.029 | 2.5369 | 2.7051 | 3.029 | 3.0533 | 2.8707 | 3.0776 | 2.9801 | 2.8568 | 2.8472 | 3.029 | 3.1998 | 2.9801 | 2.9532
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5875
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 1.2 | 1.2 | 1.3 | 1.2 | 1.2 | 0.9 | 0.8 | 0.8 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 0.8 | 1.1 | 1.2 | 1.1 | 1.0125
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.9 | 13.7 | 14.5 | 14.7 | 14.8 | 15.2 | 15.4 | 15.5 | 15.5 | 15.5 | 15.6 | 15.2 | 13.8 | 13.3 | 14.3 | 14.6 | 14.7 | 14.8 | 14.5 | 13.2 | 13.8 | 14.1 | 13.9 | 13.7 | 14.5083
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.6 | 6.6 | 6.7 | 6.8 | 7.1 | 7.3 | 7.2 | 7.1 | 7.1 | 7.1 | 7.3 | 7 | 6 | 5.6 | 6.1 | 6.3 | 6.4 | 6.6 | 6.3 | 5.4 | 5.8 | 5.9 | 5.8 | 5.6 | 6.4875
| Evaporator Delta "T" |  |  | 7.3 | 7.1 | 7.8 | 7.9 | 7.7 | 7.9 | 8.2 | 8.4 | 8.4 | 8.4 | 8.3 | 8.2 | 7.8 | 7.7 | 8.2 | 8.3 | 8.3 | 8.2 | 8.2 | 7.8 | 8 | 8.2 | 8.1 | 8.1 | 8.0208
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26.4 | 26.6 | 26.6 | 26.8 | 27 | 27.8 | 27.6 | 27.4 | 27.1 | 26.7 | 27.3 | 28.8 | 28.9 | 27.9 | 27.1 | 26.8 | 26.8 | 27.2 | 28.6 | 27.9 | 27.1 | 27.1 | 27.1 | 27.1 | 27.3208
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.1 | 31.1 | 31.5 | 31.8 | 31.9 | 32.6 | 32.6 | 32.8 | 32.5 | 32.1 | 32.6 | 33.9 | 33.8 | 32.7 | 32.4 | 32.1 | 32.2 | 32.6 | 33.8 | 32.7 | 32.2 | 32.3 | 32.2 | 32.1 | 32.4
| Condenser Delta "T" | ºC |  | 4.7 | 4.5 | 4.9 | 5 | 4.9 | 4.8 | 5 | 5.4 | 5.4 | 5.4 | 5.3 | 5.1 | 4.9 | 4.8 | 5.3 | 5.3 | 5.4 | 5.4 | 5.2 | 4.8 | 5.1 | 5.2 | 5.1 | 5 | 5.0792
| Evaporator pressure (Kpag) | kpag |  | 257.2 | 257.9 | 257.9 | 259.2 | 262 | 265.4 | 263.4 | 260.6 | 259.9 | 259.2 | 264.1 | 262 | 250.3 | 244.1 | 248.2 | 249.6 | 250.3 | 251.7 | 251 | 243.4 | 246.1 | 244.8 | 244.8 | 244.1 | 254.05
| Condenser pressure (kpag) | kpag |  | 705.3 | 704 | 715 | 721.2 | 728.1 | 741.2 | 742.6 | 746.7 | 739.8 | 729.5 | 738.4 | 771.5 | 770.8 | 745.3 | 735.7 | 728.1 | 730.2 | 741.9 | 770.8 | 746 | 733.6 | 734.3 | 733.6 | 732.2 | 736.9083
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2344.0146 | 2279.795 | 2504.5635 | 2536.6733 | 2472.4537 | 2536.6733 | 2633.0026 | 2697.2222 | 2697.2222 | 2697.2222 | 2665.1124 | 2633.0026 | 2504.5635 | 2472.4537 | 2633.0026 | 2665.1124 | 2665.1124 | 2633.0026 | 2633.0026 | 2504.5635 | 2568.7831 | 2633.0026 | 2600.8929 | 2600.8929 | 61811.3426
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1600 | 1400 | 1400 | 1500 | 1600 | 1600 | 1600 | 1600 | 1500 | 1600 | 1400 | 1600 | 1500 | 1800 | 1500 | 1600 | 1600 | 1400 | 1600 | 1700 | 1400 | 1600 | 36700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.5546 | 0.57023 | 0.63883 | 0.5519 | 0.56624 | 0.59133 | 0.60767 | 0.5932 | 0.5932 | 0.5932 | 0.56283 | 0.60767 | 0.55898 | 0.64713 | 0.56969 | 0.67539 | 0.56283 | 0.60767 | 0.60767 | 0.55898 | 0.62286 | 0.64565 | 0.53828 | 0.61517 | 0.59338
17 | Average iKW/TR |  |  | Hours 7: 0.59338 | 0.59338
18 | COP of chiller |  |  | 6.3397 | 6.166 | 5.5038 | 6.3707 | 6.2094 | 5.946 | 5.786 | 5.9271 | 5.9271 | 5.9271 | 6.247 | 5.786 | 6.29 | 5.4332 | 6.1718 | 5.2059 | 6.247 | 5.786 | 5.786 | 6.29 | 5.6449 | 5.4457 | 6.532 | 5.7155 | 5.9452
19 | EER of Chiller |  |  | 21.6373 | 21.0445 | 18.7844 | 21.7431 | 21.1927 | 20.2936 | 19.7477 | 20.2293 | 20.2293 | 20.2293 | 21.3211 | 19.7477 | 21.4679 | 18.5436 | 21.0642 | 17.7676 | 21.3211 | 19.7477 | 19.7477 | 21.4679 | 19.266 | 18.5861 | 22.2936 | 19.5069 | 20.2908
20 | LMTD of Condenser | ºC |  | 2.3005 | 1.9543 | 2.0592 | 2.0852 | 2.0592 | 2.1846 | 2.2385 | 2.3452 | 2.3452 | 2.3452 | 2.3187 | 2.2654 | 2.0592 | 2.1846 | 2.3187 | 2.3187 | 2.3452 | 2.4943 | 2.2921 | 2.1846 | 2.2654 | 2.2921 | 2.2654 | 2.2385 | 2.24
21 | LMTD of Evaporator | ºC |  | 2.9966 | 2.9451 | 3.1241 | 3.4647 | 3.4114 | 3.4647 | 3.3879 | 4.0395 | 4.0395 | 4.1796 | 4.0117 | 3.9837 | 3.4381 | 3.2583 | 3.3879 | 4.0117 | 4.0117 | 3.9837 | 3.9837 | 3.7307 | 3.3363 | 3.8413 | 3.9557 | 3.8138 | 3.6584
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## 24-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 24/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.6 | 0.3 | 0.6 | 0.5 | 0.6 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6375
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 | 0.5 | 0.6 | 0.5 | 0.5 | 0.53333
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.4 | 13.4 | 13.6 | 14.1 | 14.3 | 14.7 | 15.5 | 15.7 | 15.9 | 14.8 | 14.1 | 13.4 | 14.1 | 14.6 | 14.6 | 14.7 | 14.6 | 14.4 | 13.9 | 13.7 | 13.3 | 13.3 | 12.9 | 13.1 | 14.1708
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.6 | 5.7 | 6.2 | 6.4 | 6.7 | 7.6 | 8.2 | 8.1 | 7.5 | 6.7 | 5.9 | 6.1 | 6.3 | 6.7 | 6.4 | 6.5 | 6.1 | 5.8 | 5.6 | 5.6 | 5.6 | 5.6 | 5.4 | 6.325
| Evaporator Delta "T" |  |  | 7.9 | 7.8 | 7.9 | 7.9 | 7.9 | 8 | 7.9 | 7.5 | 7.8 | 7.3 | 7.4 | 7.5 | 8 | 8.3 | 7.9 | 8.3 | 8.1 | 8.3 | 8.1 | 8.1 | 7.7 | 7.7 | 7.3 | 7.7 | 7.8458
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26.9 | 27.1 | 27.1 | 27.1 | 27.8 | 28.2 | 28.8 | 28.4 | 29.8 | 29.4 | 28.9 | 28.3 | 27.2 | 27 | 27 | 26.7 | 26.8 | 26.7 | 26.1 | 26 | 25.8 | 25.7 | 25.7 | 26 | 27.2708
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.5 | 31.5 | 31.6 | 31.7 | 32.4 | 32.7 | 33.2 | 32.7 | 34.1 | 33.7 | 33.2 | 32.7 | 31.8 | 31.6 | 31.5 | 31.1 | 31.3 | 31.3 | 30.8 | 30.6 | 30.2 | 30.1 | 29.9 | 30.1 | 31.7208
| Condenser Delta "T" | ºC |  | 4.6 | 4.4 | 4.5 | 4.6 | 4.6 | 4.5 | 4.4 | 4.3 | 4.3 | 4.3 | 4.3 | 4.4 | 4.6 | 4.6 | 4.5 | 4.4 | 4.5 | 4.6 | 4.7 | 4.6 | 4.4 | 4.4 | 4.2 | 4.1 | 4.45
| Evaporator pressure (Kpag) | kpag |  | 247.5 | 249.6 | 249.6 | 255.1 | 259.9 | 263.4 | 275.1 | 283.4 | 284.1 | 273 | 262.7 | 251.7 | 254.4 | 257.2 | 259.2 | 260.6 | 261.3 | 256.5 | 251 | 249.6 | 248.9 | 249.6 | 250.3 | 246.8 | 258.3542
| Condenser pressure (kpag) | kpag |  | 715 | 716.4 | 719.1 | 721.9 | 736.4 | 746 | 758.4 | 743.9 | 778.4 | 766.7 | 754.3 | 739.1 | 721.9 | 719.8 | 720.5 | 709.5 | 715 | 712.9 | 701.2 | 696.4 | 688.8 | 684 | 679.8 | 684 | 722.0583
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2504.5635 | 2536.6733 | 2536.6733 | 2536.6733 | 2568.7831 | 2536.6733 | 2408.2341 | 2504.5635 | 2344.0146 | 2376.1243 | 2408.2341 | 2568.7831 | 2665.1124 | 2536.6733 | 2665.1124 | 2600.8929 | 2665.1124 | 2600.8929 | 2600.8929 | 2472.4537 | 2472.4537 | 2344.0146 | 2472.4537 | 60462.7315
15 | Power Consumption of Chiller | KWH |  | 1400 | 1600 | 1500 | 1500 | 1500 | 1600 | 1500 | 1400 | 1600 | 1500 | 1400 | 1600 | 1400 | 1700 | 1400 | 1500 | 1600 | 1600 | 1400 | 1500 | 1500 | 1300 | 1500 | 1400 | 35900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.5519 | 0.63883 | 0.59133 | 0.59133 | 0.59133 | 0.62286 | 0.59133 | 0.58134 | 0.63883 | 0.63993 | 0.58919 | 0.66439 | 0.54501 | 0.63787 | 0.5519 | 0.56283 | 0.61517 | 0.60035 | 0.53828 | 0.57673 | 0.60668 | 0.52579 | 0.63993 | 0.56624 | 0.59414
17 | Average iKW/TR |  |  | Hours 7: 0.59414 | 0.59414
18 | COP of chiller |  |  | 6.3707 | 5.5038 | 5.946 | 5.946 | 5.946 | 5.6449 | 5.946 | 6.0481 | 5.5038 | 5.4944 | 5.9675 | 5.2921 | 6.4513 | 5.5121 | 6.3707 | 6.247 | 5.7155 | 5.8566 | 6.532 | 6.0965 | 5.7954 | 6.687 | 5.4944 | 6.2094 | 5.9407
19 | EER of Chiller |  |  | 21.7431 | 18.7844 | 20.2936 | 20.2936 | 20.2936 | 19.266 | 20.2936 | 20.6422 | 18.7844 | 18.7523 | 20.367 | 18.0619 | 22.0183 | 18.8127 | 21.7431 | 21.3211 | 19.5069 | 19.9885 | 22.2936 | 20.8073 | 19.7798 | 22.8229 | 18.7523 | 21.1927 | 20.2756
20 | LMTD of Condenser | ºC |  | 2.1301 | 2.0752 | 2.1027 | 2.2723 | 2.2723 | 2.244 | 2.0752 | 2.1871 | 2.0476 | 1.5751 | 2.0476 | 1.9278 | 2.1301 | 2.2723 | 2.244 | 2.0752 | 2.244 | 2.2723 | 2.3005 | 2.2723 | 2.2156 | 2.2156 | 2.1584 | 1.9918 | 2.1395
21 | LMTD of Evaporator | ºC |  | 2.9801 | 2.9556 | 2.9801 | 2.9801 | 2.9801 | 3.0046 | 2.6051 | 2.5141 | 2.7764 | 2.6572 | 2.4912 | 2.5141 | 3.0046 | 3.0776 | 2.9801 | 2.8941 | 2.8472 | 2.8941 | 3.029 | 3.029 | 2.7527 | 2.931 | 2.6572 | 2.7527 | 2.8453
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 15: 1.7; Hours 16: 1.7; Hours 17: 1.6 | 1.6667
2 | Small temperature difference of evaporator | ºC |  | Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.6 | 0.53333
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 15: 16; Hours 16: 14.9; Hours 17: 14.3 | 15.0667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 15: 7.8; Hours 16: 7.2; Hours 17: 6.3 | 7.1
| Evaporator Delta "T" |  |  | Hours 15: 8.2; Hours 16: 7.7; Hours 17: 8 | 7.9667
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 15: 29.8; Hours 16: 29.4; Hours 17: 29 | 29.4
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 15: 34.7; Hours 16: 34.2; Hours 17: 33.8 | 34.2333
| Condenser Delta "T" | ºC |  | Hours 15: 4.9; Hours 16: 4.8; Hours 17: 4.8 | 4.8333
| Evaporator pressure (Kpag) | kpag |  | Hours 15: 276.5; Hours 16: 268.2; Hours 17: 257.9 | 267.5333
| Condenser pressure (kpag) | kpag |  | Hours 15: 821.9; Hours 16: 804.6; Hours 17: 795.7 | 807.4
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 15: 3; Hours 16: 3; Hours 17: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 15: 971; Hours 16: 971; Hours 17: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 15: 2633.0026; Hours 16: 2472.4537; Hours 17: 2568.7831 | 7674.2394
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 1700 | 1500 | 1300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5100
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 15: 0.64565; Hours 16: 0.60668; Hours 17: 0.50608 | 0.58614
17 | Average iKW/TR |  |  | Hours 7: 0.58614 | 0.58614
18 | COP of chiller |  |  | Hours 15: 5.4457; Hours 16: 5.7954; Hours 17: 6.9476 | 6.0629
19 | EER of Chiller |  |  | Hours 15: 18.5861; Hours 16: 19.7798; Hours 17: 23.7121 | 20.6926
20 | LMTD of Condenser | ºC |  | Hours 15: 3.6124; Hours 16: 3.579; Hours 17: 3.4625 | 3.5513
21 | LMTD of Evaporator | ºC |  | Hours 15: 2.8707; Hours 16: 2.7527; Hours 17: 3.0046 | 2.876
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.625
2 | Small temperature difference of evaporator | ºC |  | 1 | 1 | 1 | 1 | 1.2 | 1.2 | 1.1 | 1.1 | 1.2 | 0.9 | 1.1 | 1 | 0.9 | 1.3 | 1.2 | 1 | 1.2 | 1.2 | 1.2 | 1.1 | 1.1 | 0.9 | 0.9 | 0.9 | 1.0708
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.6 | 13.6 | 13.7 | 14.2 | 14.5 | 14.8 | 15.6 | 15.8 | 16.1 | 15.1 | 14.4 | 13.6 | 14.2 | 14.6 | 14.8 | 14.8 | 14.8 | 14.6 | 14.2 | 13.8 | 13.6 | 13.4 | 13.3 | 13.3 | 14.35
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.6 | 5.7 | 6.1 | 6.4 | 6.5 | 7.1 | 7.6 | 7.9 | 7 | 6.4 | 5.8 | 6 | 6.3 | 6.7 | 6.7 | 6.4 | 6.3 | 6 | 5.7 | 5.6 | 5.4 | 5.4 | 5.3 | 6.2292
| Evaporator Delta "T" |  |  | 8 | 8 | 8 | 8.1 | 8.1 | 8.3 | 8.5 | 8.2 | 8.2 | 8.1 | 8 | 7.8 | 8.2 | 8.3 | 8.1 | 8.1 | 8.4 | 8.3 | 8.2 | 8.1 | 8 | 8 | 7.9 | 8 | 8.1208
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26.9 | 27.1 | 27.1 | 27.1 | 27.8 | 28.2 | 28.8 | 28.6 | 29.8 | 29.4 | 29 | 28.4 | 27.2 | 26.9 | 27 | 26.6 | 26.8 | 26.7 | 26.2 | 26 | 25.9 | 25.8 | 25.7 | 25.8 | 27.2833
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 32 | 32.1 | 32.2 | 32.4 | 33 | 33.6 | 34.3 | 33.9 | 35 | 34.6 | 34.1 | 33.3 | 32.4 | 32.3 | 32.2 | 31.8 | 32.1 | 31.8 | 31.4 | 31.2 | 30.9 | 30.8 | 30.7 | 30.7 | 32.45
| Condenser Delta "T" | ºC |  | 5.1 | 5 | 5.1 | 5.3 | 5.2 | 5.4 | 5.5 | 5.3 | 5.2 | 5.2 | 5.1 | 4.9 | 5.2 | 5.4 | 5.2 | 5.2 | 5.3 | 5.1 | 5.2 | 5.2 | 5 | 5 | 5 | 4.9 | 5.1667
| Evaporator pressure (Kpag) | kpag |  | 242.7 | 244.1 | 243.4 | 244.8 | 250.3 | 251.7 | 260.6 | 267.5 | 272.3 | 262 | 253 | 246.8 | 247.5 | 249.6 | 255.1 | 255.1 | 253 | 251.7 | 246.8 | 243.4 | 242 | 242 | 242 | 242 | 250.3917
| Condenser pressure (kpag) | kpag |  | 728.8 | 732.2 | 734.3 | 739.1 | 753.6 | 768.1 | 786 | 772.2 | 801.2 | 789.4 | 778.4 | 757 | 736.4 | 734.3 | 732.2 | 722.6 | 730.8 | 726 | 713.6 | 710.2 | 704 | 700.5 | 697.7 | 699.1 | 739.4875
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2568.7831 | 2568.7831 | 2600.8929 | 2600.8929 | 2665.1124 | 2729.332 | 2633.0026 | 2633.0026 | 2600.8929 | 2568.7831 | 2504.5635 | 2633.0026 | 2665.1124 | 2600.8929 | 2600.8929 | 2697.2222 | 2665.1124 | 2633.0026 | 2600.8929 | 2568.7831 | 2568.7831 | 2536.6733 | 2568.7831 | 62581.9775
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1600 | 1700 | 1300 | 1700 | 1700 | 1500 | 1700 | 1500 | 1500 | 1700 | 1400 | 1500 | 1700 | 1400 | 1600 | 1600 | 1500 | 1500 | 1600 | 1500 | 1400 | 1500 | 37200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58393 | 0.62286 | 0.62286 | 0.65362 | 0.49983 | 0.63787 | 0.62286 | 0.56969 | 0.64565 | 0.57673 | 0.58393 | 0.67876 | 0.53171 | 0.56283 | 0.65362 | 0.53828 | 0.5932 | 0.60035 | 0.56969 | 0.57673 | 0.62286 | 0.58393 | 0.5519 | 0.58393 | 0.59449
17 | Average iKW/TR |  |  | Hours 7: 0.59449 | 0.59449
18 | COP of chiller |  |  | 6.0212 | 5.6449 | 5.6449 | 5.3793 | 7.0344 | 5.5121 | 5.6449 | 6.1718 | 5.4457 | 6.0965 | 6.0212 | 5.18 | 6.6126 | 6.247 | 5.3793 | 6.532 | 5.9271 | 5.8566 | 6.1718 | 6.0965 | 5.6449 | 6.0212 | 6.3707 | 6.0212 | 5.9449
19 | EER of Chiller |  |  | 20.5504 | 19.266 | 19.266 | 18.3594 | 24.0085 | 18.8127 | 19.266 | 21.0642 | 18.5861 | 20.8073 | 20.5504 | 17.6794 | 22.5688 | 21.3211 | 18.3594 | 22.2936 | 20.2293 | 19.9885 | 21.0642 | 20.8073 | 19.266 | 20.5504 | 21.7431 | 20.5504 | 20.29
20 | LMTD of Condenser | ºC |  | 2.4119 | 2.3842 | 2.4119 | 2.4669 | 2.4395 | 2.3452 | 2.5215 | 2.4669 | 2.2921 | 2.2921 | 2.2654 | 2.2116 | 2.1367 | 2.3452 | 2.2921 | 2.2921 | 2.3187 | 2.2654 | 2.2921 | 2.2921 | 2.2385 | 2.2385 | 2.2385 | 2.2116 | 2.3196
21 | LMTD of Evaporator | ºC |  | 3.641 | 3.641 | 3.641 | 3.668 | 3.9557 | 4.0117 | 3.9235 | 3.8413 | 3.9837 | 3.5178 | 3.7862 | 3.5866 | 3.5442 | 4.1512 | 3.9557 | 3.668 | 4.0395 | 4.0117 | 3.9837 | 3.8138 | 3.7862 | 3.4913 | 3.4647 | 3.4913 | 3.7749
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## 25-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 25/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.7 | 0.6 | 0.6 | 1 | 0.8 | 0.6 | 0.9 | 0.6 | 0.8 | 0.7 | 0.3 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 | 0.5 | 0.6 | 0.6 | 0.5 | 0.5 | 0.6 | 0.6375
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.5 | 0.6 | 0.4 | 0.8 | 0.6 | 0.5 | 0.6 | 0.5 | 0.7 | 0.6 | 0.5 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.52083
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.1 | 13.6 | 13.9 | 14.2 | 14.7 | 15.1 | 15.5 | 15.6 | 14.4 | 13.7 | 13.1 | 13.9 | 14.6 | 15.1 | 15.2 | 15.4 | 15.1 | 14 | 13.2 | 12.2 | 13.1 | 13.4 | 13.7 | 14.1208
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.6 | 5.8 | 5.9 | 6.2 | 6.8 | 6.9 | 7.6 | 7.9 | 6.9 | 6.2 | 5.7 | 6.2 | 6.8 | 7 | 7.1 | 7.3 | 7.4 | 6.5 | 5.9 | 5.5 | 5.7 | 5.8 | 6 | 6.425
| Evaporator Delta "T" |  |  | 7.6 | 7.5 | 7.8 | 8 | 8 | 7.9 | 8.2 | 7.9 | 7.7 | 7.5 | 7.5 | 7.4 | 7.7 | 7.8 | 8.1 | 8.1 | 8.1 | 7.7 | 7.5 | 7.3 | 6.7 | 7.4 | 7.6 | 7.7 | 7.6958
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.7 | 26.3 | 26.6 | 26.8 | 28 | 28.2 | 28.6 | 28.3 | 29.6 | 29 | 28.8 | 28.4 | 27.4 | 27.5 | 27.6 | 27.7 | 27.8 | 29.3 | 29.4 | 29.3 | 28.2 | 27.4 | 27.3 | 27.3 | 27.9375
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.9 | 30.6 | 31.1 | 31.5 | 32.5 | 32.7 | 33.2 | 32.8 | 34 | 33.4 | 33.2 | 32.5 | 31.9 | 32.2 | 32.3 | 32 | 32.5 | 33.9 | 33.7 | 33.4 | 31.9 | 31.5 | 31.7 | 31.7 | 32.3375
| Condenser Delta "T" | ºC |  | 4.2 | 4.3 | 4.5 | 4.7 | 4.5 | 4.5 | 4.6 | 4.5 | 4.4 | 4.4 | 4.4 | 4.1 | 4.5 | 4.7 | 4.7 | 4.3 | 4.7 | 4.6 | 4.3 | 4.1 | 3.7 | 4.1 | 4.4 | 4.4 | 4.4
| Evaporator pressure (Kpag) | kpag |  | 248.2 | 248.9 | 251 | 253 | 258.6 | 264.1 | 265.4 | 273 | 277.9 | 266.1 | 257.9 | 249.6 | 255.1 | 264.1 | 265.4 | 267.5 | 272.3 | 274.4 | 260.6 | 254.4 | 246.8 | 251.7 | 252.3 | 253 | 259.6375
| Condenser pressure (kpag) | kpag |  | 680.5 | 696.4 | 707.4 | 714.3 | 739.1 | 743.9 | 756.4 | 746 | 774.3 | 761.2 | 752.2 | 737.7 | 727.4 | 730.8 | 735 | 737 | 737 | 765.3 | 768.1 | 759.1 | 733.6 | 716.4 | 721.2 | 719.8 | 735.8375
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2408.2341 | 2504.5635 | 2568.7831 | 2568.7831 | 2536.6733 | 2633.0026 | 2536.6733 | 2472.4537 | 2408.2341 | 2408.2341 | 2376.1243 | 2472.4537 | 2504.5635 | 2600.8929 | 2600.8929 | 2600.8929 | 2472.4537 | 2408.2341 | 2344.0146 | 2151.3558 | 2376.1243 | 2440.3439 | 2472.4537 | 59306.7791
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1600 | 1500 | 1500 | 1500 | 1400 | 1600 | 1500 | 1600 | 1500 | 1500 | 1500 | 1400 | 1600 | 1500 | 1500 | 1500 | 1500 | 1600 | 1400 | 1300 | 1500 | 1400 | 35700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.57369 | 0.58134 | 0.63883 | 0.58393 | 0.58393 | 0.59133 | 0.53171 | 0.63075 | 0.60668 | 0.66439 | 0.62286 | 0.63128 | 0.60668 | 0.55898 | 0.61517 | 0.57673 | 0.57673 | 0.60668 | 0.62286 | 0.68259 | 0.65075 | 0.54711 | 0.61467 | 0.56624 | 0.60275
17 | Average iKW/TR |  |  | Hours 7: 0.60275 | 0.60275
18 | COP of chiller |  |  | 6.1287 | 6.0481 | 5.5038 | 6.0212 | 6.0212 | 5.946 | 6.6126 | 5.5743 | 5.7954 | 5.2921 | 5.6449 | 5.5696 | 5.7954 | 6.29 | 5.7155 | 6.0965 | 6.0965 | 5.7954 | 5.6449 | 5.151 | 5.403 | 6.4265 | 5.7202 | 6.2094 | 5.8543
19 | EER of Chiller |  |  | 20.9174 | 20.6422 | 18.7844 | 20.5504 | 20.5504 | 20.2936 | 22.5688 | 19.0252 | 19.7798 | 18.0619 | 19.266 | 19.0092 | 19.7798 | 21.4679 | 19.5069 | 20.8073 | 20.8073 | 19.7798 | 19.266 | 17.5803 | 18.4404 | 21.9337 | 19.5229 | 21.1927 | 19.9806
20 | LMTD of Condenser | ºC |  | 2.1584 | 2.0476 | 2.1027 | 2.7004 | 2.3799 | 2.1027 | 2.5413 | 2.1027 | 2.3507 | 2.2156 | 1.5991 | 1.9918 | 2.1027 | 2.1574 | 2.1574 | 2.1871 | 2.3005 | 2.1301 | 1.9012 | 1.9918 | 1.8787 | 1.8475 | 1.9278 | 2.0752 | 2.1229
21 | LMTD of Evaporator | ºC |  | 2.7289 | 2.5141 | 2.5824 | 2.8236 | 3.0046 | 2.8 | 3.0533 | 2.6051 | 3.2583 | 2.8816 | 2.7051 | 2.8568 | 2.7527 | 3.1241 | 3.029 | 2.8472 | 3.029 | 2.5597 | 2.5141 | 2.4683 | 2.3293 | 2.4912 | 2.9064 | 2.931 | 2.7832
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 15: 1.5; Hours 16: 1.5; Hours 17: 1.5; Hours 0: 1.3; Hours 1: 1.3 | 1.42
2 | Small temperature difference of evaporator | ºC |  | Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 0: 0.4; Hours 1: 0.4 | 0.46
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 15: 15.8; Hours 16: 14.6; Hours 17: 13.9; Hours 0: 15.4; Hours 1: 14.1 | 14.76
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 15: 7.8; Hours 16: 6.9; Hours 17: 6.1; Hours 0: 7.4; Hours 1: 6.6 | 6.96
| Evaporator Delta "T" |  |  | Hours 15: 8; Hours 16: 7.7; Hours 17: 7.8; Hours 0: 8; Hours 1: 7.5 | 7.8
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 15: 29.6; Hours 16: 29.2; Hours 17: 28.9; Hours 0: 29.2; Hours 1: 29.4 | 29.26
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 15: 34.3; Hours 16: 33.9; Hours 17: 33.6; Hours 0: 34.1; Hours 1: 34.1 | 34
| Condenser Delta "T" | ºC |  | Hours 15: 4.7; Hours 16: 4.7; Hours 17: 4.7; Hours 0: 4.9; Hours 1: 4.7 | 4.74
| Evaporator pressure (Kpag) | kpag |  | Hours 15: 275.8; Hours 16: 265.4; Hours 17: 255.1; Hours 0: 274.4; Hours 1: 262.7 | 266.68
| Condenser pressure (kpag) | kpag |  | Hours 15: 808.8; Hours 16: 792.9; Hours 17: 786.7; Hours 0: 795; Hours 1: 794.3 | 795.54
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2; Hours 0: 4.2; Hours 1: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7; Hours 0: 3.7; Hours 1: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 0: 3.8; Hours 1: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 0: 3; Hours 1: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 0: 0.5; Hours 1: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 0: 0.8; Hours 1: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 0: 971; Hours 1: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 15: 2568.7831; Hours 16: 2472.4537; Hours 17: 2504.5635; Hours 0: 2568.7831; Hours 1: 2408.2341 | 12522.8175
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1700 | 1500 | 1300 | 0 | 0 | 0 | 0 | 0 | 800 | 1600 | 1600 | 800 | 0 | 0 | 0 | 0 | 10300
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 15: 0.66179; Hours 16: 0.60668; Hours 17: 0.51905; Hours 0: 0.62286; Hours 1: 0.66439 | 0.61496
17 | Average iKW/TR |  |  | Hours 7: 0.61496 | 0.61496
18 | COP of chiller |  |  | Hours 15: 5.3128; Hours 16: 5.7954; Hours 17: 6.7739; Hours 0: 5.6449; Hours 1: 5.2921 | 5.7638
19 | EER of Chiller |  |  | Hours 15: 18.1327; Hours 16: 19.7798; Hours 17: 23.1193; Hours 0: 19.266; Hours 1: 18.0619 | 19.672
20 | LMTD of Condenser | ºC |  | Hours 15: 3.312; Hours 16: 3.312; Hours 17: 3.312; Hours 0: 3.1366; Hours 1: 3.0731 | 3.2291
21 | LMTD of Evaporator | ºC |  | Hours 15: 2.8236; Hours 16: 2.7527; Hours 17: 2.7764; Hours 0: 2.6277; Hours 1: 2.5141 | 2.6989
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6
2 | Small temperature difference of evaporator | ºC |  | 1 | 0.8 | 0.8 | 0.9 | 1.1 | 0.9 | 0.9 | 1 | 1.1 | 0.9 | 0.8 | 0.9 | 0.8 | 1.1 | 1.1 | 1.1 | 0.9 | 0.7 | 0.8 | 0.7 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8875
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.2 | 13.3 | 13.7 | 14.1 | 14.3 | 14.7 | 15.2 | 15.6 | 15.7 | 14.6 | 13.9 | 13.3 | 13.9 | 14.8 | 15.1 | 15.3 | 15.5 | 15.4 | 14.2 | 13.4 | 12.5 | 13.2 | 13.6 | 13.7 | 14.2583
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.3 | 5.6 | 5.8 | 5.9 | 6.3 | 6.8 | 7.1 | 7.6 | 7.7 | 6.8 | 6.1 | 5.6 | 5.9 | 6.6 | 6.8 | 7.3 | 7.4 | 7.7 | 6.7 | 5.9 | 5.3 | 5.8 | 5.8 | 5.9 | 6.4042
| Evaporator Delta "T" |  |  | 7.9 | 7.7 | 7.9 | 8.2 | 8 | 7.9 | 8.1 | 8 | 8 | 7.8 | 7.8 | 7.7 | 8 | 8.2 | 8.3 | 8 | 8.1 | 7.7 | 7.5 | 7.5 | 7.2 | 7.4 | 7.8 | 7.8 | 7.8542
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.8 | 26.3 | 26.7 | 26.9 | 28 | 28.2 | 28.7 | 28.2 | 29.6 | 29.2 | 28.9 | 28.3 | 27.4 | 27.7 | 27.7 | 27.7 | 27.9 | 29.3 | 29.4 | 29.2 | 28.2 | 27.4 | 27.4 | 27.2 | 27.9708
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.6 | 31.2 | 31.7 | 32.2 | 33.2 | 33.3 | 33.7 | 33.4 | 34.6 | 34.2 | 33.9 | 33.2 | 32.7 | 32.9 | 32.9 | 32.8 | 33 | 34.2 | 34.2 | 33.9 | 32.6 | 32.2 | 32.3 | 32.3 | 32.9667
| Condenser Delta "T" | ºC |  | 4.8 | 4.9 | 5 | 5.3 | 5.2 | 5.1 | 5 | 5.2 | 5 | 5 | 5 | 4.9 | 5.3 | 5.2 | 5.2 | 5.1 | 5.1 | 4.9 | 4.8 | 4.7 | 4.4 | 4.8 | 4.9 | 5.1 | 4.9958
| Evaporator pressure (Kpag) | kpag |  | 242 | 244.8 | 245.5 | 244.8 | 252.3 | 257.9 | 264.1 | 268.9 | 271 | 259.9 | 248.9 | 244.1 | 247.5 | 253.7 | 258.6 | 264.8 | 266.8 | 272.3 | 259.9 | 249.6 | 244.8 | 247.5 | 247.5 | 248.2 | 254.3917
| Condenser pressure (kpag) | kpag |  | 696.4 | 708.8 | 721.9 | 730.8 | 755.7 | 760.5 | 768.8 | 761.2 | 791.5 | 779.1 | 772.9 | 755 | 743.9 | 749.5 | 748.8 | 746.7 | 750.8 | 777 | 779.1 | 775 | 747.4 | 730.2 | 735 | 732.9 | 750.7875
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2472.4537 | 2536.6733 | 2633.0026 | 2568.7831 | 2536.6733 | 2600.8929 | 2568.7831 | 2568.7831 | 2504.5635 | 2504.5635 | 2472.4537 | 2568.7831 | 2633.0026 | 2665.1124 | 2568.7831 | 2600.8929 | 2472.4537 | 2408.2341 | 2408.2341 | 2311.9048 | 2376.1243 | 2504.5635 | 2504.5635 | 60526.9511
15 | Power Consumption of Chiller | KWH |  | 1400 | 1500 | 1600 | 1600 | 1500 | 1400 | 1700 | 1600 | 1400 | 1600 | 1700 | 1400 | 1700 | 1400 | 1600 | 1500 | 1600 | 1500 | 1400 | 1500 | 1500 | 1500 | 1500 | 1500 | 36600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.5519 | 0.60668 | 0.63075 | 0.60767 | 0.58393 | 0.5519 | 0.65362 | 0.62286 | 0.54501 | 0.63883 | 0.67876 | 0.56624 | 0.66179 | 0.53171 | 0.60035 | 0.58393 | 0.61517 | 0.60668 | 0.58134 | 0.62286 | 0.64882 | 0.63128 | 0.59891 | 0.59891 | 0.605
17 | Average iKW/TR |  |  | Hours 7: 0.605 | 0.605
18 | COP of chiller |  |  | 6.3707 | 5.7954 | 5.5743 | 5.786 | 6.0212 | 6.3707 | 5.3793 | 5.6449 | 6.4513 | 5.5038 | 5.18 | 6.2094 | 5.3128 | 6.6126 | 5.8566 | 6.0212 | 5.7155 | 5.7954 | 6.0481 | 5.6449 | 5.4191 | 5.5696 | 5.8707 | 5.8707 | 5.8343
19 | EER of Chiller |  |  | 21.7431 | 19.7798 | 19.0252 | 19.7477 | 20.5504 | 21.7431 | 18.3594 | 19.266 | 22.0183 | 18.7844 | 17.6794 | 21.1927 | 18.1327 | 22.5688 | 19.9885 | 20.5504 | 19.5069 | 19.7798 | 20.6422 | 19.266 | 18.4954 | 19.0092 | 20.0367 | 20.0367 | 19.9126
20 | LMTD of Condenser | ºC |  | 2.1846 | 2.2116 | 2.2385 | 2.3187 | 2.2921 | 2.2654 | 2.2385 | 2.2921 | 2.3842 | 2.2385 | 2.2385 | 2.2116 | 2.3187 | 2.2921 | 2.2921 | 2.2654 | 2.2654 | 2.2116 | 2.1846 | 2.1574 | 2.0752 | 2.0332 | 2.2116 | 2.2654 | 2.237
21 | LMTD of Evaporator | ºC |  | 3.6138 | 3.2583 | 3.3103 | 3.5442 | 3.7862 | 3.4647 | 3.5178 | 3.641 | 3.7862 | 3.4381 | 3.2843 | 3.4114 | 3.3363 | 3.8413 | 3.8687 | 3.7862 | 3.5178 | 3.0987 | 3.206 | 3.0478 | 3.1269 | 3.0222 | 3.1241 | 3.2843 | 3.4299
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
19 | EER of Chiller |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
20 | LMTD of Condenser | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
21 | LMTD of Evaporator | ºC |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## 26-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 26/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [8 empty] | 0.5 | 0.5 | 0.3 | 0.4 | 0.5 | 0.3 | 0.3 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.42353
2 | Small temperature difference of evaporator | ºC | [8 empty] | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.5 | 0.6 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.57647
3 | Entering Chilled Water Temp. (tchwe) | ºC | [8 empty] | 15.6 | 14.6 | 13.8 | 13.2 | 12.9 | 13.9 | 14.2 | 14.4 | 14.3 | 14.4 | 14.2 | 13.9 | 13.7 | 13.6 | 13.5 | 13.4 | 13.2 | 13.9294
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [8 empty] | 7.6 | 6.8 | 5.9 | 5.4 | 5.6 | 5.7 | 5.9 | 6.1 | 6.1 | 6.1 | 5.9 | 5.6 | 5.5 | 5.5 | 5.5 | 5.6 | 5.5 | 5.9
| Evaporator Delta "T" | [9 empty] | 8 | 7.8 | 7.9 | 7.8 | 7.3 | 8.2 | 8.3 | 8.3 | 8.2 | 8.3 | 8.3 | 8.3 | 8.2 | 8.1 | 8 | 7.8 | 7.7 | 8.0294
5 | Entering Condenser Water Temp. (tcwe) | ºC | [8 empty] | 28 | 28.2 | 28.1 | 27.8 | 26.5 | 26.3 | 26.3 | 26.3 | 26.2 | 26.4 | 26.1 | 26.1 | 26.3 | 26.3 | 26 | 25.8 | 25.8 | 26.6176
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [8 empty] | 33.2 | 33.6 | 33.3 | 33.1 | 31.3 | 31.8 | 31.9 | 31.9 | 31.9 | 32.1 | 31.8 | 31.6 | 31.7 | 31.7 | 31.4 | 31.1 | 31.1 | 32.0294
| Condenser Delta "T" | ºC | [8 empty] | 5.2 | 5.4 | 5.2 | 5.3 | 4.8 | 5.5 | 5.6 | 5.6 | 5.7 | 5.7 | 5.7 | 5.5 | 5.4 | 5.4 | 5.4 | 5.3 | 5.3 | 5.4118
| Evaporator pressure (Kpag) | kpag | [8 empty] | 274.4 | 264.8 | 253 | 246.8 | 247.5 | 250.3 | 253 | 255.1 | 253 | 254.4 | 251 | 248.2 | 247.5 | 247.5 | 246.8 | 248.2 | 246.8 | 252.2529
| Condenser pressure (kpag) | kpag | [8 empty] | 754.3 | 759.1 | 753.6 | 747.4 | 707.4 | 719.1 | 721.9 | 723.3 | 720.5 | 719.8 | 719.1 | 715.7 | 717.7 | 714.3 | 709.5 | 701.9 | 701.2 | 723.8706
7 | Chilled water inlet pressure | (Kg/Cm2) | [8 empty] | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) | [8 empty] | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) | [8 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [8 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [8 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [8 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [8 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [8 empty] | 2568.7831 | 2504.5635 | 2536.6733 | 2504.5635 | 2344.0146 | 2633.0026 | 2665.1124 | 2665.1124 | 2633.0026 | 2665.1124 | 2665.1124 | 2665.1124 | 2633.0026 | 2600.8929 | 2568.7831 | 2504.5635 | 2472.4537 | 43829.8611
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 1400 | 1500 | 1400 | 1300 | 1400 | 1400 | 1500 | 1500 | 1500 | 1300 | 1600 | 1400 | 1500 | 1400 | 1400 | 1300 | 1300 | 24500
16 | Specific power consumption of Chiller | (iKW/TR) | [8 empty] | 0.54501 | 0.59891 | 0.5519 | 0.51905 | 0.59727 | 0.53171 | 0.56283 | 0.56283 | 0.56969 | 0.48778 | 0.60035 | 0.52531 | 0.56969 | 0.53828 | 0.54501 | 0.51905 | 0.52579 | 0.55003
17 | Average iKW/TR |  |  | Hours 7: 0.55003 | 0.55003
18 | COP of chiller | [9 empty] | 6.4513 | 5.8707 | 6.3707 | 6.7739 | 5.8868 | 6.6126 | 6.247 | 6.247 | 6.1718 | 7.2081 | 5.8566 | 6.6932 | 6.1718 | 6.532 | 6.4513 | 6.7739 | 6.687 | 6.4121
19 | EER of Chiller | [9 empty] | 22.0183 | 20.0367 | 21.7431 | 23.1193 | 20.0917 | 22.5688 | 21.3211 | 21.3211 | 21.0642 | 24.6013 | 19.9885 | 22.844 | 21.0642 | 22.2936 | 22.0183 | 23.1193 | 22.8229 | 21.8845
20 | LMTD of Condenser | ºC | [8 empty] | 2.1367 | 2.1879 | 1.7877 | 1.9949 | 2.0332 | 1.857 | 1.8799 | 2.0679 | 2.264 | 2.0921 | 2.0921 | 2.2134 | 2.1879 | 2.1879 | 2.0193 | 1.9949 | 1.9949 | 2.0583
21 | LMTD of Evaporator | ºC | [8 empty] | 2.6277 | 2.5824 | 2.6051 | 2.5824 | 2.832 | 2.8707 | 3.0776 | 3.2499 | 3.0533 | 3.0776 | 3.2499 | 3.2499 | 3.2249 | 3.1998 | 3.0046 | 2.9556 | 2.931 | 2.9632
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.6 | 0.5 | 0.6 | 0.7 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.8 | 0.6 | 0.7 | 0.6 | 0.63333
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.6 | 0.5 | 0.6 | 0.6 | 0.7 | 0.4 | 0.7 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.6 | 0.5 | 0.55417
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.8 | 14 | 14.3 | 14.7 | 14.9 | 15.2 | 15.4 | 15.6 | 14.6 | 13.7 | 13.2 | 12.8 | 13.8 | 14.2 | 14.4 | 14.5 | 14.3 | 14.2 | 13.8 | 13.6 | 13.5 | 13.3 | 13.2 | 13.2 | 14.0917
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.1 | 6.2 | 6.4 | 6.4 | 6.9 | 7.1 | 7.2 | 7.5 | 6.9 | 6.2 | 5.8 | 5.4 | 5.9 | 6.1 | 6.2 | 6.2 | 6.2 | 6.2 | 5.8 | 5.7 | 5.6 | 5.6 | 5.4 | 5.5 | 6.1875
| Evaporator Delta "T" |  |  | 7.7 | 7.8 | 7.9 | 8.3 | 8 | 8.1 | 8.2 | 8.1 | 7.7 | 7.5 | 7.4 | 7.4 | 7.9 | 8.1 | 8.2 | 8.3 | 8.1 | 8 | 8 | 7.9 | 7.9 | 7.7 | 7.8 | 7.7 | 7.9042
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 27.4 | 27.4 | 27.4 | 27.6 | 27.8 | 27.9 | 27.7 | 28.3 | 28.7 | 28.4 | 28.2 | 26.9 | 26.7 | 26.8 | 26.8 | 26.6 | 26.7 | 26.6 | 26.5 | 26.8 | 26.6 | 26.4 | 26.3 | 26.2 | 27.1958
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.8 | 31.8 | 31.8 | 32.2 | 32.3 | 32.7 | 32.4 | 32.8 | 32.9 | 32.7 | 32.4 | 31 | 31.2 | 31.4 | 31.3 | 31.3 | 31.3 | 31.1 | 31 | 31.1 | 31 | 30.9 | 30.7 | 30.5 | 31.65
| Condenser Delta "T" | ºC |  | 4.4 | 4.4 | 4.4 | 4.6 | 4.5 | 4.8 | 4.7 | 4.5 | 4.2 | 4.3 | 4.2 | 4.1 | 4.5 | 4.6 | 4.5 | 4.7 | 4.6 | 4.5 | 4.5 | 4.3 | 4.4 | 4.5 | 4.4 | 4.3 | 4.4542
| Evaporator pressure (Kpag) | kpag |  | 255.1 | 257.2 | 259.2 | 260.6 | 263.4 | 266.1 | 268.2 | 271 | 265.4 | 255.8 | 251 | 248.2 | 252.3 | 253.7 | 257.9 | 256.5 | 257.2 | 255.1 | 251.7 | 249.6 | 248.2 | 248.9 | 246.8 | 248.2 | 256.1375
| Condenser pressure (kpag) | kpag |  | 721.9 | 724.6 | 726 | 730.8 | 737.7 | 743.3 | 738.4 | 750.1 | 751.5 | 742.6 | 737.7 | 702.6 | 710.2 | 713.6 | 712.9 | 712.2 | 712.9 | 709.5 | 706 | 708.8 | 706.7 | 700.5 | 697.7 | 694.3 | 720.5208
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2472.4537 | 2504.5635 | 2536.6733 | 2665.1124 | 2568.7831 | 2600.8929 | 2633.0026 | 2600.8929 | 2472.4537 | 2408.2341 | 2376.1243 | 2376.1243 | 2536.6733 | 2600.8929 | 2633.0026 | 2665.1124 | 2600.8929 | 2568.7831 | 2568.7831 | 2536.6733 | 2536.6733 | 2472.4537 | 2504.5635 | 2472.4537 | 60912.2685
15 | Power Consumption of Chiller | KWH |  | 1500 | 1700 | 1400 | 1600 | 1500 | 1600 | 1600 | 1400 | 1500 | 1400 | 1700 | 1400 | 1500 | 1500 | 1400 | 1600 | 1500 | 1400 | 1700 | 1400 | 1500 | 1500 | 1400 | 1300 | 36000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.60668 | 0.67876 | 0.5519 | 0.60035 | 0.58393 | 0.61517 | 0.60767 | 0.53828 | 0.60668 | 0.58134 | 0.71545 | 0.58919 | 0.59133 | 0.57673 | 0.53171 | 0.60035 | 0.57673 | 0.54501 | 0.66179 | 0.5519 | 0.59133 | 0.60668 | 0.55898 | 0.52579 | 0.59141
17 | Average iKW/TR |  |  | Hours 7: 0.59141 | 0.59141
18 | COP of chiller |  |  | 5.7954 | 5.18 | 6.3707 | 5.8566 | 6.0212 | 5.7155 | 5.786 | 6.532 | 5.7954 | 6.0481 | 4.9144 | 5.9675 | 5.946 | 6.0965 | 6.6126 | 5.8566 | 6.0965 | 6.4513 | 5.3128 | 6.3707 | 5.946 | 5.7954 | 6.29 | 6.687 | 5.9768
19 | EER of Chiller |  |  | 19.7798 | 17.6794 | 21.7431 | 19.9885 | 20.5504 | 19.5069 | 19.7477 | 22.2936 | 19.7798 | 20.6422 | 16.7728 | 20.367 | 20.2936 | 20.8073 | 22.5688 | 19.9885 | 20.8073 | 22.0183 | 18.1327 | 21.7431 | 20.2936 | 19.7798 | 21.4679 | 22.8229 | 20.399
20 | LMTD of Condenser | ºC |  | 1.9278 | 2.0752 | 2.0752 | 2.1301 | 2.1027 | 2.3285 | 2.3005 | 2.244 | 2.0198 | 2.1871 | 2.1584 | 1.9918 | 1.9543 | 2.1301 | 2.244 | 2.1574 | 2.2723 | 2.1027 | 2.1027 | 2.0476 | 2.3507 | 2.1027 | 2.2156 | 2.0476 | 2.1362
21 | LMTD of Evaporator | ºC |  | 2.5597 | 2.9556 | 2.8 | 3.0776 | 3.0046 | 3.1998 | 2.6727 | 3.1998 | 2.7527 | 2.8816 | 2.6811 | 2.6811 | 2.8 | 2.8472 | 3.2249 | 3.0776 | 3.029 | 3.0046 | 3.0046 | 2.8 | 2.8 | 2.7527 | 2.9556 | 2.7527 | 2.8965
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 0.6; Hours 8: 0.6; Hours 9: 0.6; Hours 10: 0.6; Hours 11: 0.6; Hours 12: 0.6; Hours 13: 0.6; Hours 14: 0.6; Hours 15: 0.4; Hours 16: 0.6; Hours 17: 0.6 | 0.58182
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.9; Hours 8: 0.9; Hours 9: 0.9; Hours 10: 1; Hours 11: 0.9; Hours 12: 0.9; Hours 13: 0.9; Hours 14: 0.9; Hours 15: 0.7; Hours 16: 0.8; Hours 17: 0.7 | 0.86364
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 13.8; Hours 8: 14.1; Hours 9: 14.4; Hours 10: 14.7; Hours 11: 15.1; Hours 12: 15.3; Hours 13: 15.6; Hours 14: 15.7; Hours 15: 14.7; Hours 16: 13.9; Hours 17: 13.4 | 14.6091
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 6; Hours 8: 6.1; Hours 9: 6.2; Hours 10: 6.7; Hours 11: 7.2; Hours 12: 7.3; Hours 13: 7.4; Hours 14: 7.8; Hours 15: 7.1; Hours 16: 6.4; Hours 17: 6.1 | 6.7545
| Evaporator Delta "T" |  |  | Hours 7: 7.8; Hours 8: 8; Hours 9: 8.2; Hours 10: 8; Hours 11: 7.9; Hours 12: 8; Hours 13: 8.2; Hours 14: 7.9; Hours 15: 7.6; Hours 16: 7.5; Hours 17: 7.3 | 7.8545
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 27.3; Hours 8: 27.4; Hours 9: 27.4; Hours 10: 27.4; Hours 11: 27.9; Hours 12: 28; Hours 13: 27.7; Hours 14: 28.2; Hours 15: 28.8; Hours 16: 28.4; Hours 17: 28.2 | 27.8818
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 32.4; Hours 8: 32.5; Hours 9: 32.6; Hours 10: 32.6; Hours 11: 32.8; Hours 12: 32.9; Hours 13: 32.8; Hours 14: 33.3; Hours 15: 33.5; Hours 16: 33.1; Hours 17: 32.8 | 32.8455
| Condenser Delta "T" | ºC |  | Hours 7: 5.1; Hours 8: 5.1; Hours 9: 5.2; Hours 10: 5.2; Hours 11: 4.9; Hours 12: 4.9; Hours 13: 5.1; Hours 14: 5.1; Hours 15: 4.7; Hours 16: 4.7; Hours 17: 4.6 | 4.9636
| Evaporator pressure (Kpag) | kpag |  | Hours 7: 248.2; Hours 8: 250.3; Hours 9: 251; Hours 10: 255.8; Hours 11: 265.4; Hours 12: 266.1; Hours 13: 266.1; Hours 14: 271.7; Hours 15: 264.8; Hours 16: 257.2; Hours 17: 252.3 | 258.9909
| Condenser pressure (kpag) | kpag |  | Hours 7: 737; Hours 8: 739.8; Hours 9: 741.9; Hours 10: 743.3; Hours 11: 746; Hours 12: 749.5; Hours 13: 747.4; Hours 14: 755.7; Hours 15: 763.2; Hours 16: 752.9; Hours 17: 746 | 747.5182
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.2; Hours 8: 4.2; Hours 9: 4.2; Hours 10: 4.2; Hours 11: 4.2; Hours 12: 4.2; Hours 13: 4.2; Hours 14: 4.2; Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.7; Hours 8: 3.7; Hours 9: 3.7; Hours 10: 3.7; Hours 11: 3.7; Hours 12: 3.7; Hours 13: 3.7; Hours 14: 3.7; Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2504.5635; Hours 8: 2568.7831; Hours 9: 2633.0026; Hours 10: 2568.7831; Hours 11: 2536.6733; Hours 12: 2568.7831; Hours 13: 2633.0026; Hours 14: 2536.6733; Hours 15: 2440.3439; Hours 16: 2408.2341; Hours 17: 2344.0146 | 27742.8571
15 | Power Consumption of Chiller | KWH |  | 1400 | 1700 | 1500 | 1600 | 1300 | 1700 | 1300 | 1500 | 1400 | 1300 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15600
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.55898; Hours 8: 0.66179; Hours 9: 0.56969; Hours 10: 0.62286; Hours 11: 0.51248; Hours 12: 0.66179; Hours 13: 0.49373; Hours 14: 0.59133; Hours 15: 0.57369; Hours 16: 0.53981; Hours 17: 0.38396 | 0.56092
17 | Average iKW/TR |  |  | Hours 7: 0.56092 | 0.56092
18 | COP of chiller |  |  | Hours 7: 6.29; Hours 8: 5.3128; Hours 9: 6.1718; Hours 10: 5.6449; Hours 11: 6.8607; Hours 12: 5.3128; Hours 13: 7.1213; Hours 14: 5.946; Hours 15: 6.1287; Hours 16: 6.5133; Hours 17: 9.1573 | 6.4054
19 | EER of Chiller |  |  | Hours 7: 21.4679; Hours 8: 18.1327; Hours 9: 21.0642; Hours 10: 19.266; Hours 11: 23.4157; Hours 12: 18.1327; Hours 13: 24.3049; Hours 14: 20.2936; Hours 15: 20.9174; Hours 16: 22.2301; Hours 17: 31.2538 | 21.8617
20 | LMTD of Condenser | ºC |  | Hours 7: 2.2654; Hours 8: 2.2654; Hours 9: 2.2921; Hours 10: 2.2921; Hours 11: 2.2116; Hours 12: 2.2116; Hours 13: 2.2654; Hours 14: 2.2654; Hours 15: 1.8464; Hours 16: 2.1574; Hours 17: 2.1301 | 2.2003
21 | LMTD of Evaporator | ºC |  | Hours 7: 3.4381; Hours 8: 3.4913; Hours 9: 3.5442; Hours 10: 3.641; Hours 11: 3.4647; Hours 12: 3.4913; Hours 13: 3.5442; Hours 14: 3.4647; Hours 15: 3.0733; Hours 16: 3.206; Hours 17: 2.9966 | 3.3959
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!

## 27-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 27/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.3 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.6 | 0.4 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.4 | 0.5 | 0.2 | 0.4 | 0.3 | 0.4 | 0.4 | 0.425
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.5 | 0.625
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.1 | 13.7 | 14 | 14 | 14.2 | 14.3 | 14.5 | 14.6 | 14.6 | 14.7 | 14.6 | 14.4 | 14.1 | 13.9 | 14.1 | 13.7 | 13.6 | 13.3 | 12.9 | 12.9 | 13.1 | 12.7 | 12.6 | 13.7792
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.5 | 5.5 | 5.7 | 5.7 | 5.8 | 5.8 | 6.1 | 6.1 | 6.2 | 5.8 | 5.8 | 5.6 | 5.4 | 5.6 | 5.6 | 5.6 | 5.5 | 5.5 | 5.6 | 5.7 | 5.4 | 5.5 | 5.5 | 5.6667
| Evaporator Delta "T" |  |  | 7.6 | 7.6 | 8.2 | 8.3 | 8.3 | 8.4 | 8.5 | 8.4 | 8.5 | 8.4 | 8.9 | 8.8 | 8.8 | 8.7 | 8.3 | 8.5 | 8.1 | 8.1 | 7.8 | 7.3 | 7.2 | 7.7 | 7.2 | 7.1 | 8.1125
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.9 | 25.7 | 25.8 | 26.3 | 26.8 | 26.8 | 26.8 | 26.2 | 26.4 | 26.3 | 26.1 | 26.3 | 25 | 24.8 | 24.6 | 24.6 | 24.7 | 24.6 | 24.6 | 24.7 | 24.6 | 24.7 | 24.7 | 24.4 | 25.475
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.7 | 30.8 | 31.2 | 31.9 | 32.4 | 32.4 | 32.4 | 32.2 | 32.1 | 32.1 | 32.1 | 32.4 | 31.2 | 30.6 | 30.1 | 30.3 | 30.1 | 30 | 29.7 | 29.7 | 29.4 | 29.6 | 29.6 | 29.2 | 30.925
| Condenser Delta "T" | ºC |  | 4.8 | 5.1 | 5.4 | 5.6 | 5.6 | 5.6 | 5.6 | 6 | 5.7 | 5.8 | 6 | 6.1 | 6.2 | 5.8 | 5.5 | 5.7 | 5.4 | 5.4 | 5.1 | 5 | 4.8 | 4.9 | 4.9 | 4.8 | 5.45
| Evaporator pressure (Kpag) | kpag |  | 248.2 | 246.8 | 247.5 | 250.3 | 250.3 | 251 | 251 | 251.7 | 253.7 | 253 | 248.2 | 250.3 | 246.1 | 244.8 | 246.8 | 248.9 | 247.5 | 246.8 | 247.5 | 246.1 | 248.2 | 246.1 | 248.2 | 247.5 | 248.6042
| Condenser pressure (kpag) | kpag |  | 695 | 696.4 | 704.6 | 719.8 | 731.5 | 732.9 | 735.7 | 728.1 | 727.4 | 727.4 | 729.5 | 732.9 | 703.3 | 692.2 | 681.2 | 676.4 | 679.8 | 681.9 | 673.6 | 670.9 | 667.4 | 670.9 | 669.5 | 660.5 | 699.5333
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2440.3439 | 2633.0026 | 2665.1124 | 2665.1124 | 2697.2222 | 2729.332 | 2697.2222 | 2729.332 | 2697.2222 | 2857.7712 | 2825.6614 | 2825.6614 | 2793.5516 | 2665.1124 | 2729.332 | 2600.8929 | 2600.8929 | 2504.5635 | 2344.0146 | 2311.9048 | 2472.4537 | 2311.9048 | 2279.795 | 62517.7579
15 | Power Consumption of Chiller | KWH |  | 1300 | 1500 | 1400 | 1500 | 1300 | 1600 | 1600 | 1400 | 1500 | 1600 | 1500 | 1600 | 1500 | 1400 | 1500 | 1300 | 1500 | 1300 | 1200 | 1300 | 1300 | 1200 | 1200 | 1100 | 33600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53271 | 0.61467 | 0.53171 | 0.56283 | 0.48778 | 0.5932 | 0.58622 | 0.51905 | 0.54959 | 0.5932 | 0.52488 | 0.56624 | 0.53085 | 0.50115 | 0.56283 | 0.47631 | 0.57673 | 0.49983 | 0.47913 | 0.5546 | 0.56231 | 0.48535 | 0.51905 | 0.4825 | 0.5372
17 | Average iKW/TR |  |  | Hours 7: 0.5372 | 0.5372
18 | COP of chiller |  |  | 6.6002 | 5.7202 | 6.6126 | 6.247 | 7.2081 | 5.9271 | 5.9977 | 6.7739 | 6.3976 | 5.9271 | 6.6986 | 6.2094 | 6.6234 | 7.0158 | 6.247 | 7.3818 | 6.0965 | 7.0344 | 7.3384 | 6.3397 | 6.2528 | 7.2443 | 6.7739 | 7.2871 | 6.5814
19 | EER of Chiller |  |  | 22.5265 | 19.5229 | 22.5688 | 21.3211 | 24.6013 | 20.2293 | 20.4702 | 23.1193 | 21.8349 | 20.2293 | 22.8624 | 21.1927 | 22.6055 | 23.9449 | 21.3211 | 25.1941 | 20.8073 | 24.0085 | 25.0459 | 21.6373 | 21.3409 | 24.7248 | 23.1193 | 24.8707 | 22.4624
20 | LMTD of Condenser | ºC |  | 1.6942 | 1.9458 | 2.0193 | 2.0679 | 2.2387 | 2.0679 | 2.0679 | 2.164 | 2.4241 | 2.1161 | 2.3392 | 2.3641 | 2.389 | 2.1161 | 2.0437 | 2.264 | 2.3452 | 2.0193 | 2.111 | 1.5346 | 1.8714 | 1.7177 | 1.8963 | 1.8714 | 2.0704
21 | LMTD of Evaporator | ºC |  | 2.7289 | 2.7289 | 3.0533 | 3.0776 | 3.0776 | 3.1019 | 3.126 | 3.1019 | 3.126 | 3.1019 | 3.399 | 3.3743 | 3.1982 | 3.3495 | 3.2499 | 3.2998 | 3.1998 | 3.029 | 3.1241 | 2.832 | 2.8071 | 3.0987 | 2.9709 | 2.6091 | 3.0736
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 6: 0.8 | 0.8
2 | Small temperature difference of evaporator | ºC |  | Hours 6: 0.4 | 0.4
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 6: 12.6 | 12.6
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 6: 5.5 | 5.5
| Evaporator Delta "T" |  |  | Hours 6: 7.1 | 7.1
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 6: 24.5 | 24.5
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 6: 28.8 | 28.8
| Condenser Delta "T" | ºC |  | Hours 6: 4.3 | 4.3
| Evaporator pressure (Kpag) | kpag |  | Hours 6: 248.9 | 248.9
| Condenser pressure (kpag) | kpag |  | Hours 6: 653.6 | 653.6
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 6: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 6: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 6: 2279.795 | 2279.795
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 1300 | 1700
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 6: 0.57023 | 0.57023
17 | Average iKW/TR |  |  | Hours 7: 0.57023 | 0.57023
18 | COP of chiller |  |  | Hours 6: 6.166 | 6.166
19 | EER of Chiller |  |  | Hours 6: 21.0445 | 21.0445
20 | LMTD of Condenser | ºC |  | Hours 6: 2.3213 | 2.3213
21 | LMTD of Evaporator | ºC |  | Hours 6: 2.4222 | 2.4222
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.5 | 0.7 | 0.6 | 0.7 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.5 | 0.5 | 0.7 | 0.5 |  | 0.6
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.5 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.5 |  | 0.56522
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 12.9 | 13.6 | 13.9 | 13.9 | 14 | 14.2 | 14.4 | 14.6 | 14.5 | 14.4 | 14.4 | 14.3 | 14 | 13.8 | 13.6 | 13.6 | 13.4 | 13.1 | 12.8 | 12.8 | 12.8 | 12.7 |  | 13.687
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.5 | 5.6 | 5.9 | 5.9 | 5.9 | 6.1 | 6.2 | 6.2 | 6.3 | 6.3 | 6.1 | 5.7 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.4 | 5.5 | 5.6 | 5.5 | 5.5 |  | 5.7478
| Evaporator Delta "T" |  |  | 7.6 | 7.4 | 8 | 8 | 8 | 8.1 | 8.1 | 8.2 | 8.4 | 8.2 | 8.1 | 8.3 | 8.6 | 8.5 | 8.3 | 8.1 | 8.1 | 7.9 | 7.7 | 7.3 | 7.2 | 7.3 | 7.2 |  | 7.9391
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26.2 | 26.2 | 26.3 | 26.7 | 27.2 | 27.2 | 27.1 | 26.8 | 26.9 | 26.8 | 26.7 | 27 | 25.6 | 25.2 | 25.1 | 25 | 25.1 | 25.1 | 25.1 | 25.2 | 25 | 25.1 | 25.3 |  | 25.9957
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.3 | 30.3 | 30.7 | 31.2 | 31.8 | 31.7 | 31.8 | 31.6 | 31.6 | 31.5 | 31.4 | 31.7 | 30.4 | 30 | 29.7 | 29.6 | 29.7 | 29.6 | 29.3 | 29.3 | 29 | 29.1 | 29.3 |  | 30.4609
| Condenser Delta "T" | ºC |  | 4.1 | 4.1 | 4.4 | 4.5 | 4.6 | 4.5 | 4.7 | 4.8 | 4.7 | 4.7 | 4.7 | 4.7 | 4.8 | 4.8 | 4.6 | 4.6 | 4.6 | 4.5 | 4.2 | 4.1 | 4 | 4 | 4 |  | 4.4652
| Evaporator pressure (Kpag) | kpag |  | 248.9 | 248.9 | 249.6 | 253 | 253 | 251.7 | 255.1 | 255.8 | 255.8 | 255.1 | 257.2 | 253.7 | 249.6 | 246.8 | 246.8 | 246.8 | 247.5 | 246.8 | 246.8 | 248.2 | 251 | 248.9 | 248.9 |  | 250.6913
| Condenser pressure (kpag) | kpag |  | 688.8 | 687.4 | 696.4 | 710.2 | 721.9 | 726 | 724.6 | 717.7 | 717.7 | 717.1 | 712.9 | 721.9 | 692.2 | 682.6 | 676.4 | 672.9 | 673.6 | 673.6 | 667.4 | 664.7 | 659.8 | 661.9 | 663.3 |  | 692.6522
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2376.1243 | 2568.7831 | 2568.7831 | 2568.7831 | 2600.8929 | 2600.8929 | 2633.0026 | 2697.2222 | 2633.0026 | 2600.8929 | 2665.1124 | 2761.4418 | 2729.332 | 2665.1124 | 2600.8929 | 2600.8929 | 2536.6733 | 2472.4537 | 2344.0146 | 2311.9048 | 2344.0146 | 2311.9048 |  | 58632.4735
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1400 | 1500 | 1600 | 1600 | 1600 | 1500 | 1500 | 1500 | 1600 | 1700 | 1600 | 1400 | 1500 | 1500 | 1500 | 1300 | 1400 | 1400 | 1300 | 1300 | 800 | 0 | 33500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.61467 | 0.63128 | 0.54501 | 0.58393 | 0.62286 | 0.61517 | 0.61517 | 0.56969 | 0.55613 | 0.56969 | 0.61517 | 0.63787 | 0.57941 | 0.51295 | 0.56283 | 0.57673 | 0.57673 | 0.51248 | 0.56624 | 0.59727 | 0.56231 | 0.5546 | 0.34604 |  | 0.57062
17 | Average iKW/TR |  |  | Hours 7: 0.57062 | 0.57062
18 | COP of chiller |  |  | 5.7202 | 5.5696 | 6.4513 | 6.0212 | 5.6449 | 5.7155 | 5.7155 | 6.1718 | 6.3223 | 6.1718 | 5.7155 | 5.5121 | 6.0683 | 6.8545 | 6.247 | 6.0965 | 6.0965 | 6.8607 | 6.2094 | 5.8868 | 6.2528 | 6.3397 | 10.1608 |  | 6.2524
19 | EER of Chiller |  |  | 19.5229 | 19.0092 | 22.0183 | 20.5504 | 19.266 | 19.5069 | 19.5069 | 21.0642 | 21.578 | 21.0642 | 19.5069 | 18.8127 | 20.711 | 23.3945 | 21.3211 | 20.8073 | 20.8073 | 23.4157 | 21.1927 | 20.0917 | 21.3409 | 21.6373 | 34.6789 |  | 21.3393
20 | LMTD of Condenser | ºC |  | 1.9918 | 1.9918 | 2.0752 | 2.1027 | 2.2723 | 1.9543 | 2.3005 | 2.1846 | 2.3005 | 2.1574 | 2.1574 | 2.3005 | 2.1846 | 2.1846 | 2.1301 | 2.1301 | 1.9807 | 2.1027 | 2.0198 | 1.8475 | 1.8205 | 2.1006 | 1.8205 |  | 2.0918
21 | LMTD of Evaporator | ºC |  | 2.7289 | 2.6811 | 2.6277 | 2.8236 | 3.0046 | 3.029 | 3.029 | 3.0533 | 3.1019 | 3.0533 | 3.029 | 3.0776 | 3.3247 | 3.126 | 3.2499 | 3.029 | 3.029 | 2.9801 | 2.931 | 2.6572 | 2.6332 | 2.4683 | 2.6332 |  | 2.9261
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!

## 28-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 28/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.4 | 0.4 | 0.2 | 0.4 | 0.5 | 0.7 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.5 | 0.6 | 0.42917
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.7 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.9 | 1.1 | 1.4 | 2.2 | 1 | 0.9 | 0.80833
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 12.9 | 12.8 | 13.2 | 13.7 | 13.6 | 13.6 | 13.7 | 14.1 | 14.4 | 14.5 | 14.7 | 14.6 | 14.2 | 14.2 | 13.9 | 13.7 | 13.3 | 13 | 12.7 | 12.1 | 13.2 | 14 | 14.5 | 14.7 | 13.7208
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.5 | 5.5 | 5.5 | 5.6 | 5.5 | 5.6 | 5.6 | 5.7 | 5.7 | 5.7 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.4 | 5.4 | 5.3 | 5.7 | 5.7 | 5.6 | 5.6 | 5.6 | 5.575
| Evaporator Delta "T" |  |  | 7.3 | 7.3 | 7.7 | 8.2 | 8 | 8.1 | 8.1 | 8.5 | 8.7 | 8.8 | 9 | 9 | 8.6 | 8.6 | 8.3 | 8.1 | 7.9 | 7.6 | 7.4 | 6.4 | 7.5 | 8.4 | 8.9 | 9.1 | 8.1458
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.5 | 24.4 | 25.3 | 25.2 | 25.6 | 25.8 | 26.1 | 26.3 | 26.3 | 26 | 26 | 25.5 | 25.2 | 24.6 | 23.9 | 22.8 | 21.7 | 21.4 | 21.3 | 20.7 | 20.5 | 20.7 | 20.3 | 20.2 | 23.7625
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.3 | 29.6 | 30.5 | 30.4 | 30.8 | 31.2 | 31.7 | 31.9 | 32 | 31.8 | 32 | 31.4 | 31 | 30.4 | 29.3 | 28.1 | 27.1 | 26.6 | 26.2 | 25.1 | 25.6 | 26.2 | 26.2 | 26.4 | 29.2
| Condenser Delta "T" | ºC |  | 4.8 | 5.2 | 5.2 | 5.2 | 5.2 | 5.4 | 5.6 | 5.6 | 5.7 | 5.8 | 6 | 5.9 | 5.8 | 5.8 | 5.4 | 5.3 | 5.4 | 5.2 | 4.9 | 4.4 | 5.1 | 5.5 | 5.9 | 6.2 | 5.4375
| Evaporator pressure (Kpag) | kpag |  | 248.2 | 246.1 | 247.5 | 246.8 | 248.9 | 247.5 | 248.9 | 248.2 | 249.6 | 248.2 | 247.5 | 246.8 | 247.5 | 245.5 | 245.5 | 246.8 | 243.4 | 240.6 | 239.9 | 235.1 | 238.6 | 242 | 242.7 | 242.7 | 245.1875
| Condenser pressure (kpag) | kpag |  | 661.9 | 669.5 | 690.2 | 690.9 | 699.1 | 703.3 | 715.7 | 723.3 | 723.9 | 721.9 | 725.3 | 712.9 | 702.6 | 686 | 666.7 | 637.1 | 612.9 | 606 | 595.7 | 574.3 | 586.7 | 597.8 | 600.5 | 599.8 | 662.6667
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2344.0146 | 2344.0146 | 2472.4537 | 2633.0026 | 2568.7831 | 2600.8929 | 2600.8929 | 2729.332 | 2793.5516 | 2825.6614 | 2889.881 | 2889.881 | 2761.4418 | 2761.4418 | 2665.1124 | 2600.8929 | 2536.6733 | 2440.3439 | 2376.1243 | 2055.0265 | 2408.2341 | 2697.2222 | 2857.7712 | 2921.9907 | 62774.6362
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1500 | 1300 | 1400 | 1400 | 1500 | 1500 | 1600 | 1600 | 1500 | 1600 | 1600 | 1400 | 1300 | 1300 | 1300 | 1100 | 1100 | 1200 | 1200 | 1400 | 1400 | 1500 | 33300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.5546 | 0.5546 | 0.60668 | 0.49373 | 0.54501 | 0.53828 | 0.57673 | 0.54959 | 0.57275 | 0.56624 | 0.51905 | 0.55366 | 0.57941 | 0.50698 | 0.48778 | 0.49983 | 0.51248 | 0.45076 | 0.46294 | 0.58393 | 0.49829 | 0.51905 | 0.48989 | 0.51335 | 0.53065
17 | Average iKW/TR |  |  | Hours 7: 0.53065 | 0.53065
18 | COP of chiller |  |  | 6.3397 | 6.3397 | 5.7954 | 7.1213 | 6.4513 | 6.532 | 6.0965 | 6.3976 | 6.1388 | 6.2094 | 6.7739 | 6.3505 | 6.0683 | 6.9352 | 7.2081 | 7.0344 | 6.8607 | 7.8002 | 7.595 | 6.0212 | 7.0561 | 6.7739 | 7.1771 | 6.8491 | 6.6636
19 | EER of Chiller |  |  | 21.6373 | 21.6373 | 19.7798 | 24.3049 | 22.0183 | 22.2936 | 20.8073 | 21.8349 | 20.9518 | 21.1927 | 23.1193 | 21.6743 | 20.711 | 23.6697 | 24.6013 | 24.0085 | 23.4157 | 26.6222 | 25.9216 | 20.5504 | 24.0826 | 23.1193 | 24.4954 | 23.3761 | 22.7427
20 | LMTD of Condenser | ºC |  | 1.8714 | 1.9704 | 1.5777 | 1.9704 | 2.1367 | 2.4943 | 2.0679 | 2.0679 | 2.0921 | 2.2891 | 2.3392 | 2.1401 | 2.1161 | 2.1161 | 1.834 | 1.8109 | 2.0193 | 1.9704 | 1.8963 | 1.7707 | 1.9458 | 2.3716 | 2.3142 | 2.5538 | 2.0724
21 | LMTD of Evaporator | ºC |  | 2.6572 | 2.9966 | 2.931 | 3.0533 | 3.0046 | 3.1998 | 3.1998 | 3.126 | 3.1742 | 3.3743 | 3.4236 | 3.4236 | 3.3247 | 3.3247 | 3.2499 | 3.1998 | 3.1494 | 3.0733 | 3.3309 | 3.334 | 4.055 | 5.3422 | 3.8822 | 3.7792 | 3.3587
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | [5 empty] | 0.64211
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | [5 empty] | 0.84737
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 12.7 | 12.7 | 13.2 | 13.4 | 13.4 | 13.4 | 13.6 | 13.9 | 14.2 | 14.3 | 14.4 | 14.3 | 14.2 | 14 | 13.7 | 13.3 | 13.1 | 12.8 | 12.3 | [5 empty] | 13.5211
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.7 | 5.6 | 5.7 | 5.7 | 5.8 | 5.6 | 5.7 | 5.8 | 5.9 | 5.9 | 6 | 5.8 | 5.7 | 5.4 | 5.3 | 5.3 | 5.3 | 5.4 | 5.3 | [5 empty] | 5.6263
| Evaporator Delta "T" |  |  | 7 | 7.1 | 7.5 | 7.7 | 7.6 | 7.8 | 7.9 | 8.1 | 8.3 | 8.4 | 8.4 | 8.5 | 8.5 | 8.6 | 8.4 | 8 | 7.8 | 7.4 | 7 | [5 empty] | 7.8947
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.5 | 24.7 | 25.4 | 25.2 | 25.7 | 25.8 | 26.3 | 26.4 | 26.2 | 26 | 26.2 | 25.6 | 25.3 | 24.7 | 24 | 22.9 | 21.9 | 21.6 | 21.3 | [5 empty] | 24.7211
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.9 | 29.2 | 30 | 30.2 | 30.6 | 30.8 | 31.3 | 31.6 | 31.6 | 31.5 | 31.6 | 31 | 30.8 | 30.1 | 29.3 | 28 | 26.7 | 26.2 | 25.9 | [5 empty] | 29.7526
| Condenser Delta "T" | ºC |  | 4.4 | 4.5 | 4.6 | 5 | 4.9 | 5 | 5 | 5.2 | 5.4 | 5.5 | 5.4 | 5.4 | 5.5 | 5.4 | 5.3 | 5.1 | 4.8 | 4.6 | 4.6 | [5 empty] | 5.0316
| Evaporator pressure (Kpag) | kpag |  | 246.8 | 246.1 | 246.8 | 246.8 | 247.5 | 244.8 | 246.8 | 246.8 | 247.5 | 248.2 | 248.2 | 246.8 | 244.8 | 242.7 | 242 | 241.3 | 242 | 244.1 | 243.4 | [5 empty] | 245.4421
| Condenser pressure (kpag) | kpag |  | 660.5 | 664.7 | 684.6 | 684.6 | 695 | 700.5 | 712.9 | 718.4 | 719.1 | 715.7 | 718.4 | 706.7 | 699.8 | 684 | 666 | 637.1 | 610.9 | 599.2 | 590.9 | [5 empty] | 677.3158
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | [5 empty] | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | [5 empty] | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [5 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [5 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2247.6852 | 2279.795 | 2408.2341 | 2472.4537 | 2440.3439 | 2504.5635 | 2536.6733 | 2600.8929 | 2665.1124 | 2697.2222 | 2697.2222 | 2729.332 | 2729.332 | 2761.4418 | 2697.2222 | 2568.7831 | 2504.5635 | 2376.1243 | 2247.6852 | [5 empty] | 48164.6825
15 | Power Consumption of Chiller | KWH |  | 1300 | 1400 | 1400 | 1500 | 1400 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1700 | 1600 | 1400 | 1400 | 1400 | 1100 | 600 | 0 | 0 | 0 | 0 | 0 | 27400
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.57837 | 0.61409 | 0.58134 | 0.60668 | 0.57369 | 0.63883 | 0.63075 | 0.61517 | 0.60035 | 0.5932 | 0.5932 | 0.58622 | 0.62286 | 0.57941 | 0.51905 | 0.54501 | 0.55898 | 0.46294 | 0.26694 | [5 empty] | 0.56669
17 | Average iKW/TR |  |  | Hours 7: 0.56669 | 0.56669
18 | COP of chiller |  |  | 6.0791 | 5.7255 | 6.0481 | 5.7954 | 6.1287 | 5.5038 | 5.5743 | 5.7155 | 5.8566 | 5.9271 | 5.9271 | 5.9977 | 5.6449 | 6.0683 | 6.7739 | 6.4513 | 6.29 | 7.595 | 13.1714 | [5 empty] | 6.4355
19 | EER of Chiller |  |  | 20.748 | 19.5413 | 20.6422 | 19.7798 | 20.9174 | 18.7844 | 19.0252 | 19.5069 | 19.9885 | 20.2293 | 20.2293 | 20.4702 | 19.266 | 20.711 | 23.1193 | 22.0183 | 21.4679 | 25.9216 | 44.9541 | [5 empty] | 21.9643
20 | LMTD of Condenser | ºC |  | 2.0752 | 2.1027 | 2.1301 | 2.2385 | 2.3564 | 2.2385 | 2.2385 | 2.4395 | 2.4943 | 2.5215 | 2.3452 | 2.4943 | 2.5215 | 2.4943 | 2.4669 | 2.2654 | 2.1846 | 2.1301 | 2.1301 | [5 empty] | 2.3088
21 | LMTD of Evaporator | ºC |  | 2.9192 | 3.1004 | 3.206 | 3.2583 | 3.2322 | 3.2843 | 3.4647 | 3.5178 | 3.5706 | 3.5969 | 3.5969 | 3.6231 | 3.6231 | 3.6492 | 3.5969 | 3.4913 | 3.2843 | 3.1797 | 3.0739 | [5 empty] | 3.3826
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!

## 29-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 29/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.6 | 0.4 | 0.5 | 0.6 | 0.4 | 0.6 | 0.4 | 0.3 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.5 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.4 | 0.4 | 0.42917
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 1.7 | 1.2 | 2.1 | 3.1 | 2.3 | 1.6 | 0.7 | 1.1 | 0.9 | 0.8 | 0.9 | 0.9 | 1 | 1.1 | 0.7 | 0.8 | 0.8 | 0.9 | 1.2 | 0.8 | 0.8 | 0.8 | 0.9 | 1.1625
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.7 | 14.1 | 13.2 | 13.1 | 12.9 | 12.9 | 13.2 | 13.5 | 14 | 14.2 | 14.1 | 14.4 | 14.2 | 13.9 | 14 | 14 | 13.9 | 13.9 | 13.7 | 13.7 | 13.8 | 13.7 | 13.7 | 13.7 | 13.7708
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.4 | 6.4 | 6.4 | 6.5 | 6.5 | 6.3 | 6.7 | 6.5 | 6.1 | 5.8 | 6.2 | 6.1 | 6.1 | 6.2 | 5.9 | 6.1 | 6.1 | 6.6 | 6.6 | 6.4 | 6.6 | 6.4 | 6.4 | 6.4 | 6.2792
| Evaporator Delta "T" |  |  | 9.3 | 7.7 | 6.8 | 6.6 | 6.4 | 6.6 | 6.5 | 7 | 7.9 | 8.4 | 7.9 | 8.3 | 8.1 | 7.7 | 8.1 | 7.9 | 7.8 | 7.3 | 7.1 | 7.3 | 7.2 | 7.3 | 7.3 | 7.3 | 7.4917
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.5 | 20.4 | 20.6 | 20.9 | 22.5 | 23.1 | 23.9 | 25.2 | 24.7 | 24.6 | 24.4 | 24.7 | 24 | 24.3 | 24.7 | 24.6 | 24.9 | 24.4 | 23.9 | 25.8 | 25.8 | 25.8 | 25.8 | 26 | 23.9792
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.3 | 25.6 | 25.5 | 25.4 | 26.9 | 27.4 | 28.5 | 30 | 30.1 | 30.2 | 29.8 | 30.1 | 29.5 | 29.8 | 29.9 | 30 | 30 | 29.1 | 28.7 | 30.8 | 30.6 | 30.8 | 30.6 | 30.8 | 29.0583
| Condenser Delta "T" | ºC |  | 6.8 | 5.2 | 4.9 | 4.5 | 4.4 | 4.3 | 4.6 | 4.8 | 5.4 | 5.6 | 5.4 | 5.4 | 5.5 | 5.5 | 5.2 | 5.4 | 5.1 | 4.7 | 4.8 | 5 | 4.8 | 5 | 4.8 | 4.8 | 5.0792
| Evaporator pressure (Kpag) | kpag |  | 242.7 | 248.9 | 242 | 248.9 | 239.9 | 248.2 | 249.6 | 253.7 | 251 | 248.9 | 253.7 | 252.3 | 252.3 | 254.4 | 251 | 251.7 | 253 | 255.8 | 254.4 | 254.4 | 257.2 | 255.1 | 254.4 | 256.5 | 251.25
| Condenser pressure (kpag) | kpag |  | 612.9 | 588.1 | 586.7 | 580.5 | 613.6 | 628.8 | 645.3 | 676.4 | 678.4 | 681.9 | 674.3 | 684 | 668.8 | 670.2 | 676.4 | 677.8 | 679.1 | 659.8 | 651.6 | 692.2 | 693.6 | 695 | 695 | 695 | 658.5583
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2986.2103 | 2472.4537 | 2183.4656 | 2119.246 | 2055.0265 | 2119.246 | 2087.1362 | 2247.6852 | 2536.6733 | 2697.2222 | 2536.6733 | 2665.1124 | 2600.8929 | 2472.4537 | 2600.8929 | 2536.6733 | 2504.5635 | 2344.0146 | 2279.795 | 2344.0146 | 2311.9048 | 2344.0146 | 2344.0146 | 2344.0146 | 57733.3995
15 | Power Consumption of Chiller | KWH |  | 1300 | 1200 | 1000 | 1000 | 1100 | 1100 | 1100 | 1400 | 1400 | 1300 | 1300 | 1500 | 1200 | 1300 | 1400 | 1300 | 1400 | 1100 | 1200 | 1400 | 1100 | 1400 | 1200 | 1200 | 29900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.43533 | 0.48535 | 0.45799 | 0.47187 | 0.53527 | 0.51905 | 0.52704 | 0.62286 | 0.5519 | 0.48198 | 0.51248 | 0.56283 | 0.46138 | 0.52579 | 0.53828 | 0.51248 | 0.55898 | 0.46928 | 0.52636 | 0.59727 | 0.4758 | 0.59727 | 0.51194 | 0.51194 | 0.51878
17 | Average iKW/TR |  |  | Hours 7: 0.51878 | 0.51878
18 | COP of chiller |  |  | 8.0766 | 7.2443 | 7.6771 | 7.4513 | 6.5686 | 6.7739 | 6.6712 | 5.6449 | 6.3707 | 7.2949 | 6.8607 | 6.247 | 7.6206 | 6.687 | 6.532 | 6.8607 | 6.29 | 7.4923 | 6.6798 | 5.8868 | 7.3897 | 5.8868 | 6.868 | 6.868 | 6.831
19 | EER of Chiller |  |  | 27.5653 | 24.7248 | 26.2018 | 25.4312 | 22.4187 | 23.1193 | 22.769 | 19.266 | 21.7431 | 24.8977 | 23.4157 | 21.3211 | 26.0092 | 22.8229 | 22.2936 | 23.4157 | 21.4679 | 25.5713 | 22.7982 | 20.0917 | 25.221 | 20.0917 | 23.4404 | 23.4404 | 23.3141
20 | LMTD of Condenser | ºC |  | 2.7067 | 1.9704 | 2.0592 | 2.1027 | 1.7707 | 2.0476 | 1.8213 | 1.6942 | 2.1879 | 2.2387 | 2.1879 | 2.0193 | 2.0437 | 2.0437 | 1.7877 | 1.834 | 2.111 | 1.8464 | 1.8714 | 1.7411 | 2.0332 | 1.7411 | 1.8714 | 1.8714 | 1.9834
21 | LMTD of Evaporator | ºC |  | 3.6677 | 4.5027 | 3.5844 | 4.6434 | 5.7148 | 4.8775 | 4.0077 | 2.9192 | 3.7585 | 3.5969 | 3.3103 | 3.5706 | 3.5178 | 3.5593 | 3.8138 | 3.1494 | 3.2843 | 3.1533 | 3.2497 | 3.7288 | 3.1269 | 3.1533 | 3.1533 | 3.3039 | 3.6812
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  | 2.6 | 1.3 | 1.3 | 1.3 | 1.2 | 1.1 | 1.2 | 1.2 | 1.4 | 1.2 | 1.4 | 1.3 | 1.3 | 1.2 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.1 | 1.1 | 1.2 | 1.2 | 1.3
2 | Small temperature difference of evaporator | ºC |  |  | 1.4 | 0.9 | 0.8 | 0.9 | 0.7 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.5 | 0.6 | 0.6 | 0.4 | 0.6 | 0.7 | 0.5 | 0.6 | 0.4 | 0.6 | 0.67826
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  | 14.3 | 13.2 | 13.2 | 12.8 | 13 | 13.1 | 13.5 | 14.1 | 14.2 | 14.2 | 14.3 | 14.3 | 14 | 14.1 | 14.1 | 14 | 13.9 | 13.7 | 13.8 | 13.9 | 13.8 | 13.8 | 13.8 | 13.787
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  | 6.4 | 6.6 | 6.6 | 6.6 | 6.7 | 6.6 | 6.7 | 6.7 | 6.4 | 6.3 | 6.6 | 6.3 | 6.1 | 6.1 | 6.1 | 6 | 6.3 | 6.6 | 6.6 | 6.6 | 6.6 | 6.7 | 6.7 | 6.4739
| Evaporator Delta "T" |  |  |  | 7.9 | 6.6 | 6.6 | 6.2 | 6.3 | 6.5 | 6.8 | 7.4 | 7.8 | 7.9 | 7.7 | 8 | 7.9 | 8 | 8 | 8 | 7.6 | 7.1 | 7.2 | 7.3 | 7.2 | 7.1 | 7.1 | 7.313
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  | 20.8 | 21.3 | 21.2 | 22.9 | 23.6 | 24.4 | 25.7 | 25.2 | 25 | 24.9 | 25.2 | 24.6 | 24.9 | 25.1 | 25.1 | 25.2 | 24.8 | 24.3 | 26.1 | 26.2 | 26.3 | 26.2 | 26.3 | 24.5783
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  | 25.5 | 25.3 | 25.2 | 26.6 | 27.3 | 28.3 | 29.7 | 29.6 | 29.7 | 29.6 | 29.9 | 29.3 | 29.6 | 29.7 | 29.8 | 29.9 | 29.3 | 28.5 | 30.4 | 30.4 | 30.6 | 30.4 | 30.5 | 28.9174
| Condenser Delta "T" | ºC |  |  | 4.7 | 4 | 4 | 3.7 | 3.7 | 3.9 | 4 | 4.4 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.6 | 4.7 | 4.7 | 4.5 | 4.2 | 4.3 | 4.2 | 4.3 | 4.2 | 4.2 | 4.3391
| Evaporator pressure (Kpag) | kpag |  |  | 253.7 | 255.8 | 257.9 | 259.2 | 261.3 | 260.6 | 262.7 | 261.3 | 259.2 | 257.9 | 259.2 | 255.8 | 255.8 | 255.8 | 255.1 | 255.1 | 257.2 | 259.2 | 261.3 | 262 | 262 | 262.7 | 262.7 | 258.8478
| Condenser pressure (kpag) | kpag |  |  | 604.7 | 597.1 | 592.3 | 621.9 | 635 | 655 | 688.1 | 689.5 | 689.5 | 687.4 | 695.7 | 680.5 | 687.4 | 691.5 | 693.6 | 695.7 | 678.4 | 665.3 | 704.6 | 706.7 | 706.7 | 704.6 | 706 | 672.9217
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  | 2536.6733 | 2119.246 | 2119.246 | 1990.8069 | 2022.9167 | 2087.1362 | 2183.4656 | 2376.1243 | 2504.5635 | 2536.6733 | 2472.4537 | 2568.7831 | 2536.6733 | 2568.7831 | 2568.7831 | 2568.7831 | 2440.3439 | 2279.795 | 2311.9048 | 2344.0146 | 2311.9048 | 2279.795 | 2279.795 | 54008.664
15 | Power Consumption of Chiller | KWH |  | 1200 | 1200 | 1100 | 1100 | 1100 | 1200 | 1200 | 1500 | 1300 | 1400 | 1500 | 1400 | 1500 | 1300 | 1400 | 1400 | 1500 | 1300 | 1200 | 1500 | 1400 | 1200 | 1500 | 1300 | 31700
16 | Specific power consumption of Chiller | (iKW/TR) |  |  | 0.47306 | 0.51905 | 0.51905 | 0.55254 | 0.5932 | 0.57495 | 0.68698 | 0.54711 | 0.55898 | 0.59133 | 0.56624 | 0.58393 | 0.51248 | 0.54501 | 0.54501 | 0.58393 | 0.53271 | 0.52636 | 0.64882 | 0.59727 | 0.51905 | 0.65795 | 0.57023 | 0.56545
17 | Average iKW/TR |  |  | Hours 7: 0.56545 | 0.56545
18 | COP of chiller |  |  |  | 7.4325 | 6.7739 | 6.7739 | 6.3633 | 5.9271 | 6.1153 | 5.118 | 6.4265 | 6.29 | 5.946 | 6.2094 | 6.0212 | 6.8607 | 6.4513 | 6.4513 | 6.0212 | 6.6002 | 6.6798 | 5.4191 | 5.8868 | 6.7739 | 5.3438 | 6.166 | 6.2631
19 | EER of Chiller |  |  |  | 25.367 | 23.1193 | 23.1193 | 21.7181 | 20.2293 | 20.8716 | 17.4679 | 21.9337 | 21.4679 | 20.2936 | 21.1927 | 20.5504 | 23.4157 | 22.0183 | 22.0183 | 20.5504 | 22.5265 | 22.7982 | 18.4954 | 20.0917 | 23.1193 | 18.2385 | 21.0445 | 21.376
20 | LMTD of Condenser | ºC |  |  | 4.5527 | 2.8463 | 2.8463 | 2.7467 | 2.6299 | 2.5757 | 2.7279 | 2.8563 | 3.1933 | 2.9511 | 3.1933 | 3.0731 | 3.0731 | 2.9196 | 3.0731 | 3.0731 | 3.009 | 2.7924 | 2.8244 | 2.6711 | 2.7026 | 2.7924 | 2.7924 | 2.9529
21 | LMTD of Evaporator | ºC |  |  | 4.1721 | 3.1128 | 2.9668 | 3.0018 | 2.7361 | 2.6306 | 2.7067 | 2.8568 | 3.1241 | 3.1494 | 3.0987 | 3.1746 | 3.3103 | 2.8236 | 3.0046 | 3.0046 | 2.5369 | 2.7821 | 2.9709 | 2.6572 | 2.8071 | 2.4222 | 2.7821 | 2.9492
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!

## 30-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 30/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 | 0.7 | 0.6 | 0.4 | 0.4 | 0.5 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.5
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.9 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.6 | 0.6 | 0.4 | 0.6 | 0.7 | 1 | 0.7375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.8 | 13.9 | 14.3 | 14 | 14 | 13.9 | 14.1 | 14.3 | 14.4 | 14.4 | 14.1 | 14.1 | 13.8 | 13.4 | 13.4 | 13.2 | 13.3 | 13.7 | 13.7 | 13.7 | 13.6 | 13.4 | 13 | 12.9 | 13.7667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.1 | 5.6 | 5.4 | 5.4 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.5 | 5.5 | 5.5 | 6.4 | 6.4 | 6.4 | 6.1 | 5.6 | 5.5 | 5.5 | 5.6 | 5.5 | 5.4 | 5.4 | 5.7125
| Evaporator Delta "T" |  |  | 7.5 | 7.8 | 8.7 | 8.6 | 8.6 | 8.3 | 8.5 | 8.7 | 8.8 | 8.8 | 8.6 | 8.6 | 8.3 | 7 | 7 | 6.8 | 7.2 | 8.1 | 8.2 | 8.2 | 8 | 7.9 | 7.6 | 7.5 | 8.0542
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26 | 25.9 | 25.2 | 24.9 | 25.4 | 26.6 | 26.3 | 25.9 | 25.1 | 25.2 | 24.2 | 23.7 | 22.8 | 22.3 | 22.5 | 24.5 | 25.9 | 26.8 | 26.9 | 26.6 | 26.4 | 25.6 | 25.6 | 25.6 | 25.2458
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.8 | 31.2 | 31 | 30.5 | 30.8 | 31.8 | 32.1 | 32.1 | 31.3 | 31.1 | 30.2 | 29.2 | 28.2 | 27.3 | 27.3 | 29.1 | 30.8 | 32.2 | 32.6 | 31.9 | 31.7 | 31.1 | 30.7 | 30.6 | 30.65
| Condenser Delta "T" | ºC |  | 4.8 | 5.3 | 5.8 | 5.6 | 5.4 | 5.2 | 5.8 | 6.2 | 6.2 | 5.9 | 6 | 5.5 | 5.4 | 5 | 4.8 | 4.6 | 4.9 | 5.4 | 5.7 | 5.3 | 5.3 | 5.5 | 5.1 | 5 | 5.4042
| Evaporator pressure (Kpag) | kpag |  | 255.8 | 246.8 | 244.8 | 245.5 | 244.1 | 246.1 | 246.8 | 245.5 | 244.8 | 244.1 | 243.4 | 244.1 | 245.5 | 239.2 | 244.1 | 257.2 | 250.3 | 246.1 | 246.8 | 247.5 | 246.8 | 246.1 | 244.1 | 242 | 246.1458
| Condenser pressure (kpag) | kpag |  | 698.4 | 708.8 | 701.9 | 692.2 | 702.6 | 727.4 | 723.3 | 721.9 | 703.3 | 706.7 | 683.3 | 662.6 | 639.1 | 614.3 | 619.8 | 658.4 | 697.1 | 729.5 | 735.7 | 723.3 | 720.5 | 701.9 | 694.3 | 690.9 | 694.05
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2504.5635 | 2793.5516 | 2761.4418 | 2761.4418 | 2665.1124 | 2729.332 | 2793.5516 | 2825.6614 | 2825.6614 | 2761.4418 | 2761.4418 | 2665.1124 | 2247.6852 | 2247.6852 | 2183.4656 | 2311.9048 | 2600.8929 | 2633.0026 | 2633.0026 | 2568.7831 | 2536.6733 | 2440.3439 | 2408.2341 | 62068.2209
15 | Power Consumption of Chiller | KWH |  | 1300 | 1500 | 1600 | 1300 | 1600 | 1500 | 1600 | 1400 | 1500 | 1600 | 1400 | 1400 | 1300 | 1200 | 1100 | 1100 | 1400 | 1500 | 1500 | 1400 | 1300 | 1400 | 1200 | 1400 | 33500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53981 | 0.59891 | 0.57275 | 0.47077 | 0.57941 | 0.56283 | 0.58622 | 0.50115 | 0.53085 | 0.56624 | 0.50698 | 0.50698 | 0.48778 | 0.53388 | 0.48939 | 0.50379 | 0.60556 | 0.57673 | 0.56969 | 0.53171 | 0.50608 | 0.5519 | 0.49173 | 0.58134 | 0.53969
17 | Average iKW/TR |  |  | Hours 7: 0.53969 | 0.53969
18 | COP of chiller |  |  | 6.5133 | 5.8707 | 6.1388 | 7.4686 | 6.0683 | 6.247 | 5.9977 | 7.0158 | 6.6234 | 6.2094 | 6.9352 | 6.9352 | 7.2081 | 6.5857 | 7.1844 | 6.9792 | 5.8062 | 6.0965 | 6.1718 | 6.6126 | 6.9476 | 6.3707 | 7.1502 | 6.0481 | 6.5493
19 | EER of Chiller |  |  | 22.2301 | 20.0367 | 20.9518 | 25.4905 | 20.711 | 21.3211 | 20.4702 | 23.9449 | 22.6055 | 21.1927 | 23.6697 | 23.6697 | 24.6013 | 22.4771 | 24.5204 | 23.8198 | 19.8165 | 20.8073 | 21.0642 | 22.5688 | 23.7121 | 21.7431 | 24.4037 | 20.6422 | 22.3529
20 | LMTD of Condenser | ºC |  | 1.8714 | 2.1624 | 2.2891 | 2.2387 | 2.1879 | 2.2921 | 2.4502 | 2.7096 | 2.5538 | 2.1401 | 2.164 | 2.2134 | 1.834 | 1.9211 | 1.8714 | 1.8213 | 1.8963 | 2.1879 | 2.4241 | 2.3187 | 2.3187 | 2.3716 | 2.2654 | 1.9211 | 2.1843
21 | LMTD of Evaporator | ºC |  | 3.206 | 3.2843 | 3.3495 | 3.3247 | 3.3247 | 3.2499 | 3.2998 | 3.3495 | 3.3743 | 3.3743 | 3.6492 | 3.4905 | 3.4136 | 3.2225 | 3.2225 | 3.1678 | 3.2769 | 2.8472 | 3.0533 | 3.0533 | 2.6277 | 2.9801 | 3.0733 | 3.5046 | 3.2383
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.1 | 1.2 | 1.2 | 1.3 | 1.2 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 1.3 | 1.2 | 1.3 | 1.2 | 1.2 | 1.2208
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.55833
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.8 | 14 | 14.3 | 14.1 | 13.9 | 14 | 14.1 | 14.3 | 14.4 | 14.6 | 14.3 | 14.1 | 13.9 | 13.4 | 13.3 | 13.2 | 13.4 | 13.7 | 13.7 | 13.7 | 13.7 | 13.4 | 13.1 | 13.1 | 13.8125
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.7 | 6.2 | 6.1 | 6 | 6 | 6.1 | 6.1 | 6.2 | 6.3 | 6.2 | 6.1 | 5.8 | 5.5 | 6.5 | 6.6 | 6.6 | 6.1 | 6.1 | 6.1 | 5.9 | 5.9 | 5.7 | 5.5 | 5.5 | 6.075
| Evaporator Delta "T" |  |  | 7.1 | 7.8 | 8.2 | 8.1 | 7.9 | 7.9 | 8 | 8.1 | 8.1 | 8.4 | 8.2 | 8.3 | 8.4 | 6.9 | 6.7 | 6.6 | 7.3 | 7.6 | 7.6 | 7.8 | 7.8 | 7.7 | 7.6 | 7.6 | 7.7375
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26.3 | 26.3 | 25.6 | 25.4 | 25.8 | 26.8 | 26.7 | 26.4 | 25.6 | 25.6 | 24.6 | 23.9 | 23.1 | 22.7 | 22.9 | 24.9 | 26.2 | 27.2 | 27.4 | 27 | 26.9 | 26.1 | 26.1 | 25.8 | 25.6375
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.5 | 30.9 | 30.4 | 30.2 | 30.6 | 31.6 | 31.5 | 31.3 | 30.5 | 30.6 | 29.6 | 28.9 | 28.2 | 26.8 | 27.1 | 28.9 | 30.6 | 31.8 | 31.9 | 31.6 | 31.5 | 30.8 | 30.6 | 30.3 | 30.2792
| Condenser Delta "T" | ºC |  | 4.2 | 4.6 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.9 | 4.9 | 5 | 5 | 5 | 5.1 | 4.1 | 4.2 | 4 | 4.4 | 4.6 | 4.5 | 4.6 | 4.6 | 4.7 | 4.5 | 4.5 | 4.6417
| Evaporator pressure (Kpag) | kpag |  | 262.7 | 257.2 | 256.5 | 253.7 | 253 | 255.8 | 255.1 | 255.8 | 257.2 | 255.8 | 254.4 | 251 | 246.1 | 255.8 | 257.9 | 260.6 | 256.5 | 254.4 | 255.8 | 254.4 | 253 | 251 | 249.6 | 248.2 | 254.6458
| Condenser pressure (kpag) | kpag |  | 706.7 | 717.7 | 708.1 | 699.8 | 710.8 | 731.5 | 730.8 | 726 | 706.7 | 710.8 | 688.1 | 674.3 | 653.6 | 626.7 | 629.5 | 668.8 | 705.3 | 736.4 | 741.2 | 730.8 | 729.5 | 710.8 | 708.1 | 703.3 | 702.3042
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2279.795 | 2504.5635 | 2633.0026 | 2600.8929 | 2536.6733 | 2536.6733 | 2568.7831 | 2600.8929 | 2600.8929 | 2697.2222 | 2633.0026 | 2665.1124 | 2697.2222 | 2215.5754 | 2151.3558 | 2119.246 | 2344.0146 | 2440.3439 | 2440.3439 | 2504.5635 | 2504.5635 | 2472.4537 | 2440.3439 | 2440.3439 | 59627.877
15 | Power Consumption of Chiller | KWH |  | 1400 | 1500 | 1400 | 1500 | 1500 | 1500 | 1500 | 1400 | 1500 | 1600 | 1500 | 1400 | 1300 | 1200 | 1300 | 1200 | 1400 | 1500 | 1500 | 1400 | 1500 | 1400 | 1500 | 1400 | 34300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.61409 | 0.59891 | 0.53171 | 0.57673 | 0.59133 | 0.59133 | 0.58393 | 0.53828 | 0.57673 | 0.5932 | 0.56969 | 0.52531 | 0.48198 | 0.54162 | 0.60427 | 0.56624 | 0.59727 | 0.61467 | 0.61467 | 0.55898 | 0.59891 | 0.56624 | 0.61467 | 0.57369 | 0.57602
17 | Average iKW/TR |  |  | Hours 7: 0.57602 | 0.57602
18 | COP of chiller |  |  | 5.7255 | 5.8707 | 6.6126 | 6.0965 | 5.946 | 5.946 | 6.0212 | 6.532 | 6.0965 | 5.9271 | 6.1718 | 6.6932 | 7.2949 | 6.4916 | 5.8186 | 6.2094 | 5.8868 | 5.7202 | 5.7202 | 6.29 | 5.8707 | 6.2094 | 5.7202 | 6.1287 | 6.125
19 | EER of Chiller |  |  | 19.5413 | 20.0367 | 22.5688 | 20.8073 | 20.2936 | 20.2936 | 20.5504 | 22.2936 | 20.8073 | 20.2293 | 21.0642 | 22.844 | 24.8977 | 22.156 | 19.8588 | 21.1927 | 20.0917 | 19.5229 | 19.5229 | 21.4679 | 20.0367 | 21.1927 | 19.5229 | 20.9174 | 20.9046
20 | LMTD of Condenser | ºC |  | 2.6711 | 2.9196 | 2.9824 | 3.1049 | 2.9824 | 3.1049 | 2.9824 | 3.0136 | 3.0136 | 3.0446 | 3.0446 | 3.0446 | 3.1996 | 2.7602 | 2.7924 | 2.7279 | 2.8563 | 2.9196 | 3.009 | 3.0411 | 2.9196 | 3.0731 | 2.8881 | 2.8881 | 2.9577
21 | LMTD of Evaporator | ºC |  | 2.7821 | 2.9556 | 3.0533 | 3.029 | 2.9801 | 2.8 | 2.6277 | 3.029 | 3.029 | 3.1019 | 3.0533 | 3.0776 | 3.1019 | 2.8933 | 2.8412 | 2.815 | 2.9966 | 2.5369 | 2.7289 | 2.5824 | 2.5824 | 2.7527 | 2.7289 | 2.5369 | 2.859
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!

## 31-03-2025
Performance Sheet for Chiller No. 1 to 6
Date :- 31/03/2025
Chiller No. 1
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.6 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.5 | 0.4 | 0.4 | 0.49167
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.7 | 0.6 | 0.6 | 0.8 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.72083
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.4 | 14 | 14.2 | 14.2 | 14.6 | 14.7 | 14.8 | 15.2 | 15.3 | 15.2 | 14.5 | 12.8 | 13.4 | 13.7 | 13.8 | 13.3 | 13.4 | 13.2 | 13.3 | 13.2 | 13.3 | 13.3 | 13.3 | 13.8833
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.4 | 5.5 | 5.6 | 5.6 | 5.6 | 5.7 | 5.9 | 5.9 | 6.2 | 6.2 | 6 | 5.6 | 5.6 | 5.7 | 5.6 | 5.6 | 5.6 | 5.4 | 5.4 | 5.7 | 5.6 | 5.6 | 5.4 | 5.6 | 5.6667
| Evaporator Delta "T" |  |  | 7.7 | 7.9 | 8.4 | 8.6 | 8.6 | 8.9 | 8.8 | 8.9 | 9 | 9.1 | 9.2 | 8.9 | 7.2 | 7.7 | 8.1 | 8.2 | 7.7 | 8 | 7.8 | 7.6 | 7.6 | 7.7 | 7.9 | 7.7 | 8.2167
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 26 | 26.4 | 26.4 | 26.4 | 27 | 27.3 | 27.4 | 27.2 | 27.5 | 26.7 | 26 | 26.4 | 25.7 | 24.2 | 25.2 | 25.7 | 26.4 | 26.1 | 25.6 | 25.8 | 26 | 25.9 | 25.7 | 25.9 | 26.2042
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.1 | 31.6 | 31.9 | 32.1 | 32.9 | 33.1 | 33.2 | 33.4 | 33.3 | 32.6 | 32 | 32.6 | 30.7 | 29.2 | 30.7 | 31.3 | 31.6 | 31.4 | 30.9 | 31 | 31.3 | 31.2 | 30.8 | 31 | 31.7042
| Condenser Delta "T" | ºC |  | 5.1 | 5.2 | 5.5 | 5.7 | 5.9 | 5.8 | 5.8 | 6.2 | 5.8 | 5.9 | 6 | 6.2 | 5 | 5 | 5.5 | 5.6 | 5.2 | 5.3 | 5.3 | 5.2 | 5.3 | 5.3 | 5.1 | 5.1 | 5.5
| Evaporator pressure (Kpag) | kpag |  | 246.1 | 245.5 | 246.1 | 246.8 | 248.2 | 249.6 | 251 | 251.7 | 254.4 | 252.3 | 248.9 | 246.8 | 239.9 | 242 | 246.1 | 244.8 | 247.5 | 245.5 | 245.5 | 248.2 | 246.1 | 246.1 | 244.8 | 245.5 | 247.0583
| Condenser pressure (kpag) | kpag |  | 704.6 | 716.4 | 723.3 | 728.1 | 743.9 | 754.3 | 755.7 | 758.4 | 759.1 | 745.3 | 729.5 | 738.4 | 693.6 | 663.3 | 694.3 | 709.5 | 715.7 | 712.2 | 699.1 | 699.8 | 707.4 | 704.6 | 699.1 | 699.8 | 718.975
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2472.4537 | 2536.6733 | 2697.2222 | 2761.4418 | 2761.4418 | 2857.7712 | 2825.6614 | 2857.7712 | 2889.881 | 2921.9907 | 2954.1005 | 2857.7712 | 2311.9048 | 2472.4537 | 2600.8929 | 2633.0026 | 2472.4537 | 2568.7831 | 2504.5635 | 2440.3439 | 2440.3439 | 2472.4537 | 2536.6733 | 2472.4537 | 63320.5026
15 | Power Consumption of Chiller | KWH |  | 1300 | 1400 | 1500 | 1600 | 1500 | 1600 | 1700 | 1600 | 1600 | 1500 | 1800 | 1400 | 1200 | 1400 | 1400 | 1400 | 1400 | 1400 | 1300 | 1300 | 1400 | 1400 | 1300 | 1300 | 34700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.52579 | 0.5519 | 0.55613 | 0.57941 | 0.54319 | 0.55988 | 0.60163 | 0.55988 | 0.55366 | 0.51335 | 0.60932 | 0.48989 | 0.51905 | 0.56624 | 0.53828 | 0.53171 | 0.56624 | 0.54501 | 0.51905 | 0.53271 | 0.57369 | 0.56624 | 0.51248 | 0.52579 | 0.54752
17 | Average iKW/TR |  |  | Hours 7: 0.54752 | 0.54752
18 | COP of chiller |  |  | 6.687 | 6.3707 | 6.3223 | 6.0683 | 6.4728 | 6.28 | 5.8441 | 6.28 | 6.3505 | 6.8491 | 5.7703 | 7.1771 | 6.7739 | 6.2094 | 6.532 | 6.6126 | 6.2094 | 6.4513 | 6.7739 | 6.6002 | 6.1287 | 6.2094 | 6.8607 | 6.687 | 6.4384
19 | EER of Chiller |  |  | 22.8229 | 21.7431 | 21.578 | 20.711 | 22.0917 | 21.4335 | 19.946 | 21.4335 | 21.6743 | 23.3761 | 19.6942 | 24.4954 | 23.1193 | 21.1927 | 22.2936 | 22.5688 | 21.1927 | 22.0183 | 23.1193 | 22.5265 | 20.9174 | 21.1927 | 23.4157 | 22.8229 | 21.9741
20 | LMTD of Condenser | ºC |  | 2.111 | 2.1367 | 2.2134 | 2.264 | 2.7761 | 2.6027 | 2.4502 | 2.5538 | 2.4502 | 2.4763 | 2.164 | 2.5538 | 1.9211 | 1.9211 | 2.0437 | 2.2387 | 1.9704 | 1.9949 | 1.9949 | 1.7877 | 1.9949 | 2.1624 | 1.9458 | 1.9458 | 2.1947
21 | LMTD of Evaporator | ºC |  | 3.0987 | 3.1494 | 3.1019 | 3.3247 | 3.3247 | 3.399 | 3.3743 | 3.399 | 3.4236 | 3.7792 | 3.805 | 3.7274 | 3.1269 | 3.2583 | 3.3621 | 3.2249 | 2.931 | 3.0046 | 3.2843 | 3.0733 | 2.9064 | 2.931 | 3.1494 | 3.0987 | 3.2607
Chiller No. 2
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 3
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 19: 0.6; Hours 20: 0.6; Hours 21: 0.6; Hours 22: 0.6; Hours 23: 0.7; Hours 0: 0.4; Hours 1: 0.5; Hours 2: 0.6; Hours 3: 0.5; Hours 4: 0.5; Hours 5: 0.5; Hours 6: 0.5 | 0.55
2 | Small temperature difference of evaporator | ºC |  | Hours 19: 0.5; Hours 20: 0.6; Hours 21: 0.6; Hours 22: 0.6; Hours 23: 0.5; Hours 0: 0.6; Hours 1: 0.5; Hours 2: 0.6; Hours 3: 0.7; Hours 4: 0.6; Hours 5: 0.5; Hours 6: 0.6 | 0.575
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 19: 12.8; Hours 20: 13.2; Hours 21: 13.6; Hours 22: 13.7; Hours 23: 13.3; Hours 0: 13.3; Hours 1: 13.3; Hours 2: 13.2; Hours 3: 13.2; Hours 4: 13.2; Hours 5: 13.2; Hours 6: 13.2 | 13.2667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 19: 5.4; Hours 20: 5.5; Hours 21: 5.5; Hours 22: 5.5; Hours 23: 5.5; Hours 0: 5.5; Hours 1: 5.5; Hours 2: 5.6; Hours 3: 5.5; Hours 4: 5.5; Hours 5: 5.5; Hours 6: 5.5 | 5.5
| Evaporator Delta "T" |  |  | Hours 19: 7.4; Hours 20: 7.7; Hours 21: 8.1; Hours 22: 8.2; Hours 23: 7.8; Hours 0: 7.8; Hours 1: 7.8; Hours 2: 7.6; Hours 3: 7.7; Hours 4: 7.7; Hours 5: 7.7; Hours 6: 7.7 | 7.7667
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 19: 26.3; Hours 20: 24.6; Hours 21: 25.7; Hours 22: 26.2; Hours 23: 26.8; Hours 0: 26.7; Hours 1: 26; Hours 2: 26.2; Hours 3: 26.4; Hours 4: 26.3; Hours 5: 25.9; Hours 6: 26.2 | 26.1083
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 19: 30.4; Hours 20: 28.8; Hours 21: 30.2; Hours 22: 30.7; Hours 23: 31.3; Hours 0: 31; Hours 1: 30.4; Hours 2: 30.3; Hours 3: 30.8; Hours 4: 30.7; Hours 5: 30.4; Hours 6: 30.4 | 30.45
| Condenser Delta "T" | ºC |  | Hours 19: 4.1; Hours 20: 4.2; Hours 21: 4.5; Hours 22: 4.5; Hours 23: 4.5; Hours 0: 4.3; Hours 1: 4.4; Hours 2: 4.1; Hours 3: 4.4; Hours 4: 4.4; Hours 5: 4.5; Hours 6: 4.2 | 4.3417
| Evaporator pressure (Kpag) | kpag |  | Hours 19: 246.8; Hours 20: 246.8; Hours 21: 248.2; Hours 22: 247.5; Hours 23: 246.8; Hours 0: 248.2; Hours 1: 246.8; Hours 2: 249.6; Hours 3: 246.8; Hours 4: 247.5; Hours 5: 246.8; Hours 6: 247.5 | 247.4417
| Condenser pressure (kpag) | kpag |  | Hours 19: 686; Hours 20: 657.1; Hours 21: 687.4; Hours 22: 699.8; Hours 23: 709.5; Hours 0: 703.3; Hours 1: 690.9; Hours 2: 692.2; Hours 3: 701.9; Hours 4: 696.4; Hours 5: 690.9; Hours 6: 693.6 | 692.4167
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 19: 4.2; Hours 20: 4.2; Hours 21: 4.2; Hours 22: 4.2; Hours 23: 4.2; Hours 0: 4.2; Hours 1: 4.2; Hours 2: 4.2; Hours 3: 4.2; Hours 4: 4.2; Hours 5: 4.2; Hours 6: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 19: 3.7; Hours 20: 3.7; Hours 21: 3.7; Hours 22: 3.7; Hours 23: 3.7; Hours 0: 3.7; Hours 1: 3.7; Hours 2: 3.7; Hours 3: 3.7; Hours 4: 3.7; Hours 5: 3.7; Hours 6: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8; Hours 5: 3.8; Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3; Hours 3: 3; Hours 4: 3; Hours 5: 3; Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5; Hours 3: 0.5; Hours 4: 0.5; Hours 5: 0.5; Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8; Hours 3: 0.8; Hours 4: 0.8; Hours 5: 0.8; Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971; Hours 3: 971; Hours 4: 971; Hours 5: 971; Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 19: 2376.1243; Hours 20: 2472.4537; Hours 21: 2600.8929; Hours 22: 2633.0026; Hours 23: 2504.5635; Hours 0: 2504.5635; Hours 1: 2504.5635; Hours 2: 2440.3439; Hours 3: 2472.4537; Hours 4: 2472.4537; Hours 5: 2472.4537; Hours 6: 2472.4537 | 29926.3228
15 | Power Consumption of Chiller | KWH |  | Hours 17: 800; Hours 18: 1500; Hours 19: 1400; Hours 20: 1400; Hours 21: 1600; Hours 22: 1500; Hours 23: 1500; Hours 0: 1400; Hours 1: 1500; Hours 2: 1300; Hours 3: 1500; Hours 4: 1500; Hours 5: 1300; Hours 6: 1500 | 19700
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 19: 0.58919; Hours 20: 0.56624; Hours 21: 0.61517; Hours 22: 0.56969; Hours 23: 0.59891; Hours 0: 0.55898; Hours 1: 0.59891; Hours 2: 0.53271; Hours 3: 0.60668; Hours 4: 0.60668; Hours 5: 0.52579; Hours 6: 0.60668 | 0.5813
17 | Average iKW/TR |  |  | Hours 7: 0.5813 | 0.5813
18 | COP of chiller |  |  | Hours 19: 5.9675; Hours 20: 6.2094; Hours 21: 5.7155; Hours 22: 6.1718; Hours 23: 5.8707; Hours 0: 6.29; Hours 1: 5.8707; Hours 2: 6.6002; Hours 3: 5.7954; Hours 4: 5.7954; Hours 5: 6.687; Hours 6: 5.7954 | 6.0641
19 | EER of Chiller |  |  | Hours 19: 20.367; Hours 20: 21.1927; Hours 21: 19.5069; Hours 22: 21.0642; Hours 23: 20.0367; Hours 0: 21.4679; Hours 1: 20.0367; Hours 2: 22.5265; Hours 3: 19.7798; Hours 4: 19.7798; Hours 5: 22.8229; Hours 6: 19.7798 | 20.6967
20 | LMTD of Condenser | ºC |  | Hours 19: 1.9918; Hours 20: 2.0198; Hours 21: 2.1027; Hours 22: 2.1027; Hours 23: 2.244; Hours 0: 1.7452; Hours 1: 1.9278; Hours 2: 1.9918; Hours 3: 1.9278; Hours 4: 1.9278; Hours 5: 1.9543; Hours 6: 1.8744 | 1.9842
21 | LMTD of Evaporator | ºC |  | Hours 19: 2.6811; Hours 20: 2.931; Hours 21: 3.029; Hours 22: 3.0533; Hours 23: 2.7764; Hours 0: 2.9556; Hours 1: 2.7764; Hours 2: 2.9064; Hours 3: 3.0987; Hours 4: 2.931; Hours 5: 2.7527; Hours 6: 2.931 | 2.9019
Chiller No. 4
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.1; Hours 8: 1.2 | 1.15
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.4; Hours 8: 0.5 | 0.45
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 13.2; Hours 8: 13.4 | 13.3
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 5.6; Hours 8: 5.6 | 5.6
| Evaporator Delta "T" |  |  | Hours 7: 7.6; Hours 8: 7.8 | 7.7
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 26.5; Hours 8: 26.9 | 26.7
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 31; Hours 8: 31 | 31
| Condenser Delta "T" | ºC |  | Hours 7: 4.5; Hours 8: 4.1 | 4.3
| Evaporator pressure (Kpag) | kpag |  | Hours 7: 249.6; Hours 8: 249.6 | 249.6
| Condenser pressure (kpag) | kpag |  | Hours 7: 717.1; Hours 8: 717.1 | 717.1
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.2; Hours 8: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.7; Hours 8: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2440.3439; Hours 8: 2504.5635 | 4944.9074
15 | Power Consumption of Chiller | KWH |  | Hours 7: 900; Hours 8: 200 | 1100
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.3688; Hours 8: 0.079854 | 0.22433
17 | Average iKW/TR |  |  | Hours 7: 0.22433 | 0.22433
18 | COP of chiller |  |  | Hours 7: 9.5336; Hours 8: 44.0302 | 26.7819
19 | EER of Chiller |  |  | Hours 7: 32.5382; Hours 8: 150.2752 | 91.4067
20 | LMTD of Condenser | ºC |  | Hours 7: 2.7651; Hours 8: 2.7602 | 2.7626
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.5369; Hours 8: 2.7764 | 2.6567
Chiller No. 5
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
| Evaporator Delta "T" | [26 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
| Condenser Delta "T" | ºC | [25 empty] | #DIV/0!
| Evaporator pressure (Kpag) | kpag | [25 empty] | #DIV/0!
| Condenser pressure (kpag) | kpag | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH | [25 empty] | 0
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR | [26 empty] | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Chiller No. 6
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 9: 1.2; Hours 10: 1.2; Hours 11: 1.1; Hours 12: 1.1; Hours 13: 1.1; Hours 14: 1.1; Hours 15: 1.2; Hours 16: 1.1; Hours 17: 1.2; Hours 18: 1.2; Hours 19: 1.1 | 1.1455
2 | Small temperature difference of evaporator | ºC |  | Hours 9: 0.5; Hours 10: 0.6; Hours 11: 0.4; Hours 12: 0.5; Hours 13: 0.6; Hours 14: 0.6; Hours 15: 0.6; Hours 16: 0.6; Hours 17: 0.7; Hours 18: 0.5; Hours 19: 0.5 | 0.55455
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 9: 14; Hours 10: 14.2; Hours 11: 14.4; Hours 12: 14.7; Hours 13: 14.7; Hours 14: 14.8; Hours 15: 15.1; Hours 16: 15.2; Hours 17: 15.3; Hours 18: 14.6; Hours 19: 13.4 | 14.5818
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 9: 5.9; Hours 10: 6.4; Hours 11: 6.3; Hours 12: 6.8; Hours 13: 6.3; Hours 14: 6.6; Hours 15: 7.1; Hours 16: 6.7; Hours 17: 6.7; Hours 18: 6.3; Hours 19: 6.3 | 6.4909
| Evaporator Delta "T" |  |  | Hours 9: 8.1; Hours 10: 7.8; Hours 11: 8.1; Hours 12: 7.9; Hours 13: 8.4; Hours 14: 8.2; Hours 15: 8; Hours 16: 8.5; Hours 17: 8.6; Hours 18: 8.3; Hours 19: 7.1 | 8.0909
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 9: 26.6; Hours 10: 26.7; Hours 11: 27.1; Hours 12: 27.4; Hours 13: 27.6; Hours 14: 27.6; Hours 15: 27.6; Hours 16: 26.9; Hours 17: 26.2; Hours 18: 26.7; Hours 19: 26.6 | 27
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 9: 32.2; Hours 10: 31.9; Hours 11: 32.7; Hours 12: 32.9; Hours 13: 33.3; Hours 14: 33.2; Hours 15: 33.1; Hours 16: 32.8; Hours 17: 31.9; Hours 18: 32.3; Hours 19: 32.3 | 32.6
| Condenser Delta "T" | ºC |  | Hours 9: 5.6; Hours 10: 5.2; Hours 11: 5.6; Hours 12: 5.5; Hours 13: 5.7; Hours 14: 5.6; Hours 15: 5.5; Hours 16: 5.9; Hours 17: 5.7; Hours 18: 5.6; Hours 19: 5.7 | 5.6
| Evaporator pressure (Kpag) | kpag |  | Hours 9: 253; Hours 10: 259.2; Hours 11: 258.6; Hours 12: 262; Hours 13: 257.9; Hours 14: 261.3; Hours 15: 266.8; Hours 16: 261.3; Hours 17: 263.4; Hours 18: 257.9; Hours 19: 257.9 | 259.9364
| Condenser pressure (kpag) | kpag |  | Hours 9: 741.9; Hours 10: 739.1; Hours 11: 759.1; Hours 12: 762.6; Hours 13: 772.2; Hours 14: 769.5; Hours 15: 766.7; Hours 16: 759.1; Hours 17: 737.7; Hours 18: 748.1; Hours 19: 748.1 | 754.9182
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 9: 4.2; Hours 10: 4.2; Hours 11: 4.2; Hours 12: 4.2; Hours 13: 4.2; Hours 14: 4.2; Hours 15: 4.2; Hours 16: 4.2; Hours 17: 4.2; Hours 18: 4.2; Hours 19: 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 9: 3.7; Hours 10: 3.7; Hours 11: 3.7; Hours 12: 3.7; Hours 13: 3.7; Hours 14: 3.7; Hours 15: 3.7; Hours 16: 3.7; Hours 17: 3.7; Hours 18: 3.7; Hours 19: 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 9: 3; Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 9: 0.5; Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 9: 971; Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 9: 2600.8929; Hours 10: 2504.5635; Hours 11: 2600.8929; Hours 12: 2536.6733; Hours 13: 2697.2222; Hours 14: 2633.0026; Hours 15: 2568.7831; Hours 16: 2729.332; Hours 17: 2761.4418; Hours 18: 2665.1124; Hours 19: 2279.795 | 28577.7116
15 | Power Consumption of Chiller | KWH |  | Hours 9: 1600; Hours 10: 1400; Hours 11: 1600; Hours 12: 1500; Hours 13: 1500; Hours 14: 1700; Hours 15: 1500; Hours 16: 1600; Hours 17: 1500; Hours 18: 1700; Hours 19: 1400 | 17000
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 9: 0.61517; Hours 10: 0.55898; Hours 11: 0.61517; Hours 12: 0.59133; Hours 13: 0.55613; Hours 14: 0.64565; Hours 15: 0.58393; Hours 16: 0.58622; Hours 17: 0.54319; Hours 18: 0.63787; Hours 19: 0.61409 | 0.59525
17 | Average iKW/TR |  |  | Hours 7: 0.59525 | 0.59525
18 | COP of chiller |  |  | Hours 9: 5.7155; Hours 10: 6.29; Hours 11: 5.7155; Hours 12: 5.946; Hours 13: 6.3223; Hours 14: 5.4457; Hours 15: 6.0212; Hours 16: 5.9977; Hours 17: 6.4728; Hours 18: 5.5121; Hours 19: 5.7255 | 5.924
19 | EER of Chiller |  |  | Hours 9: 19.5069; Hours 10: 21.4679; Hours 11: 19.5069; Hours 12: 20.2936; Hours 13: 21.578; Hours 14: 18.5861; Hours 15: 20.5504; Hours 16: 20.4702; Hours 17: 22.0917; Hours 18: 18.8127; Hours 19: 19.5413 | 20.2187
20 | LMTD of Condenser | ºC |  | Hours 9: 3.2284; Hours 10: 3.1064; Hours 11: 3.0994; Hours 12: 3.0696; Hours 13: 3.1291; Hours 14: 3.0994; Hours 15: 3.1981; Hours 16: 3.1882; Hours 17: 3.2586; Hours 18: 3.2284; Hours 19: 3.1291 | 3.1577
21 | LMTD of Evaporator | ºC |  | Hours 9: 2.8472; Hours 10: 2.9556; Hours 11: 2.6502; Hours 12: 2.8; Hours 13: 3.1019; Hours 14: 3.0533; Hours 15: 3.0046; Hours 16: 3.126; Hours 17: 3.3247; Hours 18: 2.8941; Hours 19: 2.6091 | 2.9424