## Summery
Date |  | Avg. DB Temperature (°C) | Avg. WB Temperature (°C) | Chilled Water Avg. Inlet Temperature (°C) | Chilled Water Avg. Outlet Temperature (°C) | Condenser Water Avg. Outlet Temperature (°C) | Condenser Water Avg. Inlet Temperature (°C) | Chiller No.1 | [10 empty] | Chiller No.2 | [10 empty] | Chiller No.3 | [10 empty] | Chiller No.4 | [10 empty] | Chiller No.5 | [10 empty] | Chiller No.6 | [10 empty] | Total TR Generated | Difference from previous day | Total Power Consumption (KWH) | Difference from previous day | Total Running Hrs. | Avg. FLA % | Avg iKW/tr
| Avg.RH Temp.(%) | [6 empty] | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C) | Running Hrs. | Total TR Generated | Total Power Consumption (KWH) | Specific Power Consumption (iKW/TR) | Avg. COP | Avg. EER | Avg. LMTD of Condenser (°C) | Avg. LMTD of Evaporator (°C) | Avg. FLA (%) | Avg. Small Temp. diff. of condenser (°C) | Avg. Small Temp. diff. of evaporator (°C)
2021-02-28 | [29 empty] | 24 |  | 33400 | [6 empty] | 3.4 | 0.81667 | [22 empty] | 10 |  | 12600 | [6 empty] | 1.1714 | 0.57143 | 0 | 0 | 46000 | -300 | 34 | #DIV/0! | #DIV/0!
2023-03-01 | 48.9917 | 28.4708 | 18.2833 | 13.4 | 9.0667 | 26.95 | 22.1792 | [22 empty] | 24 | 57540.7407 | 33800 | 0.5899 | 6.0045 | 20.4933 | 5.421 | 3.1624 | 84.0417 | 3.3833 | 0.78333 | [11 empty] | 12 | 28031.8452 | 16800 | 0.57514 | 10.5699 | 36.075 | 2.9051 | 3.4389 | 82.5455 | 1.0462 | 1.1231 | [11 empty] | 85572.586 | 85572.586 | 50600 | 4600 | 36 | 83.2936 | 0.59131
2023-03-02 | 34.3667 | 29.2833 | 18.1833 | 13.5542 | 9.1958 | 26.7167 | 22.0417 | [22 empty] | 24 | 59242.5595 | 34100 | 0.5764 | 6.1297 | 20.9206 | 5.6511 | 3.3332 | 83.4 | 3.59 | 0.85 | [11 empty] | 11 | 24371.3294 | 14800 | 0.60738 | 5.9076 | 20.1626 | 3.1421 | 4.0782 | 81.1 | 1.1909 | 1.5636 | [11 empty] | 83613.8889 | -1958.6971 | 48900 | -1700 | 35 | 82.25 | 0.58483
2023-03-03 | 37.525 | 29.6292 | 19.1167 | 13.7792 | 9.3625 | 27.4667 | 22.7708 | [22 empty] | 24 | 59499.4378 | 34800 | 0.58579 | 6.0231 | 20.5568 | 5.7962 | 3.2035 | 84.4 | 3.75 | 0.77 | [11 empty] | 11 | 25013.5251 | 15100 | 0.60373 | 6.0008 | 20.4806 | 3.136 | 4.0578 | 82.2 | 1.1818 | 1.5091 |  |  | 1500 | [8 empty] | 84512.963 | 899.0741 | 51400 | 2500 | 35 | 83.3 | 0.60819
2023-03-04 | 41.3167 | 30.0333 | 20.1458 | 13.925 | 9.1417 | 28.4417 | 23.7875 | [22 empty] | 24 | 58150.8267 | 33700 | 0.58071 | 6.0922 | 20.7928 | 5.7525 | 3.034 | 81.9 | 3.8042 | 0.6875 | [22 empty] | 16 | 37407.9034 | 21700 | 0.58213 | 6.1213 | 20.8919 | 3.13 | 2.9664 | 81.8 | 1.1812 | 0.65 | 95558.7302 | 11045.7672 | 55400 | 4000 | 40 | 81.85 | 0.57975
2023-03-05 | 42.4042 | 30.3875 | 20.6833 | 14 | 9.3 | 28.3 | 23.7 | [22 empty] | 24 | 57412.3016 | 33300 | 0.58105 | 6.0924 | 20.7935 | 5.8765 | 2.9163 | 83.2 | 3.93 | 0.63 | [22 empty] | 18 | 36605.1587 | 23900 | 0.58784 | 6.0426 | 20.6235 | 3.2079 | 2.7969 | 80.9 | 1.24 | 0.61 | 94017.4603 | -1541.2698 | 57200 | 1800 | 42 | 82.05 | 0.6084
2023-03-06 | 32.8333 | 29.7042 | 18.225 | 13.5792 | 9.125 | 26.5667 | 21.9 | [22 empty] | 24 | 59692.0966 | 34300 | 0.57757 | 6.1447 | 20.9718 | 6.2494 | 3.1276 | 84.7 | 4.1833 | 0.71667 | [22 empty] | 10 | 15605.3571 | 14900 | 0.67761 | 5.3466 | 18.2478 | 3.51 | 2.919 | 81.8 | 1.3333 | 0.75 | 75297.4537 | -18720.0066 | 49200 | -8000 | 34 | 83.25 | 0.65341
2023-03-07 | 38.325 | 28.7875 | 18.6417 | 13.4958 | 9.2375 | 26.6833 | 22.0583 | [22 empty] | 24 | 59338.8889 | 34500 | 0.58256 | 6.0665 | 20.705 | 6.2521 | 2.9758 | 83.6 | 4.1875 | 0.63333 | [11 empty] | 8 | 18431.0185 | 12500 | 0.646 | 5.4586 | 18.6302 | 3.2883 | 4.1645 | 87.3 | 1.275 | 1.5625 | 2 | 5009.127 | 2600 | 0.51243 | 7.0067 | 23.914 | 3.7747 | 2.9544 | 81 | 1.5 | 0.6 | 82779.0344 | 7481.5807 | 49600 | 400 | 34 | 83.9667 | 0.59919
2023-03-08 | 35.175 | 29.3625 | 18.5542 | 13.6125 | 9.2125 | 26.85 | 22.1333 | [22 empty] | 24 | 59178.3399 | 35100 | 0.59438 | 5.9579 | 20.3342 | 6.566 | 3.2852 | 84.5 | 4.4708 | 0.825 | [11 empty] | 11 | 24242.8902 | 16300 | 0.61915 | 6.023 | 20.5566 | 3.3877 | 4.4034 | 83.1 | 1.38 | 1.66 | [11 empty] | 83421.2302 | 642.1958 | 51400 | 1800 | 35 | 83.8 | 0.61615
2023-03-09 | 23.1208 | 30.7833 | 16.8958 | 13.6833 | 9.3417 | 25.7083 | 21.0542 | [22 empty] | 24 | 58439.8148 | 33800 | 0.57977 | 6.1118 | 20.8595 | 6.54 | 3.0946 | 82.8333 | 4.475 | 0.725 | [11 empty] | 11 | 23568.5847 | 15700 | 0.64615 | 5.6854 | 19.4043 | 3.3713 | 4.2252 | 78.9 | 1.4182 | 1.7364 | [11 empty] | 82008.3995 | -1412.8307 | 49500 | -1900 | 35 | 80.8667 | 0.6036
2023-03-10 | 24.7417 | 30.3917 | 16.9042 | 13.5542 | 9.1583 | 25.5083 | 20.8458 | [22 empty] | 24 | 58375.5952 | 33900 | 0.5826 | 6.0879 | 20.7781 | 6.7733 | 3.1418 | 82.375 | 4.6833 | 0.75417 | [11 empty] | 11 | 25591.5013 | 17100 | 0.64358 | 5.7901 | 19.7615 | 3.4725 | 4.1402 | 80.7273 | 1.5333 | 1.675 | [11 empty] | 83967.0966 | 1958.6971 | 51000 | 1500 | 35 | 81.5511 | 0.60738
2023-03-11 | 29.8 | 31.1 | 18.5 | 13.5 | 8.9 | 26.9 | 22.4 | 17 | 36027.1825 | 21200 | 0.5782 | 6.0991 | 20.8162 | 6.6066 | 3.5776 | 72.4 | 4.31 | 1.19 | [11 empty] | 20 | 50059.1601 | 27900 | 0.55394 | 6.1649 | 21.0408 | 6.7781 | 3.0054 | 83.8 | 4.76 | 0.69 | [11 empty] | 2 | 5266 | 2500 | 0.64358 | 5.7901 | 19.7615 | 3.4725 | 4.1402 | 89 | 1.29 | 1.74 | [11 empty] | 91352.3426 | 7385.246 | 51600 | 600 | 39 | 81.7333 | 0.56485
2023-03-12 | 33.4 | 31.2 | 19.5 | 13.8 | 9.1 | 28.3 | 23.3 | 24 | 58921.4616 | 34800 | 0.59341 | 5.9762 | 20.3969 | 7.0169 | 3.2184 | 79.5 | 4.53 | 0.8 | [33 empty] | 13 | 29091.4683 | 21700 | 0.53165 | 5.7443 | 19.6053 | 3.6346 | 3.7987 | 80.5 | 1.59 | 1.33 | [11 empty] | 88012.9299 | -3339.4127 | 56500 | 4900 | 37 | 80 | 0.64195
2023-03-13 | 36.1 | 31.3 | 20.1 | 13.9 | 9.1 | 28.8 | 23..8 | 20 | 50123.3796 | 29600 | 0.55374 | 6.8947 | 23.5317 | 6.9694 | 3.1268 | 79.4 | 4.5 | 0.71 | [33 empty] | 19 | 41710.6151 | 26300 | 0.61823 | 7.4579 | 25.4538 | 3.8681 | 4.0566 | 82.9 | 1.74 | 1.47 | [11 empty] | 91833.9947 | 91833.9947 | 55900 | -600 | 39 | 81.15 | 0.60871
2023-03-14 | 42.1 | 30.2 | 20.5 | 13.7 | 8.6 | 28.9 | 23.9 | 21 | 52692.1627 | 30200 | 0.54837 | 6.2423 | 21.3049 | 6.9817 | 3.1009 | 78.8 | 4.57 | 0.69 | [44 empty] | 19 | 50405.074 | 26900 | 0.55382 | 6.457 | 22.0378 | 3.5843 | 3.133 | 83.5 | 1.44 | 0.75 | 103097.2367 | 11263.242 | 57100 | 1200 | 40 | 81.15 | 0.55385
2023-03-15 | 57.5 | 29.6 | 22.8 | 13.9 | 8.7 | 30.2 | 25.3 | 22 | 52788.4921 | 31200 | 0.58811 | 6.0596 | 20.6815 | 6.6033 | 3.0671 | 77 | 4.29 | 0.74 | [44 empty] | 22 | 50316.0384 | 34100 | 0.64417 | 5.4886 | 18.7324 | 3.495 | 3.0351 | 84.5 | 1.44 | 0.75 | 103104.5304 | 7.2937 | 65300 | 8200 | 44 | 80.75 | 0.63334
2023-03-16 | 62.1833 | 27.9125 | 22.2625 | 13.725 | 8.5917 | 29.8958 | 24.9 | 18 | 42513.3598 | 24900 | 0.58702 | 6.0694 | 20.715 | 6.4564 | 2.9786 | 74.5 | 4.1611 | 0.68889 | [24 empty] | 1800 | [19 empty] | 24 | 56063.6905 | 35400 | 0.63242 | 5.5802 | 19.0453 | 3.5815 | 3.0547 | 84.2 | 1.4917 | 0.74167 | 98577.0503 | -4527.4802 | 62100 | -3200 | 42 | 79.35 | 0.62996
2023-03-17 | 65.3 | 27.7708 | 22.6167 | 13.9833 | 8.9708 | 30.2583 | 25.2167 | [33 empty] | 24 | 58857.2421 | 36100 | 0.6137 | 5.7469 | 19.6141 | 3.5291 | 3.1415 | 89 | 1.6125 | 0.7375 | [11 empty] | 18 | 34935.4497 | 26300 | 0.63925 | 5.5316 | 18.8795 | 3.541 | 3.1399 | 84.9 | 1.4467 | 0.8 | 93792.6918 | -4784.3585 | 62400 | 300 | 42 | 86.95 | 0.6653
2023-03-18 | 66.7333 | 27.7625 | 22.8583 | 13.6125 | 8.2667 | 30.125 | 25.3375 | [33 empty] | 24 | 53880.2249 | 33200 | 0.61821 | 5.7273 | 19.5472 | 3.2318 | 2.8805 | 84.6 | 1.4792 | 0.67917 | [11 empty] | 24 | 52049.9669 | 33400 | 0.64278 | 5.4881 | 18.7308 | 3.4326 | 2.8666 | 81.9 | 1.4542 | 0.70833 | 105930.1918 | 12137.5 | 66600 | 4200 | 48 | 83.25 | 0.62872
2023-03-19 | 60.4375 | 27.8292 | 21.9333 | 13.475 | 8.4917 | 29.6208 | 24.6875 | [33 empty] | 24 | 56256.3492 | 35100 | 0.6293 | 5.6491 | 19.2805 | 3.0648 | 3.085 | 86.8 | 1.2458 | 0.75833 | [11 empty] | 16 | 32206.1177 | 24600 | 0.6301 | 5.7058 | 19.4738 | 3.3413 | 3.0505 | 80.2 | 1.3214 | 0.75714 | 88462.4669 | -17467.7249 | 59700 | -6900 | 40 | 83.5 | 0.67486
2023-03-20 | 57.175 | 27.3458 | 20.9417 | 13.7125 | 8.8875 | 29.025 | 23.9083 | [33 empty] | 24 | 59852.6455 | 35600 | 0.59534 | 5.9338 | 20.252 | 3.1218 | 3.3103 | 87.4 | 1.2167 | 0.825 | [11 empty] | 12 | 19651.1905 | 19100 | 0.6165 | 5.7298 | 19.5557 | 3.4863 | 3.2024 | 80.1 | 1.3625 | 0.775 | 79503.836 | -8958.631 | 54700 | -5000 | 36 | 83.75 | 0.68802
2023-03-21 | 67.35 | 26.2792 | 21.5208 | 13.7208 | 9.0583 | 29.3792 | 24.2833 | [33 empty] | 24 | 59210.4497 | 35700 | 0.6044 | 5.8508 | 19.9688 | 2.9482 | 3.2967 | 88 | 1.0917 | 1 | [11 empty] | 12 | 19008.9947 | 18200 | 0.63429 | 5.5868 | 19.0677 | 3.4746 | 3.2167 | 80.9 | 1.3625 | 0.825 | 78219.4444 | -1284.3915 | 53900 | -800 | 36 | 84.45 | 0.68909
2023-03-22 | 61.7667 | 27.325 | 21.6 | 13.9458 | 9.0833 | 29.8333 | 24.6292 | [33 empty] | 24 | 60334.2923 | 36600 | 0.60692 | 5.8091 | 19.8265 | 2.9716 | 3.3275 | 90.0833 | 1.0708 | 0.825 | [11 empty] | 13 | 30183.2011 | 19500 | 0.61683 | 5.8585 | 19.9952 | 3.345 | 3.1567 | 86 | 1.2769 | 0.81538 | 90517.4934 | 12298.0489 | 56100 | 2200 | 37 | 88.0417 | 0.61977
2023-03-23 | 62.9458 | 27.3625 | 21.8625 | 14.025 | 9.125 | 29.9083 | 24.7125 | [33 empty] | 24 | 59595.7672 | 36200 | 0.60799 | 5.8018 | 19.8014 | 2.8349 | 3.3029 | 90.5 | 0.99583 | 0.825 | [11 empty] | 13 | 33458.3995 | 20700 | 0.59748 | 6.0706 | 20.719 | 3.5054 | 3.2007 | 86.7692 | 1.35 | 0.80714 | 93054.1667 | 2536.6733 | 56900 | 800 | 37 | 88.6346 | 0.61147
2023-03-24 | 61.2208 | 27.65 | 21.8625 | 13.6542 | 8.5792 | 29.7458 | 24.725 | [33 empty] | 24 | 57380.1918 | 34500 | 0.6024 | 5.8613 | 20.0046 | 2.6157 | 3.1701 | 88.9583 | 0.87826 | 0.78696 | [11 empty] | 17 | 39206.0516 | 26300 | 0.63918 | 5.5466 | 18.9305 | 3.2388 | 3.0373 | 84 | 1.225 | 0.74375 | 96586.2434 | 3532.0767 | 60800 | 3900 | 41 | 86.4792 | 0.62949
2023-03-25 | 52.7042 | 26.3958 | 19.3375 | 13.6542 | 8.9958 | 27.75 | 22.6458 | [33 empty] | 16 | 39270.2712 | 20300 | 0.51556 | 7.4134 | 25.3021 | 2.701 | 3.5842 | 85.3 | 0.90625 | 1.0313 | [11 empty] | 20 | 48036.2434 | 28300 | 0.59085 | 6.1187 | 20.8831 | 3.0699 | 3.0539 | 79.8 | 1.115 | 0.71 | 87306.5146 | -9279.7288 | 48600 | -12200 | 36 | 82.55 | 0.55666
2023-03-26 | 57.3542 | 26.5292 | 20.2542 | 13.6 | 8.9 | 28.3 | 23.3 | [22 empty] | 19 | 40233.5648 | 25600 | 0.59072 | 6.0009 | 20.4812 | 1.9365 | 3.8343 | 82.2 | 1.46 | 1.26 | [22 empty] | 18 | 43637.2024 | 25600 | 0.58509 | 6.1981 | 21.1543 | 3.2165 | 3.1034 | 81.4 | 1.17 | 0.73 | 83870.7672 | -3435.7474 | 51200 | 2600 | 37 | 81.8 | 0.61046
2023-03-27 | 62.9292 | 27.0917 | 21.6792 | 13.15 | 8.2 | 29.0917 | 24.5208 | [22 empty] | 24 | 53655.4563 | 32700 | 0.61098 | 5.7923 | 19.769 | 2.0181 | 3.8298 | 79.3 | 0.53333 | 1.35 | [22 empty] | 19 | 40458.3333 | 25500 | 0.63246 | 5.6803 | 19.3867 | 2.9827 | 3.2574 | 82.2 | 1.1316 | 1.0158 | 94113.7897 | 10243.0225 | 58200 | 7000 | 43 | 80.75 | 0.6184
2023-03-28 | 63.1417 | 27.3375 | 21.8833 | 12.925 | 7.9958 | 28.9792 | 24.6833 | [22 empty] | 24 | 50926.1243 | 30900 | 0.60714 | 5.8157 | 19.849 | 1.9945 | 3.6688 | 76.2 | 0.57917 | 1.3083 | [22 empty] | 21 | 41453.7368 | 28000 | 0.68315 | 5.2253 | 17.8339 | 2.9793 | 3.4144 | 79.4 | 1.14 | 1.28 | 92379.8611 | -1733.9286 | 58900 | 700 | 45 | 77.8 | 0.63758
2023-03-29 | 63.65 | 27.3292 | 21.9792 | 12.3042 | 7.3542 | 28.7875 | 24.8833 | [22 empty] | 24 | 43219.7751 | 27000 | 0.62776 | 5.627 | 19.2049 | 1.7778 | 3.1813 | 68.6667 | 0.55 | 1.1625 | [22 empty] | 24 | 38884.9537 | 34100 | 0.88323 | 4.0126 | 13.6951 | 3.1088 | 4.7538 | 82.4167 | 1.1875 | 2.675 | 82104.7288 | -10275.1323 | 61100 | 2200 | 48 | 75.5417 | 0.74417
2023-03-30 | 60.8542 | 27.75 | 21.9125 | 12.4125 | 7.5375 | 28.9292 | 24.9125 | [22 empty] | 24 | 45692.2288 | 29000 | 0.63949 | 5.5326 | 18.8826 | 1.8527 | 3.2762 | 70.9583 | 0.55 | 1.1625 | [11 empty] | 2 | 4944.9074 | 3000 | 0.56624 | 6.2094 | 21.1927 | 3.226 | 3.7029 | 87 | 1 | 1.1 | 19 | 29797.8836 | 27600 | 0.92815 | 3.8152 | 13.0211 | 3.2082 | 5.0914 | 82.8421 | 1.2211 | 3.0368 | 80435.0198 | -1669.709 | 59600 | -1500 | 45 | 80.2668 | 0.74097
2023-03-31 | 63.2 | 27.8 | 22.4 | 13.5 | 8.5 | 29.5 | 25.3 | [22 empty] | 24 | 52114.1865 | 32200 | 0.61822 | 5.7121 | 19.4953 | 2.1394 | 3.8504 | 78.8 | 0.64 | 1.41 | [11 empty] | 24 | 50316.0384 | 32300 | 0.64207 | 5.4999 | 18.7711 | 2.5332 | 3.3349 | 77.8 | 0.83 | 1.08 | [11 empty] | 102430.2249 | 21995.205 | 64500 | 4900 | 48 | 78.3 | 0.6297
Average/Total | 48.5336 | 28.7438 | 20.2731 | 13.6631 | 8.9174 | 28.3644 | 23.5156 | 122 | 293066.0384 | 171900 | 0.57481 | 6.2236 | 21.241 | 6.7724 | 3.1782 | 76.9333 | 4.3935 | 0.80315 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 327 | 781744.9074 | 458400 | 0.58525 | 6.0369 | 20.604 | 5.245 | 3.2654 | 82.6036 | 3.4159 | 0.85595 | 208 | 504637.4339 | 305100 | 0.59931 | 5.9771 | 20.3997 | 3.0021 | 3.2332 | 87.8491 | 1.1663 | 0.8298 | 109 | 245318.7778 | 158800 | 0.61346 | 5.9842 | 20.4241 | 3.4192 | 4.1183 | 82.8273 | 1.3999 | 1.537 | 314 | 685697.2367 | 456500 | 0.6157 | 5.8307 | 19.9001 | 3.363 | 3.0821 | 82.3826 | 1.3148 | 0.77996 | 2510464.3941 | 180392.791 | 1550700 | 12900 | 1080 | 82.7952 | 0.61838

## 01-03-2023
Performance Sheet Chiller
Date :- 01/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 3.7 | 3.7 | 3.6 | 3.8 | 3.6 | 3.7 | 3.4 | 3.2 | 3.2 | 2.7 | 3.3 | 3.4 | 3.4 | 3.4 | 3.2 | 3.5 | 3.7 | 3.7 | 3.6 | 3 | 3 | 2.7 | 3.2 | 3.5 | 3.3833
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.9 | 1.1 | 1 | 1.1 | 1 | 0.9 | 0.6 | 0.6 | 0.8 | 0.6 | 0.7 | 0.6 | 0.9 | 1 | 0.9 | 0.7 | 1.1 | 0.7 | 0.5 | 0.4 | 0.4 | 0.9 | 0.6 | 0.78333
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.9 | 14.2 | 14.5 | 14.7 | 15 | 15 | 15 | 14.1 | 13.7 | 13.6 | 13.1 | 13.2 | 13 | 13 | 14.4 | 15.2 | 14.8 | 13.2 | 12.2 | 11.7 | 11.5 | 11.4 | 12.8 | 13.1 | 13.5958
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.8 | 6.1 | 6.2 | 6.4 | 6.6 | 7 | 6.8 | 7 | 7.2 | 5.8 | 5.6 | 5.4 | 5.7 | 6.2 | 6.8 | 7.2 | 6.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.5 | 5.7 | 6.1292
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.5 | 20.7 | 20.9 | 20.8 | 20.5 | 21.2 | 24.2 | 23.8 | 23.4 | 24.3 | 23.5 | 23.1 | 22.7 | 22.4 | 22.1 | 22.3 | 22.4 | 22.3 | 22.2 | 22.1 | 22 | 21.9 | 21.7 | 21.3 | 22.1792
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 25.5 | 25.6 | 26 | 26.1 | 25.6 | 26.3 | 29.3 | 28.1 | 28 | 28.7 | 28 | 27.6 | 27.3 | 27.4 | 27.3 | 28.2 | 29.7 | 27.6 | 26 | 26.3 | 25.8 | 25.3 | 25.4 | 25.7 | 26.95
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2697.2222 | 2697.2222 | 2697.2222 | 2729.332 | 2761.4418 | 2697.2222 | 2568.7831 | 2344.0146 | 2151.3558 | 2055.0265 | 2344.0146 | 2440.3439 | 2440.3439 | 2344.0146 | 2633.0026 | 2697.2222 | 2440.3439 | 2151.3558 | 2151.3558 | 1990.8069 | 1926.5873 | 1862.3677 | 2344.0146 | 2376.1243 | 57540.7407
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1500 | 1500 | 1500 | 1500 | 1400 | 1200 | 1300 | 1500 | 1400 | 1400 | 1400 | 1500 | 1500 | 1700 | 1500 | 1500 | 1200 | 1300 | 1100 | 1100 | 1200 | 1500 | 33800
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.55613 | 0.5932 | 0.55613 | 0.54959 | 0.54319 | 0.55613 | 0.54501 | 0.51194 | 0.60427 | 0.72992 | 0.59727 | 0.57369 | 0.57369 | 0.63993 | 0.56969 | 0.63028 | 0.61467 | 0.69723 | 0.55779 | 0.653 | 0.57096 | 0.59065 | 0.51194 | 0.63128 | 0.5899
17 | Average iKW/TR |  |  | Hours 7: 0.5899 | 0.5899
18 | COP of chiller |  |  | 6.3223 | 5.9271 | 6.3223 | 6.3976 | 6.4728 | 6.3223 | 6.4513 | 6.868 | 5.8186 | 4.817 | 5.8868 | 6.1287 | 6.1287 | 5.4944 | 6.1718 | 5.5785 | 5.7202 | 5.0428 | 6.3035 | 5.3844 | 6.1581 | 5.9528 | 6.868 | 5.5696 | 6.0045
19 | EER of Chiller |  |  | 21.578 | 20.2293 | 21.578 | 21.8349 | 22.0917 | 21.578 | 22.0183 | 23.4404 | 19.8588 | 16.4404 | 20.0917 | 20.9174 | 20.9174 | 18.7523 | 21.0642 | 19.0394 | 19.5229 | 17.211 | 21.5138 | 18.3768 | 21.0175 | 20.3169 | 23.4404 | 19.0092 | 20.4933
20 | LMTD of Condenser | ºC |  | 5.848 | 5.8096 | 5.7798 | 6.0691 | 5.7798 | 5.8863 | 5.5659 | 5.0484 | 5.1629 | 4.5509 | 5.2313 | 5.3375 | 5.3759 | 5.5282 | 5.3881 | 5.972 | 6.6999 | 5.9625 | 5.2738 | 4.7974 | 4.6437 | 4.1716 | 4.8154 | 5.4047 | 5.421
21 | LMTD of Evaporator | ºC |  | 3.4393 | 3.5969 | 3.8961 | 3.7756 | 3.9507 | 3.7488 | 3.4913 | 2.832 | 2.6814 | 2.9128 | 2.832 | 3.0733 | 2.9064 | 3.3039 | 3.695 | 3.5969 | 3.0733 | 3.4204 | 2.8412 | 2.389 | 2.164 | 2.1161 | 3.3039 | 2.8568 | 3.1624
Performance Sheet Chiller
Date :- 01/03/2023
CHILLER NO.5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 12: 1; Hours 13: 1; Hours 14: 1; Hours 15: 1; Hours 16: 1; Hours 17: 0.9; Hours 18: 1.1; Hours 23: 1.1; Hours 0: 1.1; Hours 1: 1.1; Hours 2: 1.1; Hours 3: 1.1; Hours 4: 1.1 | 1.0462 | 0
2 | Small temperature difference of evaporator | ºC |  | Hours 12: 0.9; Hours 13: 0.9; Hours 14: 0.9; Hours 15: 0.9; Hours 16: 0.9; Hours 17: 0.9; Hours 18: 1.6; Hours 23: 1.9; Hours 0: 1.9; Hours 1: 1.1; Hours 2: 0.9; Hours 3: 0.9; Hours 4: 0.9 | 1.1231
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 12: 13.6; Hours 13: 13.6; Hours 14: 13.6; Hours 15: 13.6; Hours 16: 13.6; Hours 17: 13.4; Hours 18: 13.2; Hours 23: 14.6; Hours 0: 14.6; Hours 1: 13.2; Hours 2: 12.2; Hours 3: 11.8; Hours 4: 11.5 | 13.2692
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 12: 7; Hours 13: 7; Hours 14: 7; Hours 15: 7; Hours 16: 6.9; Hours 17: 6.4; Hours 18: 6.2; Hours 23: 7.8; Hours 0: 7.8; Hours 1: 5.6; Hours 2: 5.5; Hours 3: 5.5; Hours 4: 5.5 | 6.5538
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 12: 24.2; Hours 13: 24.2; Hours 14: 24.2; Hours 15: 24.2; Hours 16: 24.3; Hours 17: 23.5; Hours 18: 23.1; Hours 23: 22.3; Hours 0: 22.3; Hours 1: 22.3; Hours 2: 22.2; Hours 3: 21.4; Hours 4: 21.4 | 23.0462
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 12: 29.4; Hours 13: 29.4; Hours 14: 29.4; Hours 15: 29.4; Hours 16: 29.2; Hours 17: 28.4; Hours 18: 28.6; Hours 23: 27.7; Hours 0: 27.7; Hours 1: 27.4; Hours 2: 27.2; Hours 3: 26.7; Hours 4: 26.5 | 28.2308
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 12: 4.3; Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 23: 4.3; Hours 0: 4.3; Hours 1: 4.3; Hours 2: 4.3; Hours 3: 4.3; Hours 4: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3; Hours 3: 3; Hours 4: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5; Hours 3: 0.5; Hours 4: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8; Hours 3: 0.8; Hours 4: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971; Hours 3: 971; Hours 4: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 12: 2119.246; Hours 13: 2119.246; Hours 14: 2119.246; Hours 15: 2119.246; Hours 16: 2151.3558; Hours 17: 2247.6852; Hours 18: 2247.6852; Hours 23: 2183.4656; Hours 0: 2183.4656; Hours 1: 2440.3439; Hours 2: 2151.3558; Hours 3: 2022.9167; Hours 4: 1926.5873 | 28031.8452
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 1400 | 1500 | 1300 | 1400 | 1500 | 1400 | 900 | 0 | 0 | 0 | 600 | 1400 | 1400 | 1300 | 1300 | 1300 | 100 | 0 | 0 | 16800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 12: 0.66061; Hours 13: 0.7078; Hours 14: 0.61343; Hours 15: 0.66061; Hours 16: 0.69723; Hours 17: 0.62286; Hours 18: 0.40041; Hours 23: 0.64118; Hours 0: 0.64118; Hours 1: 0.53271; Hours 2: 0.60427; Hours 3: 0.64264; Hours 4: 0.051905 | 0.57514
17 | Average iKW/TR |  |  | Hours 7: 0.57514 | 0.57514
18 | COP of chiller |  |  | Hours 12: 5.3223; Hours 13: 4.9675; Hours 14: 5.7317; Hours 15: 5.3223; Hours 16: 5.0428; Hours 17: 5.6449; Hours 18: 8.781; Hours 23: 5.4836; Hours 0: 5.4836; Hours 1: 6.6002; Hours 2: 5.8186; Hours 3: 5.4712; Hours 4: 67.7388 | 10.5699
19 | EER of Chiller |  |  | Hours 12: 18.1651; Hours 13: 16.9541; Hours 14: 19.5624; Hours 15: 18.1651; Hours 16: 17.211; Hours 17: 19.266; Hours 18: 29.9694; Hours 23: 18.7156; Hours 0: 18.7156; Hours 1: 22.5265; Hours 2: 19.8588; Hours 3: 18.6732; Hours 4: 231.1926 | 36.075
20 | LMTD of Condenser | ºC |  | Hours 12: 2.85; Hours 13: 2.85; Hours 14: 2.85; Hours 15: 2.85; Hours 16: 2.7606; Hours 17: 2.6299; Hours 18: 3.0696; Hours 23: 3.0397; Hours 0: 3.0397; Hours 1: 2.9493; Hours 2: 2.9189; Hours 3: 3.0097; Hours 4: 2.9493 | 2.9051
21 | LMTD of Evaporator | ºC |  | Hours 12: 3.1128; Hours 13: 3.1128; Hours 14: 3.1128; Hours 15: 3.1128; Hours 16: 3.1404; Hours 17: 3.2225; Hours 18: 4.1623; Hours 23: 4.4694; Hours 0: 4.4694; Hours 1: 3.675; Hours 2: 3.1404; Hours 3: 3.0297; Hours 4: 2.9457 | 3.4389

## 02-03-2023
Performance Sheet Chiller
Date :- 02/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 3.6 | 3.7 | 3.5 | 3.4 | 3.8 | 3.8 | 3.8 | 3.9 | 3.4 | 3.1 | 3.5 | 3.6 | 3.4 | 3.4 | 3.7 | 3.9 | 3.8 | 3.8 | 3.7 | 3.2 | 3.1 | 3.4 | 3.7 | 3.9 | 3.5875
2 | Small temperature difference of evaporator | ºC |  | 1 | 0.9 | 1 | 1.1 | 1.1 | 1.1 | 0.9 | 0.6 | 0.6 | 0.6 | 0.9 | 0.6 | 0.8 | 0.8 | 0.9 | 1.1 | 1.1 | 0.9 | 0.8 | 0.6 | 0.8 | 0.6 | 0.8 | 0.9 | 0.85417
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.5 | 13.8 | 14.5 | 14.8 | 15.3 | 15.6 | 15.8 | 14.4 | 14 | 13.7 | 13.7 | 13.2 | 12.6 | 13.2 | 14.1 | 14.6 | 14.9 | 15.1 | 13.8 | 12.6 | 11.8 | 12.2 | 13.1 | 13.9 | 13.925
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.7 | 6.1 | 6.7 | 6.9 | 7 | 7.8 | 7 | 7 | 6.9 | 5.9 | 5.5 | 5.5 | 5.6 | 6.1 | 6.6 | 6.9 | 7 | 5.9 | 5.4 | 5.3 | 5.8 | 5.7 | 5.9 | 6.2375
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.1 | 21 | 21.3 | 21.6 | 21.8 | 22 | 23.9 | 24.3 | 23.7 | 22.9 | 22.7 | 22.6 | 22.1 | 21.7 | 22 | 22 | 22 | 22.7 | 22.7 | 22.5 | 22.6 | 21.6 | 21.6 | 21.2 | 22.2333
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.1 | 26.2 | 26.6 | 26.8 | 27.2 | 27.4 | 29 | 29 | 27.9 | 27.2 | 27.4 | 27.3 | 26.5 | 26.2 | 27 | 27.2 | 27.2 | 27.8 | 27.6 | 26.8 | 26.4 | 25.4 | 26.4 | 26.2 | 27.0333
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2600.8929 | 2697.2222 | 2600.8929 | 2697.2222 | 2761.4418 | 2568.7831 | 2376.1243 | 2247.6852 | 2183.4656 | 2504.5635 | 2472.4537 | 2279.795 | 2440.3439 | 2568.7831 | 2568.7831 | 2568.7831 | 2600.8929 | 2536.6733 | 2311.9048 | 2087.1362 | 2055.0265 | 2376.1243 | 2568.7831 | 59242.5595
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1500 | 1600 | 1500 | 1500 | 1500 | 1100 | 1400 | 1400 | 1400 | 1400 | 1300 | 1400 | 1500 | 1600 | 1400 | 1500 | 1400 | 1200 | 1200 | 1300 | 1500 | 1500 | 34100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58393 | 0.57673 | 0.55613 | 0.61517 | 0.55613 | 0.54319 | 0.58393 | 0.46294 | 0.62286 | 0.64118 | 0.55898 | 0.56624 | 0.57023 | 0.57369 | 0.58393 | 0.62286 | 0.54501 | 0.57673 | 0.5519 | 0.51905 | 0.57495 | 0.6326 | 0.63128 | 0.58393 | 0.5764
17 | Average iKW/TR |  |  | Hours 7: 0.5764 | 0.5764
18 | COP of chiller |  |  | 6.0212 | 6.0965 | 6.3223 | 5.7155 | 6.3223 | 6.4728 | 6.0212 | 7.595 | 5.6449 | 5.4836 | 6.29 | 6.2094 | 6.166 | 6.1287 | 6.0212 | 5.6449 | 6.4513 | 6.0965 | 6.3707 | 6.7739 | 6.1153 | 5.5581 | 5.5696 | 6.0212 | 6.1297
19 | EER of Chiller |  |  | 20.5504 | 20.8073 | 21.578 | 19.5069 | 21.578 | 22.0917 | 20.5504 | 25.9216 | 19.266 | 18.7156 | 21.4679 | 21.1927 | 21.0445 | 20.9174 | 20.5504 | 19.266 | 22.0183 | 20.8073 | 21.7431 | 23.1193 | 20.8716 | 18.9696 | 19.0092 | 20.5504 | 20.9206
20 | LMTD of Condenser | ºC |  | 5.7417 | 5.9245 | 5.7484 | 5.6035 | 6.1072 | 6.1072 | 5.9926 | 5.9435 | 5.2215 | 4.9421 | 5.5205 | 5.6266 | 5.299 | 5.3375 | 5.848 | 6.1372 | 6.0309 | 5.9926 | 5.8096 | 5.0484 | 4.7493 | 5.0646 | 5.7711 | 6.0601 | 5.6511
21 | LMTD of Evaporator | ºC |  | 3.641 | 3.5178 | 3.7488 | 3.8138 | 3.8961 | 3.9507 | 3.4913 | 2.8568 | 2.757 | 2.7067 | 3.4381 | 2.931 | 3.1004 | 3.2322 | 3.4913 | 3.7862 | 3.7862 | 3.5178 | 3.3103 | 2.8071 | 2.9398 | 2.6051 | 3.1797 | 3.4913 | 3.3332
Performance Sheet Chiller
Date :- 02/03/2023
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 13: 1.2; Hours 14: 1.2; Hours 15: 1.2; Hours 16: 1.1; Hours 17: 1.2; Hours 18: 1.2; Hours 19: 1.2; Hours 0: 1.3; Hours 1: 1.2; Hours 2: 1.2; Hours 3: 1.1 | 1.1909
2 | Small temperature difference of evaporator | ºC |  | Hours 13: 2; Hours 14: 1.4; Hours 15: 1.4; Hours 16: 1.6; Hours 17: 1.6; Hours 18: 1.6; Hours 19: 1.5; Hours 0: 2; Hours 1: 1.7; Hours 2: 1.6; Hours 3: 0.8 | 1.5636
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 13: 15.7; Hours 14: 14.4; Hours 15: 13.9; Hours 16: 13.6; Hours 17: 13.6; Hours 18: 13.1; Hours 19: 12.7; Hours 0: 15.2; Hours 1: 13.7; Hours 2: 12.6; Hours 3: 11.8 | 13.6636
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 13: 8.5; Hours 14: 7.6; Hours 15: 7.2; Hours 16: 7; Hours 17: 6.6; Hours 18: 6.1; Hours 19: 5.8; Hours 0: 7.8; Hours 1: 6.7; Hours 2: 5.8; Hours 3: 5.3 | 6.7636
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 13: 23.7; Hours 14: 24.4; Hours 15: 23.7; Hours 16: 22.7; Hours 17: 22.6; Hours 18: 22.5; Hours 19: 22.1; Hours 0: 22.5; Hours 1: 22.7; Hours 2: 22.5; Hours 3: 22.3 | 22.8818
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 13: 29.4; Hours 14: 29.7; Hours 15: 28.9; Hours 16: 27.7; Hours 17: 28.1; Hours 18: 27.9; Hours 19: 27.4; Hours 0: 28.3; Hours 1: 28.2; Hours 2: 27.7; Hours 3: 27.3 | 28.2364
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 0: 4.3; Hours 1: 4.3; Hours 2: 4.3; Hours 3: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3; Hours 3: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5; Hours 3: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8; Hours 3: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971; Hours 3: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 13: 2311.9048; Hours 14: 2183.4656; Hours 15: 2151.3558; Hours 16: 2119.246; Hours 17: 2247.6852; Hours 18: 2247.6852; Hours 19: 2215.5754; Hours 0: 2376.1243; Hours 1: 2247.6852; Hours 2: 2183.4656; Hours 3: 2087.1362 | 24371.3294
15 | Power Consumption of Chiller | KWH |  | Hours 13: 1400; Hours 14: 1500; Hours 15: 1300; Hours 16: 1500; Hours 17: 1400; Hours 18: 1500; Hours 19: 1200; Hours 0: 1200; Hours 1: 1500; Hours 2: 1400; Hours 3: 900 | 14800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 13: 0.60556; Hours 14: 0.68698; Hours 15: 0.60427; Hours 16: 0.7078; Hours 17: 0.62286; Hours 18: 0.66735; Hours 19: 0.54162; Hours 0: 0.50502; Hours 1: 0.66735; Hours 2: 0.64118; Hours 3: 0.43121 | 0.60738
17 | Average iKW/TR |  |  | Hours 7: 0.60738 | 0.60738
18 | COP of chiller |  |  | Hours 13: 5.8062; Hours 14: 5.118; Hours 15: 5.8186; Hours 16: 4.9675; Hours 17: 5.6449; Hours 18: 5.2686; Hours 19: 6.4916; Hours 0: 6.962; Hours 1: 5.2686; Hours 2: 5.4836; Hours 3: 8.1537 | 5.9076
19 | EER of Chiller |  |  | Hours 13: 19.8165; Hours 14: 17.4679; Hours 15: 19.8588; Hours 16: 16.9541; Hours 17: 19.266; Hours 18: 17.9816; Hours 19: 22.156; Hours 0: 23.7615; Hours 1: 17.9816; Hours 2: 18.7156; Hours 3: 27.8287 | 20.1626
20 | LMTD of Condenser | ºC |  | Hours 13: 3.2586; Hours 14: 3.1371; Hours 15: 3.1064; Hours 16: 2.9189; Hours 17: 3.1981; Hours 18: 3.1676; Hours 19: 3.1371; Hours 0: 3.4163; Hours 1: 3.1981; Hours 2: 3.1064; Hours 3: 2.9189 | 3.1421
21 | LMTD of Evaporator | ºC |  | Hours 13: 4.718; Hours 14: 3.8469; Hours 15: 3.8168; Hours 16: 4.0388; Hours 17: 4.1623; Hours 18: 4.1623; Hours 19: 4.0052; Hours 0: 4.7817; Hours 1: 4.2874; Hours 2: 4.1008; Hours 3: 2.9398 | 4.0782

## 03-03-2023
Performance Sheet Chiller
Date :- 03/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4 | 4 | 3.9 | 4 | 3.8 | 3.7 | 3.6 | 3.5 | 3.4 | 3.4 | 3.8 | 3.9 | 3.6 | 3.6 | 3.6 | 4.1 | 3.8 | 3.9 | 3.6 | 3.3 | 3.4 | 3.5 | 4.1 | 4.1 | 3.7333 | 110
2 | Small temperature difference of evaporator | ºC |  | 1 | 1 | 1.1 | 0.9 | 0.8 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 1 | 0.9 | 0.8 | 0.9 | 0.4 | 0.6 | 0.8 | 0.9 | 0.9 | 0.76667 | 850
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.2 | 14.4 | 14.9 | 15.2 | 15.5 | 15.8 | 14.8 | 14.4 | 14.3 | 14.2 | 13.8 | 13.6 | 12.8 | 12.8 | 13.9 | 14.4 | 15.1 | 14.9 | 13.1 | 12.2 | 12.8 | 13.6 | 14.2 | 14.5 | 14.1417
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.2 | 6.3 | 6.8 | 7.1 | 7.2 | 7.8 | 7.3 | 7.2 | 7.2 | 7 | 6.2 | 5.6 | 5.5 | 5.7 | 6.1 | 6.3 | 7.1 | 6.9 | 5.5 | 5.4 | 5.6 | 5.8 | 6.1 | 6.2 | 6.4208
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.1 | 21.3 | 22.1 | 22.4 | 23.2 | 23.5 | 24.6 | 25.3 | 25.4 | 24.1 | 23.4 | 22.8 | 22.6 | 22.1 | 22.1 | 22.3 | 22.7 | 23.4 | 23.3 | 23.8 | 22.4 | 22.4 | 22.4 | 22.7 | 22.975
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 25.8 | 26.3 | 26.8 | 27.6 | 28.5 | 28.4 | 29.6 | 29.8 | 29.8 | 28.4 | 27.9 | 27.6 | 26.9 | 26.5 | 27 | 27.3 | 27.8 | 28.4 | 28.1 | 27.8 | 26.7 | 27.5 | 27.6 | 27.9 | 27.75
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2600.8929 | 2600.8929 | 2600.8929 | 2665.1124 | 2568.7831 | 2408.2341 | 2311.9048 | 2279.795 | 2311.9048 | 2440.3439 | 2568.7831 | 2344.0146 | 2279.795 | 2504.5635 | 2600.8929 | 2568.7831 | 2568.7831 | 2440.3439 | 2183.4656 | 2311.9048 | 2504.5635 | 2600.8929 | 2665.1124 | 59499.4378
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1500 | 1400 | 1500 | 1500 | 1400 | 1500 | 1400 | 1400 | 1400 | 1400 | 1300 | 1500 | 1500 | 1400 | 1600 | 1400 | 1300 | 1300 | 1400 | 1600 | 1600 | 1500 | 34800
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58393 | 0.57673 | 0.57673 | 0.53828 | 0.56283 | 0.58393 | 0.58134 | 0.64882 | 0.61409 | 0.60556 | 0.57369 | 0.54501 | 0.5546 | 0.65795 | 0.59891 | 0.53828 | 0.62286 | 0.54501 | 0.53271 | 0.59538 | 0.60556 | 0.63883 | 0.61517 | 0.56283 | 0.58579
17 | Average iKW/TR |  |  | Hours 7: 0.58579 | 0.58579
18 | COP of chiller |  |  | 6.0212 | 6.0965 | 6.0965 | 6.532 | 6.247 | 6.0212 | 6.0481 | 5.4191 | 5.7255 | 5.8062 | 6.1287 | 6.4513 | 6.3397 | 5.3438 | 5.8707 | 6.532 | 5.6449 | 6.4513 | 6.6002 | 5.9054 | 5.8062 | 5.5038 | 5.7155 | 6.247 | 6.0231
19 | EER of Chiller |  |  | 20.5504 | 20.8073 | 20.8073 | 22.2936 | 21.3211 | 20.5504 | 20.6422 | 18.4954 | 19.5413 | 19.8165 | 20.9174 | 22.0183 | 21.6373 | 18.2385 | 20.0367 | 22.2936 | 19.266 | 22.0183 | 22.5265 | 20.1552 | 19.8165 | 18.7844 | 19.5069 | 21.3211 | 20.5568
20 | LMTD of Condenser | ºC |  | 6.0487 | 6.1658 | 5.9435 | 6.2432 | 6.0691 | 5.8096 | 5.7417 | 5.4435 | 5.299 | 5.2603 | 5.76 | 5.9825 | 5.4712 | 5.5103 | 5.7034 | 6.2713 | 5.9926 | 6.0601 | 5.6651 | 5.0381 | 5.2603 | 5.673 | 6.349 | 6.349 | 5.7962
21 | LMTD of Evaporator | ºC |  | 3.641 | 3.668 | 3.8138 | 3.5178 | 3.4136 | 3.4913 | 2.8816 | 2.8071 | 2.7821 | 2.8071 | 3.0733 | 3.0046 | 2.832 | 2.7821 | 2.9556 | 3.668 | 3.4913 | 3.3363 | 3.3847 | 2.3526 | 2.8071 | 3.2843 | 3.5178 | 3.5706 | 3.2035
Performance Sheet Chiller
Date :- 03/03/2023
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 12: 1.2; Hours 13: 1.1; Hours 14: 1.1; Hours 15: 1.1; Hours 16: 1.1; Hours 17: 1.2; Hours 18: 1.2; Hours 19: 1.3; Hours 0: 1.3; Hours 1: 1.2; Hours 2: 1.2 | 1.1818
2 | Small temperature difference of evaporator | ºC |  | Hours 12: 1.8; Hours 13: 1.6; Hours 14: 0.8; Hours 15: 1.9; Hours 16: 1.4; Hours 17: 1.7; Hours 18: 1.6; Hours 19: 1.6; Hours 0: 1.8; Hours 1: 1.6; Hours 2: 0.8 | 1.5091
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 12: 15.7; Hours 13: 14.8; Hours 14: 14.4; Hours 15: 14.3; Hours 16: 14.2; Hours 17: 13.8; Hours 18: 13.4; Hours 19: 12.8; Hours 0: 14.9; Hours 1: 13.2; Hours 2: 12.2 | 13.9727
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 12: 8.7; Hours 13: 8.1; Hours 14: 7.6; Hours 15: 7.4; Hours 16: 7.4; Hours 17: 6.6; Hours 18: 5.9; Hours 19: 5.5; Hours 0: 7.4; Hours 1: 5.9; Hours 2: 5.3 | 6.8909
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 12: 23.3; Hours 13: 24.7; Hours 14: 25.2; Hours 15: 25.4; Hours 16: 24.2; Hours 17: 23.2; Hours 18: 22.8; Hours 19: 22.6; Hours 0: 23.3; Hours 1: 23.4; Hours 2: 23.3 | 23.7636
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 12: 28.8; Hours 13: 29.9; Hours 14: 30.3; Hours 15: 30.3; Hours 16: 29.3; Hours 17: 28.7; Hours 18: 28.5; Hours 19: 28.1; Hours 0: 29.3; Hours 1: 28.9; Hours 2: 28.4 | 29.1364
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 12: 4.3; Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 0: 4.3; Hours 1: 4.3; Hours 2: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 12: 2247.6852; Hours 13: 2151.3558; Hours 14: 2183.4656; Hours 15: 2215.5754; Hours 16: 2183.4656; Hours 17: 2311.9048; Hours 18: 2408.2341; Hours 19: 2344.0146; Hours 0: 2408.2341; Hours 1: 2344.0146; Hours 2: 2215.5754 | 25013.5251
15 | Power Consumption of Chiller | KWH |  | Hours 12: 1000; Hours 13: 1500; Hours 14: 1400; Hours 15: 1400; Hours 16: 1500; Hours 17: 1400; Hours 18: 1600; Hours 19: 1000; Hours 0: 1700; Hours 1: 1500; Hours 2: 1100 | 15100
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 12: 0.4449; Hours 13: 0.69723; Hours 14: 0.64118; Hours 15: 0.63189; Hours 16: 0.68698; Hours 17: 0.60556; Hours 18: 0.66439; Hours 19: 0.42662; Hours 0: 0.70591; Hours 1: 0.63993; Hours 2: 0.49649 | 0.60373
17 | Average iKW/TR |  |  | Hours 7: 0.60373 | 0.60373
18 | COP of chiller |  |  | Hours 12: 7.9029; Hours 13: 5.0428; Hours 14: 5.4836; Hours 15: 5.5643; Hours 16: 5.118; Hours 17: 5.8062; Hours 18: 5.2921; Hours 19: 8.2416; Hours 0: 4.9808; Hours 1: 5.4944; Hours 2: 7.0818 | 6.0008
19 | EER of Chiller |  |  | Hours 12: 26.9725; Hours 13: 17.211; Hours 14: 18.7156; Hours 15: 18.9908; Hours 16: 17.4679; Hours 17: 19.8165; Hours 18: 18.0619; Hours 19: 28.1284; Hours 0: 16.9995; Hours 1: 18.7523; Hours 2: 24.1701 | 20.4806
20 | LMTD of Condenser | ºC |  | Hours 12: 3.1981; Hours 13: 2.9795; Hours 14: 2.9493; Hours 15: 2.8884; Hours 16: 2.9493; Hours 17: 3.1981; Hours 18: 3.2586; Hours 19: 3.3241; Hours 0: 3.4772; Hours 1: 3.1981; Hours 2: 3.0756 | 3.136
21 | LMTD of Evaporator | ºC |  | Hours 12: 4.4109; Hours 13: 4.0699; Hours 14: 3.0205; Hours 15: 4.5013; Hours 16: 3.8469; Hours 17: 4.3493; Hours 18: 4.3146; Hours 19: 4.254; Hours 0: 4.567; Hours 1: 4.254; Hours 2: 3.0472 | 4.0578

## 04-03-2023
Performance Sheet Chiller
Date :- 04/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4.3 | 3.7 | 3.3 | 3.9 | 3.9 | 4 | 4 | 4.1 | 3.9 | 3.7 | 3.9 | 3.7 | 3.8 | 4 | 4.1 | 4.1 | 3.7 | 3.7 | 3.7 | 3.5 | 3.5 | 3.7 | 3.2 | 3.9 | 3.8042
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 0.5 | 0.5 | 0.7 | 0.8 | 0.7 | 0.7 | 1.1 | 0.9 | 0.6 | 0.7 | 0.7 | 0.6 | 0.7 | 0.8 | 0.8 | 0.6 | 0.7 | 0.6 | 0.6 | 0.7 | 0.6 | 0.4 | 0.6 | 0.6875
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.6 | 12.9 | 12.2 | 13.6 | 14.4 | 14.9 | 15.8 | 16.5 | 15.3 | 14.6 | 14 | 13.4 | 13 | 13.6 | 14.9 | 15.9 | 16.1 | 14.9 | 14.1 | 13.7 | 13.7 | 13.5 | 13.3 | 13.2 | 14.2542
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.4 | 5.5 | 5.4 | 5.8 | 6.4 | 6.9 | 7.8 | 8.3 | 7.4 | 7.1 | 6.2 | 6 | 5.6 | 5.8 | 6.9 | 7.7 | 8 | 7.2 | 6.9 | 7.1 | 6.9 | 7.1 | 7.1 | 5.5 | 6.7083
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.1 | 22.8 | 22.8 | 23.2 | 23.1 | 23.4 | 25 | 25.2 | 24.7 | 24.1 | 23.8 | 23.5 | 24.7 | 24.3 | 24.7 | 25.1 | 25.2 | 24.7 | 24.7 | 23.9 | 23.9 | 24 | 23.6 | 23.3 | 24.0333
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.1 | 27.2 | 26.8 | 28.1 | 27.8 | 28.4 | 29.9 | 30.1 | 29.3 | 28.5 | 28.6 | 27.8 | 29.1 | 28.9 | 29.5 | 30.1 | 29.9 | 29.2 | 28.7 | 27.8 | 27.7 | 27.7 | 27.1 | 27.8 | 28.5042
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2633.0026 | 2376.1243 | 2183.4656 | 2504.5635 | 2568.7831 | 2568.7831 | 2568.7831 | 2633.0026 | 2536.6733 | 2408.2341 | 2504.5635 | 2376.1243 | 2376.1243 | 2504.5635 | 2568.7831 | 2633.0026 | 2600.8929 | 2472.4537 | 2311.9048 | 2119.246 | 2183.4656 | 2055.0265 | 1990.8069 | 2472.4537 | 58150.8267
15 | Power Consumption of Chiller | KWH |  | 1500 | 1200 | 1500 | 1400 | 1600 | 1400 | 1500 | 1500 | 1400 | 1500 | 1400 | 1400 | 1400 | 1500 | 1600 | 1400 | 1600 | 1300 | 1200 | 1200 | 1200 | 1200 | 1400 | 1400 | 33700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.56969 | 0.50502 | 0.68698 | 0.55898 | 0.62286 | 0.54501 | 0.58393 | 0.56969 | 0.5519 | 0.62286 | 0.55898 | 0.58919 | 0.58919 | 0.59891 | 0.62286 | 0.53171 | 0.61517 | 0.52579 | 0.51905 | 0.56624 | 0.54959 | 0.58393 | 0.70323 | 0.56624 | 0.58071
17 | Average iKW/TR |  |  | Hours 7: 0.58071 | 0.58071
18 | COP of chiller |  |  | 6.1718 | 6.962 | 5.118 | 6.29 | 5.6449 | 6.4513 | 6.0212 | 6.1718 | 6.3707 | 5.6449 | 6.29 | 5.9675 | 5.9675 | 5.8707 | 5.6449 | 6.6126 | 5.7155 | 6.687 | 6.7739 | 6.2094 | 6.3976 | 6.0212 | 4.9998 | 6.2094 | 6.0922
19 | EER of Chiller |  |  | 21.0642 | 23.7615 | 17.4679 | 21.4679 | 19.266 | 22.0183 | 20.5504 | 21.0642 | 21.7431 | 19.266 | 21.4679 | 20.367 | 20.367 | 20.0367 | 19.266 | 22.5688 | 19.5069 | 22.8229 | 23.1193 | 21.1927 | 21.8349 | 20.5504 | 17.0642 | 21.1927 | 20.7928
20 | LMTD of Condenser | ºC |  | 6.4817 | 5.6156 | 5.0381 | 6.0213 | 5.9435 | 6.1658 | 6.1269 | 6.2322 | 5.9043 | 5.6156 | 5.9825 | 5.5764 | 5.7207 | 6.0094 | 6.193 | 6.2713 | 5.7324 | 5.6547 | 5.4579 | 5.2089 | 5.1693 | 5.338 | 4.7364 | 5.8651 | 5.7525
21 | LMTD of Evaporator | ºC |  | 3.5442 | 2.6811 | 2.5363 | 3.1241 | 3.3363 | 3.1746 | 3.1746 | 3.8413 | 3.4647 | 2.8816 | 3.1241 | 3.0222 | 2.8568 | 3.1241 | 3.3363 | 3.3879 | 3.029 | 3.0987 | 2.8071 | 2.656 | 2.8673 | 2.6051 | 2.2116 | 2.931 | 3.034
Performance Sheet Chiller
Date :- 04/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.3 | [5 empty] | 1.3 | 1.1 | 0.9 | 1.5 | 1.5 | 1.1 |  |  |  | 1.1 | 1.1 | 1.1 | 1 | 1 | 1.2 | 1 | 1.5 | 1.1812
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.8 | [5 empty] | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 |  |  |  | 0.6 | 0.7 | 0.7 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.65
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.6 | 14.7 | [5 empty] | 15.7 | 16.4 | 15.4 | 14.3 | 13.9 | 13.3 |  |  |  | 15.9 | 15.9 | 14.9 | 13.9 | 13.7 | 13.5 | 13.3 | 13.2 | 13.2
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.2 | 6.8 | [5 empty] | 9 | 8.2 | 7.3 | 6.9 | 6.1 | 6 |  |  |  | 8.8 | 8.8 | 7 | 7 | 6.9 | 7.1 | 6.9 | 7.1 | 5.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.3 | 22.7 | [5 empty] | 20.2 | 24.9 | 24.4 | 23.8 | 23.8 | 23.2 |  |  |  | 21.3 | 25 | 24.4 | 24.6 | 23.8 | 23.8 | 23.8 | 23.4 | 23.1
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 23.7 | 28.9 | [5 empty] | 23.8 | 31.2 | 30.6 | 29.5 | 29.4 | 28.8 |  |  |  | 25.4 | 30.6 | 30.4 | 29.7 | 28.7 | 28.6 | 28.8 | 28.2 | 28.8
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | [5 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | [5 empty] | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | [5 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | [5 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | [5 empty] | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2697.2222 | 2536.6733 | [5 empty] | 2151.3558 | 2633.0026 | 2600.8929 | 2376.1243 | 2504.5635 | 2344.0146 |  |  |  | 2279.795 | 2279.795 | 2536.6733 | 2215.5754 | 2183.4656 | 2055.0265 | 2055.0265 | 1958.6971 | 37407.9034
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | [5 empty] | 1100 | 1500 | 1500 | 1400 | 1300 | 1500 |  |  |  | 1000 | 1600 | 1400 | 1200 | 1300 | 1200 | 1300 | 1400 | 21700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.55613 | 0.59133 | [5 empty] | 0.51131 | 0.56969 | 0.57673 | 0.58919 | 0.51905 | 0.63993 |  |  |  | 0.43864 | 0.70182 | 0.5519 | 0.54162 | 0.59538 | 0.58393 | 0.6326 | 0.71476 | 0.58213
17 | Average iKW/TR |  |  | Hours 7: 0.58213 | 0.58213
18 | COP of chiller |  |  | 6.3223 | 5.946 | [5 empty] | 6.8765 | 6.1718 | 6.0965 | 5.9675 | 6.7739 | 5.4944 |  |  |  | 8.0158 | 5.0098 | 6.3707 | 6.4916 | 5.9054 | 6.0212 | 5.5581 | 4.9191 | 6.1213
19 | EER of Chiller |  |  | 21.578 | 20.2936 | [5 empty] | 23.4695 | 21.0642 | 20.8073 | 20.367 | 23.1193 | 18.7523 |  |  |  | 27.3578 | 17.0986 | 21.7431 | 22.156 | 20.1552 | 20.5504 | 18.9696 | 16.789 | 20.8919
20 | LMTD of Condenser | ºC |  | 3.54 | 3.5377 | [5 empty] | 2.7132 | 3.3051 | 3.0018 | 3.6338 | 3.6021 | 3.0994 |  |  |  | 2.6395 | 3.0994 | 3.2175 | 2.8203 | 2.7606 | 2.9824 | 2.7906 | 3.3448 | 3.1305
21 | LMTD of Evaporator | ºC |  | 4.0395 | 3.3103 | [5 empty] | 2.8412 | 3.0533 | 3.029 | 3.0222 | 3.1241 | 2.832 |  |  |  | 2.7821 | 2.9451 | 3.1494 | 2.7319 | 2.7067 | 2.7625 | 2.6051 | 2.528 | 2.9664

## 05-03-2023
Performance Sheet Chiller
Date :- 05/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4.2 | 4.2 | 4.2 | 4.6 | 4.3 | 4.2 | 3.8 | 3.6 | 3.5 | 3.6 | 4.1 | 4 | 4.1 | 4.2 | 4.5 | 4.3 | 4.3 | 3.4 | 3.7 | 3.7 | 3.5 | 3.6 | 3.5 | 3.3 | 3.9333
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.8 | 0.8 | 0.9 | 1.1 | 0.8 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.63333
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 12.5 | 13.8 | 14.7 | 15.4 | 15.8 | 15.7 | 14.3 | 13.8 | 13.8 | 14.2 | 14.1 | 13.8 | 13.6 | 14 | 15.4 | 16.3 | 16.4 | 14.9 | 14.1 | 13.7 | 13.7 | 13.7 | 13.4 | 13.3 | 14.35
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.4 | 5.8 | 6.5 | 7.1 | 7.7 | 7.6 | 6.9 | 7.1 | 7.2 | 7.1 | 6.3 | 6 | 5.9 | 6.1 | 7.4 | 8 | 8.1 | 7.1 | 7.1 | 7.1 | 7 | 7 | 7.1 | 7 | 6.9
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.8 | 22.7 | 23.7 | 23.4 | 23.1 | 23.3 | 22.9 | 23.1 | 25.3 | 25.2 | 24.8 | 24.5 | 24.6 | 24.6 | 24.8 | 24.6 | 24.7 | 24.2 | 24.2 | 24.1 | 24.1 | 23.8 | 23.2 | 22.6 | 23.9292
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.9 | 27.6 | 28.7 | 28.6 | 28.2 | 28.3 | 27.4 | 27.2 | 29.1 | 29.1 | 29.5 | 29.1 | 29.2 | 29.3 | 29.7 | 29.7 | 29.7 | 28.8 | 28.4 | 27.9 | 27.8 | 27.6 | 26.9 | 26.2 | 28.3708
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2279.795 | 2568.7831 | 2633.0026 | 2665.1124 | 2600.8929 | 2600.8929 | 2376.1243 | 2151.3558 | 2119.246 | 2279.795 | 2504.5635 | 2504.5635 | 2472.4537 | 2536.6733 | 2568.7831 | 2665.1124 | 2665.1124 | 2504.5635 | 2247.6852 | 2119.246 | 2151.3558 | 2151.3558 | 2022.9167 | 2022.9167 | 57412.3016
15 | Power Consumption of Chiller | KWH |  | 1400 | 1500 | 1500 | 1500 | 1600 | 1300 | 1200 | 1300 | 1400 | 1600 | 1400 | 1500 | 1500 | 1500 | 1600 | 1500 | 1500 | 1200 | 1300 | 1300 | 1200 | 1200 | 1100 | 1200 | 33300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.61409 | 0.58393 | 0.56969 | 0.56283 | 0.61517 | 0.49983 | 0.50502 | 0.60427 | 0.66061 | 0.70182 | 0.55898 | 0.59891 | 0.60668 | 0.59133 | 0.62286 | 0.56283 | 0.56283 | 0.47913 | 0.57837 | 0.61343 | 0.55779 | 0.55779 | 0.54377 | 0.5932 | 0.58105
17 | Average iKW/TR |  |  | Hours 7: 0.58105 | 0.58105
18 | COP of chiller |  |  | 5.7255 | 6.0212 | 6.1718 | 6.247 | 5.7155 | 7.0344 | 6.962 | 5.8186 | 5.3223 | 5.0098 | 6.29 | 5.8707 | 5.7954 | 5.946 | 5.6449 | 6.247 | 6.247 | 7.3384 | 6.0791 | 5.7317 | 6.3035 | 6.3035 | 6.466 | 5.9271 | 6.0924
19 | EER of Chiller |  |  | 19.5413 | 20.5504 | 21.0642 | 21.3211 | 19.5069 | 24.0085 | 23.7615 | 19.8588 | 18.1651 | 17.0986 | 21.4679 | 20.0367 | 19.7798 | 20.2936 | 19.266 | 21.3211 | 21.3211 | 25.0459 | 20.748 | 19.5624 | 21.5138 | 21.5138 | 22.0684 | 20.2293 | 20.7935
20 | LMTD of Condenser | ºC |  | 6.019 | 6.3374 | 6.3766 | 6.8753 | 6.5209 | 6.3766 | 5.76 | 5.3927 | 5.1693 | 5.3136 | 6.1537 | 6.0094 | 6.1143 | 6.2586 | 6.6519 | 6.5209 | 6.4817 | 5.3759 | 5.537 | 5.3781 | 5.1295 | 5.2738 | 5.1295 | 4.8807 | 5.8765
21 | LMTD of Evaporator | ºC |  | 3.1004 | 3.3363 | 3.3879 | 3.5706 | 3.8138 | 3.3621 | 2.6811 | 2.6814 | 2.656 | 2.7821 | 3.1241 | 3.1241 | 2.931 | 3.1494 | 3.1746 | 3.2499 | 3.0776 | 2.9556 | 2.3991 | 2.3059 | 2.3293 | 2.3293 | 2.2353 | 2.2353 | 2.9163
Performance Sheet Chiller
Date :- 05/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [6 empty] | 1.3 | 1.3 | 1.2 | 1.3 | 1.2 | 1.3 | 1.3 | 1.2 |  |  |  | 1.3 | 1.5 | 1.2 | 1.2 | 1.2 | 0.9 | 1.2 | 1.2 | 1.2375
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.7 | 0.6 | 0.5 | 0.6 | 0.7 | 0.7 | 0.6 | 0.6 |  |  |  | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.5 | 0.4 | 0.60625
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 15.8 | 14.3 | 13.6 | 13.9 | 14.1 | 14 | 13.8 | 13.4 |  |  |  | 16.3 | 14.8 | 13.9 | 13.9 | 13.7 | 13.6 | 13.4 | 13.2 | 14.1063
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 7.4 | 7.1 | 7 | 6.9 | 6.9 | 6.2 | 6.1 | 6.1 |  |  |  | 8.3 | 7.1 | 7.1 | 7.2 | 7 | 7.1 | 7.1 | 7.1 | 6.9812
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 23.2 | 23 | 23.1 | 25.2 | 24.9 | 24.7 | 24.2 | 24.3 |  |  |  | 24.6 | 23.9 | 24 | 23.8 | 24 | 23.6 | 22.8 | 22.4 | 23.8563
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 29.5 | 28.2 | 28.1 | 30.1 | 30.4 | 30.8 | 30.1 | 29.9 |  |  |  | 30.7 | 30.2 | 29.3 | 29.1 | 28.6 | 28.2 | 27.7 | 26.9 | 29.2375
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 2697.2222 | 2311.9048 | 2119.246 | 2247.6852 | 2311.9048 | 2504.5635 | 2472.4537 | 2344.0146 |  |  |  | 2568.7831 | 2472.4537 | 2183.4656 | 2151.3558 | 2151.3558 | 2087.1362 | 2022.9167 | 1958.6971 | 36605.1587
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 400 | 1600 | 1400 | 1200 | 1400 | 1500 | 1500 | 1600 | 1000 | 0 | 400 | 1600 | 1500 | 1300 | 1300 | 1300 | 1300 | 1200 | 1100 | 1300 | 23900
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.5932 | 0.60556 | 0.56624 | 0.62286 | 0.64882 | 0.59891 | 0.64713 | 0.42662 |  |  |  | 0.58393 | 0.52579 | 0.59538 | 0.60427 | 0.60427 | 0.57495 | 0.54377 | 0.66371 | 0.58784
17 | Average iKW/TR |  |  | Hours 7: 0.58784 | 0.58784
18 | COP of chiller | [7 empty] | 5.9271 | 5.8062 | 6.2094 | 5.6449 | 5.4191 | 5.8707 | 5.4332 | 8.2416 |  |  |  | 6.0212 | 6.687 | 5.9054 | 5.8186 | 5.8186 | 6.1153 | 6.466 | 5.2975 | 6.0426
19 | EER of Chiller | [7 empty] | 20.2293 | 19.8165 | 21.1927 | 19.266 | 18.4954 | 20.0367 | 18.5436 | 28.1284 |  |  |  | 20.5504 | 22.8229 | 20.1552 | 19.8588 | 19.8588 | 20.8716 | 22.0684 | 18.0804 | 20.6235
20 | LMTD of Condenser | ºC | [6 empty] | 3.5678 | 3.2309 | 3.0446 | 3.1366 | 3.1981 | 3.5075 | 3.4468 | 3.2284 |  |  |  | 3.5075 | 3.8213 | 3.1371 | 3.1371 | 2.9196 | 2.5413 | 3.0136 | 2.8881 | 3.2079
21 | LMTD of Evaporator | ºC | [6 empty] | 3.2749 | 2.8071 | 2.4875 | 2.757 | 2.9709 | 3.1241 | 2.931 | 2.832 |  |  |  | 3.1746 | 2.931 | 2.7067 | 2.6814 | 2.6814 | 2.7888 | 2.4137 | 2.1879 | 2.7969
27.4

## 06-03-2023
Performance Sheet Chiller
Date :- 06/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 3.3 | 4 | 3.8 | 3.9 | 4.6 | 4.6 | 3.8 | 4.3 | 4 | 3.9 | 3.9 | 4.1 | 4.1 | 4.3 | 4.1 | 4.8 | 4.8 | 4.7 | 4.3 | 3.7 | 3.9 | 4.3 | 4.5 | 4.7 | 4.1833
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.8 | 0.7 | 0.8 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.9 | 1.1 | 1 | 0.7 | 0.4 | 0.7 | 0.9 | 1 | 0.9 | 0.71667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.3 | 12.9 | 12.4 | 13.9 | 14.4 | 15.1 | 15.6 | 16.1 | 14.7 | 13.9 | 13.5 | 12.9 | 12.3 | 13.6 | 14.7 | 15.3 | 15.4 | 14.7 | 13.1 | 11.9 | 12.7 | 13.7 | 14.1 | 14.3 | 13.9375
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7 | 5.3 | 5.5 | 5.8 | 6.3 | 6.7 | 7.3 | 7.9 | 7 | 6.9 | 5.8 | 5.6 | 5.5 | 5.7 | 6.4 | 6.8 | 7 | 6.4 | 5.3 | 5.3 | 5.7 | 5.7 | 5.7 | 6 | 6.1917
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.1 | 22.1 | 21.7 | 21.6 | 21.8 | 22.6 | 22.9 | 23.6 | 23.1 | 23.4 | 23.7 | 22.6 | 22.4 | 23.2 | 21.8 | 21.8 | 21.6 | 21.8 | 21.4 | 21 | 20.8 | 21.1 | 20.9 | 21.1 | 22.0875
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 25.6 | 26.6 | 25.7 | 26.5 | 27 | 27.8 | 27.9 | 28.6 | 27.5 | 27.7 | 28.3 | 26.9 | 26.3 | 27.7 | 27 | 26.8 | 29 | 26.9 | 26.1 | 24.9 | 24.9 | 25.7 | 26.1 | 26 | 26.8125
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2022.9167 | 2440.3439 | 2215.5754 | 2600.8929 | 2600.8929 | 2697.2222 | 2665.1124 | 2633.0026 | 2472.4537 | 2247.6852 | 2472.4537 | 2344.0146 | 2183.4656 | 2536.6733 | 2665.1124 | 2729.332 | 2697.2222 | 2665.1124 | 2504.5635 | 2119.246 | 2247.6852 | 2568.7831 | 2697.2222 | 2665.1124 | 59692.0966
15 | Power Consumption of Chiller | KWH |  | 1400 | 1300 | 1400 | 1500 | 1500 | 1500 | 1500 | 1400 | 1300 | 1500 | 1400 | 1300 | 1500 | 1500 | 1500 | 1500 | 1700 | 1300 | 1200 | 1200 | 1500 | 1500 | 1500 | 1400 | 34300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.69207 | 0.53271 | 0.63189 | 0.57673 | 0.57673 | 0.55613 | 0.56283 | 0.53171 | 0.52579 | 0.66735 | 0.56624 | 0.5546 | 0.68698 | 0.59133 | 0.56283 | 0.54959 | 0.63028 | 0.48778 | 0.47913 | 0.56624 | 0.66735 | 0.58393 | 0.55613 | 0.52531 | 0.57757
17 | Average iKW/TR |  |  | Hours 7: 0.57757 | 0.57757
18 | COP of chiller |  |  | 5.0804 | 6.6002 | 5.5643 | 6.0965 | 6.0965 | 6.3223 | 6.247 | 6.6126 | 6.687 | 5.2686 | 6.2094 | 6.3397 | 5.118 | 5.946 | 6.247 | 6.3976 | 5.5785 | 7.2081 | 7.3384 | 6.2094 | 5.2686 | 6.0212 | 6.3223 | 6.6932 | 6.1447
19 | EER of Chiller |  |  | 17.3394 | 22.5265 | 18.9908 | 20.8073 | 20.8073 | 21.578 | 21.3211 | 22.5688 | 22.8229 | 17.9816 | 21.1927 | 21.6373 | 17.4679 | 20.2936 | 21.3211 | 21.8349 | 19.0394 | 24.6013 | 25.0459 | 21.1927 | 17.9816 | 20.5504 | 21.578 | 22.844 | 20.9718
20 | LMTD of Condenser | ºC |  | 4.8409 | 5.97 | 5.5623 | 6.0213 | 6.8753 | 6.8753 | 5.9541 | 6.4817 | 5.9304 | 5.7861 | 5.9043 | 5.9952 | 5.8344 | 6.2837 | 6.349 | 7.0051 | 7.9329 | 6.9405 | 6.3633 | 5.4181 | 5.7066 | 6.3236 | 6.7704 | 6.8608 | 6.2494
21 | LMTD of Evaporator | ºC |  | 2.5795 | 2.7289 | 2.5607 | 2.8472 | 3.5178 | 3.5969 | 3.4136 | 3.2249 | 3.2583 | 2.5849 | 2.7527 | 2.832 | 2.7067 | 2.9801 | 3.0776 | 3.6231 | 3.8961 | 3.7219 | 3.1241 | 2.3059 | 2.9192 | 3.4913 | 3.7488 | 3.5706 | 3.1276
Performance Sheet Chiller
Date :- 06/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.2; Hours 14: 1.3; Hours 15: 1.3; Hours 16: 1.3; Hours 17: 1.3; Hours 0: 1.6 | 1.3333
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.4; Hours 14: 1.3; Hours 15: 0.9; Hours 16: 0.6; Hours 17: 0.6; Hours 0: 0.7 | 0.75
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 13.4; Hours 14: 15.8; Hours 15: 14.2; Hours 16: 13.8; Hours 17: 13.1; Hours 23: 15.4; Hours 0: 14.7 | 14.3429
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 6.5; Hours 14: 9.1; Hours 15: 8.2; Hours 16: 8; Hours 17: 7.4; Hours 23: 6.3; Hours 0: 6.3 | 7.4
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 22; Hours 14: 23.7; Hours 15: 22.9; Hours 16: 23.2; Hours 17: 23.8; Hours 23: 21.1; Hours 0: 21.6 | 22.6143
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 26.9; Hours 14: 29.9; Hours 15: 28.6; Hours 16: 28.6; Hours 17: 29.3; Hours 23: 28.1; Hours 0: 28.1 | 28.5
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 23: 4.3; Hours 0: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 23: 3.8; Hours 0: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 23: 3.8; Hours 0: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 23: 3; Hours 0: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 23: 0.5; Hours 0: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 23: 0.8; Hours 0: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 23: 971; Hours 0: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2215.5754; Hours 14: 2151.3558; Hours 15: 1926.5873; Hours 16: 1862.3677; Hours 17: 1830.2579; Hours 23: 2921.9907; Hours 0: 2697.2222 | 15605.3571
15 | Power Consumption of Chiller | KWH |  | 1400 | 200 | 0 | 0 | 0 | 400 | 1600 | 1300 | 1400 | 1500 | 1600 | 700 | 0 | 0 | 0 | 600 | 1700 | 1400 | 700 | 0 | 0 | 0 | 0 | 400 | 14900
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.63189; Hours 14: 0.60427; Hours 15: 0.72667; Hours 16: 0.80543; Hours 17: 0.87419; Hours 23: 0.5818; Hours 0: 0.51905 | 0.67761
17 | Average iKW/TR |  |  | Hours 7: 0.67761 | 0.67761
18 | COP of chiller |  |  | Hours 7: 5.5643; Hours 14: 5.8186; Hours 15: 4.8385; Hours 16: 4.3654; Hours 17: 4.022; Hours 23: 6.0434; Hours 0: 6.7739 | 5.3466
19 | EER of Chiller |  |  | Hours 7: 18.9908; Hours 14: 19.8588; Hours 15: 16.5138; Hours 16: 14.8991; Hours 17: 13.7271; Hours 23: 20.626; Hours 0: 23.1193 | 18.2478
20 | LMTD of Condenser | ºC |  | Hours 7: 3.0136; Hours 14: 3.5377; Hours 15: 3.3857; Hours 16: 3.2932; Hours 17: 3.3241; Hours 23: 4.0077; Hours 0: 4.0077 | 3.51
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.3759; Hours 14: 3.6872; Hours 15: 2.9457; Hours 16: 2.4502; Hours 17: 2.4241; Hours 23: 3.2749; Hours 0: 3.2749 | 2.919

## 07-03-2023
Performance Sheet Chiller
Date :- 07/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4.5 | 4.6 | 4 | 4.2 | 4.6 | 4.7 | 4.6 | 4.6 | 4.5 | 4.1 | 4 | 4 | 4.2 | 4.2 | 4.6 | 4.5 | 4.4 | 3.8 | 4 | 3.8 | 3.5 | 3.8 | 3.7 | 3.6 | 4.1875
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 0.9 | 0.5 | 0.5 | 0.8 | 0.9 | 0.8 | 0.8 | 0.6 | 0.5 | 0.6 | 0.4 | 0.7 | 0.7 | 0.7 | 0.9 | 0.9 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.63333
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.7 | 13.8 | 12.8 | 12.9 | 13.8 | 14.3 | 14.8 | 15.1 | 15.2 | 13.9 | 13.2 | 12.6 | 12.6 | 14.4 | 15.4 | 16 | 15.8 | 14.3 | 13.2 | 12.2 | 11.6 | 12.8 | 13.7 | 13.7 | 13.8667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.2 | 5.9 | 5.4 | 5.7 | 5.8 | 6.1 | 6.4 | 7.1 | 7.2 | 6.9 | 5.5 | 5.4 | 5.6 | 6.5 | 7 | 7.7 | 7.6 | 6.8 | 5.4 | 5.4 | 5.5 | 5.7 | 5.6 | 5.6 | 6.1667
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.1 | 21.8 | 21.7 | 21.5 | 21.8 | 22.2 | 22.2 | 22.6 | 22.4 | 22.3 | 22.1 | 22.8 | 24.1 | 24.7 | 24.3 | 24.3 | 23.8 | 22.3 | 21.8 | 21.5 | 21.4 | 20.6 | 20.7 | 20.5 | 22.2708
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.3 | 26.8 | 26 | 25.7 | 26.8 | 27 | 27.3 | 29.4 | 27.6 | 26.3 | 26.7 | 26.9 | 28.2 | 29.5 | 29.4 | 29.4 | 28.8 | 26.5 | 26.6 | 25.6 | 25.1 | 24.7 | 25.6 | 25.6 | 26.9917
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2729.332 | 2536.6733 | 2376.1243 | 2311.9048 | 2568.7831 | 2633.0026 | 2697.2222 | 2568.7831 | 2568.7831 | 2247.6852 | 2472.4537 | 2311.9048 | 2247.6852 | 2536.6733 | 2697.2222 | 2665.1124 | 2633.0026 | 2408.2341 | 2504.5635 | 2183.4656 | 1958.6971 | 2279.795 | 2600.8929 | 2600.8929 | 59338.8889
15 | Power Consumption of Chiller | KWH |  | 1600 | 1400 | 1300 | 1400 | 1500 | 1500 | 1500 | 1400 | 1500 | 1400 | 1400 | 1300 | 1600 | 1500 | 1600 | 1600 | 1500 | 1400 | 1200 | 1200 | 1200 | 1500 | 1500 | 1500 | 34500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58622 | 0.5519 | 0.54711 | 0.60556 | 0.58393 | 0.56969 | 0.55613 | 0.54501 | 0.58393 | 0.62286 | 0.56624 | 0.56231 | 0.71184 | 0.59133 | 0.5932 | 0.60035 | 0.56969 | 0.58134 | 0.47913 | 0.54959 | 0.61265 | 0.65795 | 0.57673 | 0.57673 | 0.58256
17 | Average iKW/TR |  |  | Hours 7: 0.58256 | 0.58256
18 | COP of chiller |  |  | 5.9977 | 6.3707 | 6.4265 | 5.8062 | 6.0212 | 6.1718 | 6.3223 | 6.4513 | 6.0212 | 5.6449 | 6.2094 | 6.2528 | 4.9393 | 5.946 | 5.9271 | 5.8566 | 6.1718 | 6.0481 | 7.3384 | 6.3976 | 5.739 | 5.3438 | 6.0965 | 6.0965 | 6.0665
19 | EER of Chiller |  |  | 20.4702 | 21.7431 | 21.9337 | 19.8165 | 20.5504 | 21.0642 | 21.578 | 22.0183 | 20.5504 | 19.266 | 21.1927 | 21.3409 | 16.8578 | 20.2936 | 20.2293 | 19.9885 | 21.0642 | 20.6422 | 25.0459 | 21.8349 | 19.5871 | 18.2385 | 20.8073 | 20.8073 | 20.705
20 | LMTD of Condenser | ºC |  | 6.7704 | 6.7962 | 5.8907 | 6.0593 | 6.7962 | 6.8208 | 6.8358 | 7.4926 | 6.7704 | 5.8748 | 6.0094 | 5.8109 | 6.019 | 6.2981 | 6.8358 | 6.731 | 6.5867 | 5.6418 | 6.0878 | 5.6022 | 5.1295 | 5.6022 | 5.8096 | 5.7798 | 6.2521
21 | LMTD of Evaporator | ºC |  | 3.6231 | 3.4647 | 2.6811 | 2.6332 | 3.3363 | 3.5442 | 3.4393 | 3.3363 | 3.0046 | 2.5849 | 2.931 | 2.4453 | 2.9192 | 3.1494 | 3.2749 | 3.5706 | 3.5442 | 2.5141 | 2.7764 | 2.3526 | 2.1879 | 2.6091 | 2.8472 | 2.6502 | 2.9758
Performance Sheet Chiller
Date :- 07/03/2023
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 15: 1.3; Hours 16: 1.3; Hours 17: 1.3; Hours 18: 1.3; Hours 23: 1.2; Hours 0: 1.3; Hours 1: 1.2; Hours 2: 1.3 | 1.275
2 | Small temperature difference of evaporator | ºC |  | Hours 15: 1.8; Hours 16: 1.7; Hours 17: 1.5; Hours 18: 1.2; Hours 23: 1.4; Hours 0: 1.9; Hours 1: 1.6; Hours 2: 1.4 | 1.5625
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 15: 15.5; Hours 16: 13.8; Hours 17: 13.3; Hours 18: 12.6; Hours 23: 15.8; Hours 0: 14.4; Hours 1: 13.2; Hours 2: 12.3 | 13.8625
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 15: 8; Hours 16: 6.9; Hours 17: 6.1; Hours 18: 5.7; Hours 23: 8.4; Hours 0: 7.1; Hours 1: 6; Hours 2: 5.3 | 6.6875
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 15: 22.5; Hours 16: 22.2; Hours 17: 21.9; Hours 18: 22.5; Hours 23: 23.8; Hours 0: 22.3; Hours 1: 21.7; Hours 2: 21.5 | 22.3
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 15: 28.4; Hours 16: 27.5; Hours 17: 27.4; Hours 18: 27.8; Hours 23: 29.5; Hours 0: 27.7; Hours 1: 27.3; Hours 2: 26.7 | 27.7875
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 23: 4.3; Hours 0: 4.3; Hours 1: 4.3; Hours 2: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 15: 2408.2341; Hours 16: 2215.5754; Hours 17: 2311.9048; Hours 18: 2215.5754; Hours 23: 2376.1243; Hours 0: 2344.0146; Hours 1: 2311.9048; Hours 2: 2247.6852 | 18431.0185
15 | Power Consumption of Chiller | KWH |  | Hours 14: 400; Hours 15: 1500; Hours 16: 1600; Hours 17: 1400; Hours 18: 1400; Hours 23: 1500; Hours 0: 1600; Hours 1: 1500; Hours 2: 1400; Hours 3: 200 | 12500
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 15: 0.62286; Hours 16: 0.72216; Hours 17: 0.60556; Hours 18: 0.63189; Hours 23: 0.63128; Hours 0: 0.68259; Hours 1: 0.64882; Hours 2: 0.62286 | 0.646
17 | Average iKW/TR |  |  | Hours 7: 0.646 | 0.646
18 | COP of chiller |  |  | Hours 15: 5.6449; Hours 16: 4.8687; Hours 17: 5.8062; Hours 18: 5.5643; Hours 23: 5.5696; Hours 0: 5.151; Hours 1: 5.4191; Hours 2: 5.6449 | 5.4586
19 | EER of Chiller |  |  | Hours 15: 19.266; Hours 16: 16.617; Hours 17: 19.8165; Hours 18: 18.9908; Hours 23: 19.0092; Hours 0: 17.5803; Hours 1: 18.4954; Hours 2: 19.266 | 18.6302
20 | LMTD of Condenser | ºC |  | Hours 15: 3.4468; Hours 16: 3.2621; Hours 17: 3.3241; Hours 18: 3.2621; Hours 23: 3.2586; Hours 0: 3.2932; Hours 1: 3.2284; Hours 2: 3.2309 | 3.2883
21 | LMTD of Evaporator | ºC |  | Hours 15: 4.567; Hours 16: 4.2563; Hours 17: 4.0959; Hours 18: 3.6134; Hours 23: 4.0255; Hours 0: 4.628; Hours 1: 4.2235; Hours 2: 3.9068 | 4.1645
Performance Sheet Chiller
Date :- 07/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 8: 1.6; Hours 9: 1.4 | 1.5
2 | Small temperature difference of evaporator | ºC |  | Hours 8: 0.7; Hours 9: 0.5 | 0.6
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 8: 14.3; Hours 9: 12.7 | 13.5
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 8: 5.8; Hours 9: 5.6 | 5.7
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 8: 21.4; Hours 9: 21.3 | 21.35
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 8: 28.1; Hours 9: 26.9 | 27.5
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 8: 4.3; Hours 9: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 8: 3.8; Hours 9: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 8: 3.8; Hours 9: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 8: 3; Hours 9: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 8: 0.5; Hours 9: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 8: 0.8; Hours 9: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 8: 971; Hours 9: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 8: 2729.332; Hours 9: 2279.795 | 5009.127
15 | Power Consumption of Chiller | KWH |  | Hours 8: 1600; Hours 9: 1000 | 2600
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 8: 0.58622; Hours 9: 0.43864 | 0.51243
17 | Average iKW/TR |  |  | Hours 7: 0.51243 | 0.51243
18 | COP of chiller |  |  | Hours 8: 5.9977; Hours 9: 8.0158 | 7.0067
19 | EER of Chiller |  |  | Hours 8: 20.4702; Hours 9: 27.3578 | 23.914
20 | LMTD of Condenser | ºC |  | Hours 8: 4.0699; Hours 9: 3.4795 | 3.7747
21 | LMTD of Evaporator | ºC |  | Hours 8: 3.2998; Hours 9: 2.6091 | 2.9544

## 08-03-2023
Performance Sheet Chiller
Date :- 08/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | 49 | 27.7 | 19.8 | [24 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4.8 | 4.8 | 4.9 | 4.8 | 4.9 | 4.2 | 4.6 | 4.6 | 3.4 | 3.7 | 4.1 | 4.3 | 4.3 | 4.5 | 4.8 | 4.9 | 4.9 | 5.1 | 4.9 | 4.2 | 3.9 | 3.7 | 4.3 | 4.7 | 4.4708
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 1 | 0.9 | 0.9 | 0.9 | 1 | 0.8 | 0.8 | 0.9 | 0.9 | 0.5 | 0.6 | 0.6 | 0.7 | 0.9 | 1.1 | 1 | 1 | 0.9 | 0.7 | 0.6 | 0.5 | 0.8 | 0.9 | 0.825
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.8 | 14.1 | 14.5 | 14.8 | 15 | 15.3 | 14.7 | 13.7 | 13.6 | 13.6 | 13.4 | 12.9 | 12.7 | 13.4 | 14.4 | 15.2 | 15.6 | 15.9 | 14.5 | 13.1 | 12.2 | 11.9 | 12.8 | 13.7 | 13.95
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.8 | 5.8 | 6.2 | 6.4 | 6.8 | 7.2 | 6.9 | 7 | 7.1 | 7.1 | 5.7 | 5.5 | 5.4 | 5.7 | 6.3 | 6.9 | 7.1 | 7.5 | 6.2 | 5.5 | 5.4 | 5.4 | 5.8 | 5.8 | 6.2708
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.5 | 20.5 | 21.1 | 21.7 | 22.4 | 22.7 | 23.2 | 24.4 | 24.3 | 22.9 | 23.7 | 23.6 | 23.3 | 23 | 22.4 | 22.7 | 22.8 | 23.6 | 22.1 | 21.7 | 21.4 | 20.7 | 20.7 | 20.8 | 22.3417
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 25.7 | 25.8 | 26.3 | 27 | 27.7 | 28.2 | 27.8 | 28.4 | 28.1 | 26.7 | 28.4 | 28.1 | 27.7 | 27.8 | 27.6 | 27.9 | 28 | 28.9 | 27.2 | 26.6 | 25.3 | 24.4 | 25.1 | 25.8 | 27.1042
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2665.1124 | 2665.1124 | 2697.2222 | 2633.0026 | 2600.8929 | 2504.5635 | 2151.3558 | 2087.1362 | 2087.1362 | 2472.4537 | 2376.1243 | 2344.0146 | 2472.4537 | 2600.8929 | 2665.1124 | 2729.332 | 2697.2222 | 2665.1124 | 2440.3439 | 2183.4656 | 2087.1362 | 2247.6852 | 2536.6733 | 59178.3399
15 | Power Consumption of Chiller | KWH |  | 1600 | 1500 | 1600 | 1500 | 1600 | 1400 | 1400 | 1200 | 1400 | 1400 | 1500 | 1400 | 1400 | 1600 | 1500 | 1700 | 1600 | 1600 | 1500 | 1200 | 1100 | 1300 | 1600 | 1500 | 35100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.62286 | 0.56283 | 0.60035 | 0.55613 | 0.60767 | 0.53828 | 0.55898 | 0.55779 | 0.67078 | 0.67078 | 0.60668 | 0.58919 | 0.59727 | 0.64713 | 0.57673 | 0.63787 | 0.58622 | 0.5932 | 0.56283 | 0.49173 | 0.50379 | 0.62286 | 0.71184 | 0.59133 | 0.59438
17 | Average iKW/TR |  |  | 7: 0.59438 | 0.59438
18 | COP of chiller |  |  | 5.6449 | 6.247 | 5.8566 | 6.3223 | 5.786 | 6.532 | 6.29 | 6.3035 | 5.2417 | 5.2417 | 5.7954 | 5.9675 | 5.8868 | 5.4332 | 6.0965 | 5.5121 | 5.9977 | 5.9271 | 6.247 | 7.1502 | 6.9792 | 5.6449 | 4.9393 | 5.946 | 5.9579
19 | EER of Chiller |  |  | 19.266 | 21.3211 | 19.9885 | 21.578 | 19.7477 | 22.2936 | 21.4679 | 21.5138 | 17.8899 | 17.8899 | 19.7798 | 20.367 | 20.0917 | 18.5436 | 20.8073 | 18.8127 | 20.4702 | 20.2293 | 21.3211 | 24.4037 | 23.8198 | 19.266 | 16.8578 | 20.2936 | 20.3342
20 | LMTD of Condenser | ºC |  | 7.0848 | 7.1244 | 7.1893 | 7.1244 | 7.2291 | 6.5708 | 6.6364 | 6.3928 | 5.0646 | 5.3781 | 6.1537 | 6.2837 | 6.2437 | 6.6121 | 7.0848 | 7.1893 | 7.1893 | 7.4379 | 7.1494 | 6.3374 | 5.6265 | 5.338 | 6.2437 | 6.9007 | 6.566
21 | LMTD of Evaporator | ºC |  | 3.4913 | 3.7219 | 3.5706 | 3.5969 | 3.5442 | 3.668 | 3.2843 | 2.9937 | 3.0852 | 3.0852 | 2.7527 | 2.8568 | 2.832 | 3.0987 | 3.5178 | 3.8687 | 3.7756 | 3.7488 | 3.5706 | 3.0733 | 2.7067 | 2.463 | 3.0739 | 3.4647 | 3.2852
Performance Sheet Chiller
Date :- 08/03/2023
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | 49 | 27.7 | 19.8 | [24 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 12: 1.4; 13: 1.4; 14: 1.4; 15: 1.3; 16: 1.3; 17: 1.4; 23: 1.4; 0: 1.5; 1: 1.4; 2: 1.3 | 1.38
2 | Small temperature difference of evaporator | ºC |  | 12: 1.7; 13: 1.7; 14: 1.6; 15: 1.6; 16: 1.5; 17: 1.5; 23: 1.8; 0: 1.9; 1: 1.9; 2: 1.4 | 1.66
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 12: 13.5; 13: 13.5; 14: 13.5; 15: 13.5; 16: 13.4; 17: 13.4; 23: 15.4; 0: 15.6; 1: 14.5; 2: 13.6 | 13.99
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 12: 6.8; 13: 6.8; 14: 6.8; 15: 6.8; 16: 7; 17: 5.8; 23: 6.1; 0: 6.1; 1: 6.1; 2: 6.1 | 6.44
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 12: 24.3; 13: 24.3; 14: 24.3; 15: 24.3; 16: 22.9; 17: 23.6; 23: 21.7; 0: 21.7; 1: 21.7; 2: 21.7 | 23.05
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 12: 29.2; 13: 29.2; 14: 29.2; 15: 29.2; 16: 27.8; 17: 29.4; 23: 27.6; 0: 27.6; 1: 27.6; 2: 27.6 | 28.44
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 12: 4.3; 13: 4.3; 14: 4.3; 15: 4.3; 16: 4.3; 17: 4.3; 23: 4.3; 0: 4.3; 1: 4.3; 2: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 12: 3.8; 13: 3.8; 14: 3.8; 15: 3.8; 16: 3.8; 17: 3.8; 23: 3.8; 0: 3.8; 1: 3.8; 2: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 12: 3.8; 13: 3.8; 14: 3.8; 15: 3.8; 16: 3.8; 17: 3.8; 23: 3.8; 0: 3.8; 1: 3.8; 2: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 12: 3; 13: 3; 14: 3; 15: 3; 16: 3; 17: 3; 23: 3; 0: 3; 1: 3; 2: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 12: 0.5; 13: 0.5; 14: 0.5; 15: 0.5; 16: 0.5; 17: 0.5; 23: 0.5; 0: 0.5; 1: 0.5; 2: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 12: 0.8; 13: 0.8; 14: 0.8; 15: 0.8; 16: 0.8; 17: 0.8; 23: 0.8; 0: 0.8; 1: 0.8; 2: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 12: 971; 13: 971; 14: 971; 15: 971; 16: 971; 17: 971; 23: 971; 0: 971; 1: 971; 2: 971 | 971
14 | TR Genrated by Chiller | TR |  | 12: 2151.3558; 13: 2151.3558; 14: 2151.3558; 15: 2151.3558; 16: 2055.0265; 17: 2440.3439; 23: 2986.2103; 0: 3050.4299; 1: 2697.2222; 2: 2408.2341 | 24242.8902
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 600 | 1600 | 1500 | 1400 | 1500 | 1600 | 1600 | 800 | 0 | 0 | 0 | 0 | 1000 | 1400 | 1600 | 1400 | 300 | 0 | 0 | 0 | 16300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 12: 0.74372; 13: 0.69723; 14: 0.65075; 15: 0.69723; 16: 0.77858; 17: 0.65565; 23: 0.33487; 0: 0.45895; 1: 0.5932; 2: 0.58134 | 0.61915
17 | Average iKW/TR |  |  | 7: 0.61915 | 0.61915
18 | COP of chiller |  |  | 12: 4.7276; 13: 5.0428; 14: 5.403; 15: 5.0428; 16: 4.5159; 17: 5.3627; 23: 10.4995; 0: 7.6609; 1: 5.9271; 2: 6.0481 | 6.023
19 | EER of Chiller |  |  | 12: 16.1353; 13: 17.211; 14: 18.4404; 15: 17.211; 16: 15.4128; 17: 18.3027; 23: 35.8348; 0: 26.1468; 1: 20.2293; 2: 20.6422 | 20.5566
20 | LMTD of Condenser | ºC |  | 12: 3.2578; 13: 3.2578; 14: 3.2578; 15: 3.1366; 16: 3.1366; 17: 3.5417; 23: 3.5727; 0: 3.6967; 1: 3.5727; 2: 3.4468 | 3.3877
21 | LMTD of Evaporator | ºC |  | 12: 4.1938; 13: 4.1938; 14: 4.0699; 15: 4.0699; 16: 3.8522; 17: 4.2156; 23: 5.1123; 0: 5.3021; 1: 4.9696; 2: 4.055 | 4.4034

## 09-03-2023
Performance Sheet Chiller
Date :- 09/03/2021
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4.8 | 4.9 | 5 | 4.9 | 4.9 | 4.8 | 4.7 | 4.6 | 4.2 | 4.1 | 4.4 | 4.6 | 4.6 | 4.8 | 4.8 | 4.8 | 4.9 | 3.8 | 3.6 | 4.1 | 4.1 | 4 | 4 | 4 | 4.475
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 0.9 | 0.9 | 1.1 | 1.1 | 0.9 | 0.9 | 0.6 | 0.7 | 0.6 | 0.9 | 0.7 | 0.7 | 0.8 | 0.8 | 0.8 | 1 | 0.5 | 0.4 | 0.5 | 0.4 | 0.5 | 0.4 | 0.4 | 0.725
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14 | 14.3 | 14.8 | 15.1 | 15.3 | 15.7 | 15.7 | 14.4 | 13.7 | 13.6 | 13.4 | 13.2 | 12.9 | 13.4 | 14.7 | 15.4 | 15.3 | 13.4 | 12.7 | 12.2 | 12.2 | 13.3 | 13.9 | 14 | 14.025
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.8 | 6.1 | 6.6 | 7 | 7.1 | 7.7 | 7.8 | 7 | 7 | 6.9 | 5.8 | 5.7 | 5.5 | 5.7 | 6.6 | 6.7 | 7.6 | 6.9 | 6.9 | 5.4 | 5.7 | 5.6 | 5.6 | 5.9 | 6.4417
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21 | 21.1 | 21.2 | 21.6 | 21.8 | 23.2 | 22.9 | 22.4 | 22.9 | 22.9 | 23.1 | 23.3 | 22.4 | 21.9 | 21.6 | 20.7 | 20.7 | 19.7 | 19 | 19.3 | 18.9 | 19.3 | 19.4 | 19.4 | 21.2375
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.1 | 26.3 | 26.3 | 26.7 | 27.1 | 28.3 | 27.6 | 27 | 26.8 | 27 | 27.7 | 27.8 | 27.1 | 26.7 | 26.8 | 26.1 | 25.4 | 23.4 | 22.4 | 23.2 | 22.9 | 24.2 | 24.7 | 24.6 | 25.925
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2633.0026 | 2633.0026 | 2633.0026 | 2600.8929 | 2633.0026 | 2568.7831 | 2536.6733 | 2376.1243 | 2151.3558 | 2151.3558 | 2440.3439 | 2408.2341 | 2376.1243 | 2472.4537 | 2600.8929 | 2793.5516 | 2472.4537 | 2087.1362 | 1862.3677 | 2183.4656 | 2087.1362 | 2472.4537 | 2665.1124 | 2600.8929 | 58439.8148
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1500 | 1600 | 1500 | 1400 | 1400 | 1400 | 1300 | 1400 | 1500 | 1400 | 1500 | 1500 | 1700 | 1400 | 1100 | 1100 | 1100 | 1200 | 1400 | 1500 | 1500 | 1400 | 33800
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.56969 | 0.56969 | 0.56969 | 0.61517 | 0.56969 | 0.54501 | 0.5519 | 0.58919 | 0.60427 | 0.65075 | 0.61467 | 0.58134 | 0.63128 | 0.60668 | 0.65362 | 0.50115 | 0.4449 | 0.52704 | 0.59065 | 0.54959 | 0.67078 | 0.60668 | 0.56283 | 0.53828 | 0.57977
17 | Average iKW/TR |  |  | Hours 7: 0.57977 | 0.57977
18 | COP of chiller |  |  | 6.1718 | 6.1718 | 6.1718 | 5.7155 | 6.1718 | 6.4513 | 6.3707 | 5.9675 | 5.8186 | 5.403 | 5.7202 | 6.0481 | 5.5696 | 5.7954 | 5.3793 | 7.0158 | 7.9029 | 6.6712 | 5.9528 | 6.3976 | 5.2417 | 5.7954 | 6.247 | 6.532 | 6.1118
19 | EER of Chiller |  |  | 21.0642 | 21.0642 | 21.0642 | 19.5069 | 21.0642 | 22.0183 | 21.7431 | 20.367 | 19.8588 | 18.4404 | 19.5229 | 20.6422 | 19.0092 | 19.7798 | 18.3594 | 23.9449 | 26.9725 | 22.769 | 20.3169 | 21.8349 | 17.8899 | 19.7798 | 21.3211 | 22.2936 | 20.8595
20 | LMTD of Condenser | ºC |  | 7.045 | 7.1893 | 7.2536 | 7.1494 | 7.2291 | 7.045 | 6.7807 | 6.6364 | 5.9381 | 5.915 | 6.428 | 6.5961 | 6.6765 | 6.9249 | 7.0848 | 7.164 | 6.9886 | 5.442 | 5.113 | 5.8344 | 5.8748 | 6.1269 | 6.2817 | 6.2432 | 6.54
21 | LMTD of Evaporator | ºC |  | 3.5442 | 3.5442 | 3.5442 | 3.8138 | 3.8413 | 3.4913 | 3.4647 | 2.8568 | 2.8412 | 2.6814 | 3.3847 | 3.0478 | 3.0222 | 3.2583 | 3.3621 | 3.516 | 3.5593 | 2.463 | 2.1161 | 2.5363 | 2.2825 | 2.7527 | 2.6951 | 2.6502 | 3.0946
Performance Sheet Chiller
Date :- 09/03/2021
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 12: 1.4; Hours 13: 1.4; Hours 14: 1.5; Hours 15: 1.4; Hours 16: 1.3; Hours 17: 1.4; Hours 18: 1.6; Hours 22: 1.5; Hours 23: 1.3; Hours 0: 1.3; Hours 1: 1.5 | 1.4182
2 | Small temperature difference of evaporator | ºC |  | Hours 12: 1.9; Hours 13: 1.8; Hours 14: 1.7; Hours 15: 1.4; Hours 16: 1.5; Hours 17: 1.6; Hours 18: 1.7; Hours 22: 2.2; Hours 23: 2; Hours 0: 1.8; Hours 1: 1.5 | 1.7364
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 12: 13.6; Hours 13: 13.6; Hours 14: 13.6; Hours 15: 13.6; Hours 16: 13.6; Hours 17: 13.5; Hours 18: 13.2; Hours 22: 13.4; Hours 23: 13.4; Hours 0: 13.4; Hours 1: 12.7 | 13.4182
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 12: 7; Hours 13: 7; Hours 14: 7; Hours 15: 7; Hours 16: 7.1; Hours 17: 5.9; Hours 18: 5.7; Hours 22: 6.9; Hours 23: 6.9; Hours 0: 6.9; Hours 1: 6.8 | 6.7455
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 12: 22.7; Hours 13: 22.7; Hours 14: 22.7; Hours 15: 22.7; Hours 16: 22.8; Hours 17: 22.9; Hours 18: 23.1; Hours 22: 19.7; Hours 23: 19.7; Hours 0: 19.7; Hours 1: 19 | 21.6091
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 12: 27.9; Hours 13: 27.9; Hours 14: 27.9; Hours 15: 27.9; Hours 16: 27.9; Hours 17: 28.9; Hours 18: 28.9; Hours 22: 24.7; Hours 23: 24.7; Hours 0: 24.7; Hours 1: 23.4 | 26.8
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 12: 4.3; Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 22: 4.3; Hours 23: 4.3; Hours 0: 4.3; Hours 1: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 12: 2119.246; Hours 13: 2119.246; Hours 14: 2119.246; Hours 15: 2119.246; Hours 16: 2087.1362; Hours 17: 2440.3439; Hours 18: 2408.2341; Hours 22: 2087.1362; Hours 23: 2087.1362; Hours 0: 2087.1362; Hours 1: 1894.4775 | 23568.5847
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 400 | 1600 | 1500 | 1400 | 1500 | 1600 | 1700 | 900 | 0 | 0 | 100 | 1500 | 1300 | 1300 | 900 | 0 | 0 | 0 | 0 | 0 | 15700
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 12: 0.75499; Hours 13: 0.7078; Hours 14: 0.66061; Hours 15: 0.7078; Hours 16: 0.7666; Hours 17: 0.69662; Hours 18: 0.37372; Hours 22: 0.71869; Hours 23: 0.62286; Hours 0: 0.62286; Hours 1: 0.47507 | 0.64615
17 | Average iKW/TR |  |  | Hours 7: 0.64615 | 0.64615
18 | COP of chiller |  |  | Hours 12: 4.657; Hours 13: 4.9675; Hours 14: 5.3223; Hours 15: 4.9675; Hours 16: 4.5865; Hours 17: 5.0472; Hours 18: 9.4082; Hours 22: 4.8922; Hours 23: 5.6449; Hours 0: 5.6449; Hours 1: 7.4011 | 5.6854
19 | EER of Chiller |  |  | Hours 12: 15.8945; Hours 13: 16.9541; Hours 14: 18.1651; Hours 15: 16.9541; Hours 16: 15.6537; Hours 17: 17.2261; Hours 18: 32.1101; Hours 22: 16.6972; Hours 23: 19.266; Hours 0: 19.266; Hours 1: 25.2599 | 19.4043
20 | LMTD of Condenser | ºC |  | Hours 12: 3.3535; Hours 13: 3.3535; Hours 14: 3.4744; Hours 15: 3.3535; Hours 16: 3.1996; Hours 17: 3.6036; Hours 18: 3.7872; Hours 22: 3.4099; Hours 23: 3.1682; Hours 0: 3.1682; Hours 1: 3.2129 | 3.3713
21 | LMTD of Evaporator | ºC |  | Hours 12: 4.4053; Hours 13: 4.2845; Hours 14: 4.1624; Hours 15: 3.7866; Hours 16: 3.883; Hours 17: 4.3448; Hours 18: 4.4416; Hours 22: 4.7277; Hours 23: 4.4923; Hours 0: 4.2526; Hours 1: 3.6967 | 4.2252
1.51

## 10-03-2023
Performance Sheet Chiller
Date :- 10/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 5.2 | 5.2 | 5.3 | 5.2 | 4.7 | 4.6 | 4.4 | 4.1 | 4.1 | 4.1 | 4.9 | 4.5 | 4.3 | 5.1 | 5.3 | 5.4 | 5 | 4 | 4.6 | 4.1 | 4.2 | 4.4 | 4.6 | 5.1 | 4.6833
2 | Small temperature difference of evaporator | ºC |  | 1.1 | 1.1 | 1 | 1 | 1.1 | 1 | 0.6 | 0.4 | 0.5 | 0.5 | 0.8 | 0.5 | 0.5 | 0.7 | 1 | 1.1 | 1 | 0.5 | 0.6 | 0.4 | 0.5 | 0.7 | 0.8 | 0.7 | 0.75417
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.4 | 14.7 | 15 | 15.4 | 15.8 | 15.3 | 13.9 | 13.4 | 13.4 | 13.5 | 13.3 | 12.7 | 12.4 | 13.3 | 14.3 | 14.9 | 15.2 | 13.3 | 12.6 | 11.9 | 12.5 | 13.6 | 14.2 | 14.4 | 13.8917
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.2 | 6.4 | 6.7 | 6.9 | 7.3 | 7.2 | 6.9 | 7 | 7 | 6.9 | 5.4 | 5.6 | 5.6 | 5.7 | 6.2 | 6.6 | 7 | 6.8 | 5.4 | 5.4 | 5.6 | 5.7 | 5.9 | 6.2 | 6.3167
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 19.4 | 19.3 | 19.6 | 20.3 | 20.9 | 21.6 | 21.9 | 21.9 | 22.2 | 22 | 22.2 | 21.3 | 21.3 | 22.1 | 21.2 | 21 | 21.2 | 20.8 | 21.3 | 21.3 | 20.4 | 20.7 | 20.6 | 20.8 | 21.0542
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 24.6 | 24.5 | 25 | 25.7 | 27.8 | 26.8 | 26.2 | 25.8 | 26 | 25.7 | 26.8 | 25.7 | 25.5 | 26.7 | 26.4 | 26 | 26.2 | 24.5 | 25.6 | 25.2 | 24.7 | 25.6 | 25.8 | 26 | 25.7833
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2633.0026 | 2665.1124 | 2665.1124 | 2729.332 | 2729.332 | 2600.8929 | 2247.6852 | 2055.0265 | 2055.0265 | 2119.246 | 2536.6733 | 2279.795 | 2183.4656 | 2440.3439 | 2600.8929 | 2665.1124 | 2633.0026 | 2087.1362 | 2311.9048 | 2087.1362 | 2215.5754 | 2536.6733 | 2665.1124 | 2633.0026 | 58375.5952
15 | Power Consumption of Chiller | KWH |  | 1700 | 1400 | 1700 | 1500 | 1600 | 1200 | 1200 | 1200 | 1300 | 1400 | 1300 | 1400 | 1400 | 1500 | 1500 | 1500 | 1300 | 1300 | 1200 | 1200 | 1400 | 1600 | 1600 | 1500 | 33900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.64565 | 0.52531 | 0.63787 | 0.54959 | 0.58622 | 0.46138 | 0.53388 | 0.58393 | 0.6326 | 0.66061 | 0.51248 | 0.61409 | 0.64118 | 0.61467 | 0.57673 | 0.56283 | 0.49373 | 0.62286 | 0.51905 | 0.57495 | 0.63189 | 0.63075 | 0.60035 | 0.56969 | 0.5826
17 | Average iKW/TR |  |  | Hours 7: 0.5826 | 0.5826
18 | COP of chiller |  |  | 5.4457 | 6.6932 | 5.5121 | 6.3976 | 5.9977 | 7.6206 | 6.5857 | 6.0212 | 5.5581 | 5.3223 | 6.8607 | 5.7255 | 5.4836 | 5.7202 | 6.0965 | 6.247 | 7.1213 | 5.6449 | 6.7739 | 6.1153 | 5.5643 | 5.5743 | 5.8566 | 6.1718 | 6.0879
19 | EER of Chiller |  |  | 18.5861 | 22.844 | 18.8127 | 21.8349 | 20.4702 | 26.0092 | 22.4771 | 20.5504 | 18.9696 | 18.1651 | 23.4157 | 19.5413 | 18.7156 | 19.5229 | 20.8073 | 21.3211 | 24.3049 | 19.266 | 23.1193 | 20.8716 | 18.9908 | 19.0252 | 19.9885 | 21.0642 | 20.7781
20 | LMTD of Condenser | ºC |  | 7.502 | 7.502 | 7.6864 | 7.5822 | 7.6375 | 6.8753 | 6.3076 | 5.8344 | 5.7938 | 5.7531 | 6.948 | 6.4519 | 6.1633 | 7.1552 | 7.606 | 7.6288 | 7.2135 | 5.6495 | 6.5152 | 5.8344 | 6.0994 | 6.5472 | 6.8753 | 7.3979 | 6.7733
21 | LMTD of Evaporator | ºC |  | 3.8413 | 3.8687 | 3.7219 | 3.7756 | 3.9235 | 3.668 | 2.757 | 2.2589 | 2.4384 | 2.4875 | 3.3103 | 2.6091 | 2.5363 | 3.0733 | 3.668 | 3.8687 | 3.695 | 2.463 | 2.8071 | 2.2825 | 2.5607 | 3.1494 | 3.4136 | 3.2249 | 3.1418
Performance Sheet Chiller
Date :- 10/03/2023
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 11: 1.5; Hours 12: 1.5; Hours 13: 1.3; Hours 14: 1.4; Hours 15: 1.4; Hours 16: 1.7; Hours 17: 1.6; Hours 18: 1.6; Hours 22: 1.7; Hours 23: 1.4; Hours 0: 1.7; Hours 1: 1.6 | 1.5333
2 | Small temperature difference of evaporator | ºC |  | Hours 11: 1.8; Hours 12: 1.8; Hours 13: 1.4; Hours 14: 1.6; Hours 15: 1.7; Hours 16: 1.7; Hours 17: 1.6; Hours 18: 1.6; Hours 22: 2.1; Hours 23: 1.7; Hours 0: 1.7; Hours 1: 1.4 | 1.675
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 11: 13.5; Hours 12: 13.5; Hours 13: 13.5; Hours 14: 13.5; Hours 15: 13.3; Hours 16: 13.4; Hours 17: 13.2; Hours 18: 12.7; Hours 22: 13.3; Hours 23: 13.3; Hours 0: 13.3; Hours 1: 12.6 | 13.2583
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 11: 6.9; Hours 12: 6.9; Hours 13: 6.9; Hours 14: 6.9; Hours 15: 7.1; Hours 16: 7.1; Hours 17: 5.8; Hours 18: 5.4; Hours 22: 7; Hours 23: 7; Hours 0: 7; Hours 1: 5.4 | 6.6167
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 11: 21.9; Hours 12: 21.9; Hours 13: 21.9; Hours 14: 21.9; Hours 15: 22.1; Hours 16: 21.9; Hours 17: 22.1; Hours 18: 21.2; Hours 22: 20.7; Hours 23: 20.7; Hours 0: 20.7; Hours 1: 21.1 | 21.5083
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 11: 26.8; Hours 12: 26.8; Hours 13: 26.8; Hours 14: 26.8; Hours 15: 26.9; Hours 16: 26.7; Hours 17: 27.8; Hours 18: 26.8; Hours 22: 25.6; Hours 23: 25.6; Hours 0: 25.6; Hours 1: 26.8 | 26.5833
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 11: 4.3; Hours 12: 4.3; Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 22: 4.3; Hours 23: 4.3; Hours 0: 4.3; Hours 1: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 11: 2119.246; Hours 12: 2119.246; Hours 13: 2119.246; Hours 14: 2119.246; Hours 15: 1990.8069; Hours 16: 2022.9167; Hours 17: 2376.1243; Hours 18: 2344.0146; Hours 22: 2022.9167; Hours 23: 2022.9167; Hours 0: 2022.9167; Hours 1: 2311.9048 | 25591.5013
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 300 | 1500 | 1500 | 1300 | 1300 | 1400 | 1600 | 1400 | 1000 | 0 | 0 | 0 | 1600 | 1500 | 1400 | 800 | 0 | 0 | 0 | 0 | 500 | 17100
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 11: 0.7078; Hours 12: 0.7078; Hours 13: 0.61343; Hours 14: 0.61343; Hours 15: 0.70323; Hours 16: 0.79094; Hours 17: 0.58919; Hours 18: 0.42662; Hours 22: 0.79094; Hours 23: 0.7415; Hours 0: 0.69207; Hours 1: 0.34604 | 0.64358
17 | Average iKW/TR |  |  | Hours 7: 0.64358 | 0.64358
18 | COP of chiller |  |  | Hours 11: 4.9675; Hours 12: 4.9675; Hours 13: 5.7317; Hours 14: 5.7317; Hours 15: 4.9998; Hours 16: 4.4454; Hours 17: 5.9675; Hours 18: 8.2416; Hours 22: 4.4454; Hours 23: 4.7417; Hours 0: 5.0804; Hours 1: 10.1608 | 5.7901
19 | EER of Chiller |  |  | Hours 11: 16.9541; Hours 12: 16.9541; Hours 13: 19.5624; Hours 14: 19.5624; Hours 15: 17.0642; Hours 16: 15.172; Hours 17: 20.367; Hours 18: 28.1284; Hours 22: 15.172; Hours 23: 16.1835; Hours 0: 17.3394; Hours 1: 34.6789 | 19.7615
20 | LMTD of Condenser | ºC |  | Hours 11: 3.3774; Hours 12: 3.3774; Hours 13: 3.1366; Hours 14: 3.2578; Hours 15: 3.2256; Hours 16: 3.579; Hours 17: 3.7553; Hours 18: 3.7232; Hours 22: 3.6124; Hours 23: 3.2578; Hours 0: 3.6124; Hours 1: 3.7553 | 3.4725
21 | LMTD of Evaporator | ºC |  | Hours 11: 4.2845; Hours 12: 4.2845; Hours 13: 3.7866; Hours 14: 4.0388; Hours 15: 4.0358; Hours 16: 4.0676; Hours 17: 4.2843; Hours 18: 4.254; Hours 22: 4.5445; Hours 23: 4.0676; Hours 0: 4.0676; Hours 1: 3.9663 | 4.1402

## 11-03-2023
Performance Sheet Chiller
Date :- 11/03/2023
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [9 empty] | 4.8 | 4.5 | 4.6 | 4.4 | 4.6 | 4.4 | 4.9 | 4 | 3.9 | 3.9 | 3.7 | 3.7 | 4 | 4 | 4.4 | 5.1 | 4.3062
2 | Small temperature difference of evaporator | ºC | [9 empty] | 0.8 | 0.8 | 0.6 | 0.6 | 0.7 | 0.9 | 0.7 | 1.5 | 1.6 | 2.2 | 1.3 | 1.5 | 2.1 | 1.3 | 1.3 | 1.1 | 1.1875
3 | Entering Chilled Water Temp. (tchwe) | ºC | [9 empty] | 16 | 14.8 | 14.1 | 13.8 | 13.6 | 13.2 | 12.9 | 12.7 | 13.1 | 13.1 | 12.6 | 12.2 | 11.6 | 12.1 | 13.1 | 13.8 | 13.2937
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [9 empty] | 8.1 | 7.2 | 6.5 | 6.2 | 5.9 | 5.7 | 5.5 | 6.9 | 6.7 | 7 | 7 | 5.5 | 5.4 | 5.7 | 5.6 | 5.6 | 6.2812
5 | Entering Condenser Water Temp. (tcwe) | ºC | [9 empty] | 23.9 | 24.2 | 24.2 | 23.3 | 23.2 | 22.4 | 21.7 | 21.6 | 21.9 | 21.8 | 22.3 | 22.3 | 22.1 | 21.3 | 21.1 | 21.7 | 22.4375
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [9 empty] | 29.6 | 29.9 | 29.9 | 29.1 | 28.9 | 27.8 | 26.2 | 26.4 | 26.5 | 26.3 | 27.4 | 26.9 | 27 | 27 | 27.1 | 27.9 | 27.7437
7 | Chilled water inlet pressure | (Kg/Cm2) | [9 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [9 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [9 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [9 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [9 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [9 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [9 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [9 empty] | 2536.6733 | 2440.3439 | 2440.3439 | 2440.3439 | 2472.4537 | 2408.2341 | 2376.1243 | 1862.3677 | 2055.0265 | 1958.6971 | 1798.1481 | 2151.3558 | 1990.8069 | 2055.0265 | 2408.2341 | 2633.0026 | 36027.1825
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 1500 | 1400 | 1400 | 1400 | 1500 | 1500 | 1200 | 1100 | 1100 | 1200 | 1100 | 1200 | 1200 | 1200 | 1300 | 1500 | 21200
16 | Specific power consumption of Chiller | (iKW/TR) | [9 empty] | 0.59133 | 0.57369 | 0.57369 | 0.57369 | 0.60668 | 0.62286 | 0.50502 | 0.59065 | 0.53527 | 0.61265 | 0.61174 | 0.55779 | 0.60277 | 0.58393 | 0.53981 | 0.56969 | 0.5782
17 | Average iKW/TR |  |  | Hours 7: 0.5782 | 0.5782
18 | COP of chiller | [10 empty] | 5.946 | 6.1287 | 6.1287 | 6.1287 | 5.7954 | 5.6449 | 6.962 | 5.9528 | 6.5686 | 5.739 | 5.7475 | 6.3035 | 5.8331 | 6.0212 | 6.5133 | 6.1718 | 6.0991
19 | EER of Chiller | [10 empty] | 20.2936 | 20.9174 | 20.9174 | 20.9174 | 19.7798 | 19.266 | 23.7615 | 20.3169 | 22.4187 | 19.5871 | 19.6163 | 21.5138 | 19.9082 | 20.5504 | 22.2301 | 21.0642 | 20.8162
20 | LMTD of Condenser | ºC | [9 empty] | 7.2819 | 6.9656 | 7.0712 | 6.8983 | 7.0712 | 6.7434 | 6.9074 | 6.0878 | 5.9043 | 5.8651 | 5.8863 | 5.6936 | 6.1269 | 6.4346 | 6.9751 | 7.7932 | 6.6066
21 | LMTD of Evaporator | ºC | [9 empty] | 3.3103 | 3.2322 | 2.9064 | 2.9064 | 3.0987 | 3.3578 | 3.0222 | 3.6653 | 3.9765 | 4.5941 | 3.355 | 3.9443 | 4.5113 | 3.5978 | 3.9218 | 3.8413 | 3.5776
Performance Sheet Chiller
Date :- 11/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 5.4 | 5.2 | 4.7 | 4.9 | 5.3 | 5.3 | 5.6 | 5.3 | 5.3 | 5.2 | 5.1 | 5 | 4.9 | 4.9 | 4.9 | 4.14 | 3.4 | 4.1 | 3.8 | 3.4 | 4.1 |  |  |  | 4.759
2 | Small temperature difference of evaporator | ºC |  | 1.1 | 0.9 | 0.6 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.5 | 0.4 | 0.4 | 0.5 | 0.4 |  |  |  | 0.69048
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.8 | 13.9 | 12.6 | 13.2 | 13.9 | 14.6 | 15.2 | 16 | 16.3 | 14.8 | 14.4 | 14.1 | 13.9 | 13.5 | 13.2 | 13.1 | 13.4 | 13.4 | 12.9 | 12.5 | 11.9 |  |  |  | 13.8857
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6 | 5.3 | 5.7 | 6 | 6.6 | 7 | 7.9 | 8.4 | 7.3 | 6.5 | 6.3 | 6.2 | 5.8 | 5.4 | 6.9 | 7.1 | 7 | 6.9 | 5.6 | 5.5 |  |  |  | 6.4619
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.1 | 21.2 | 21.6 | 21.3 | 21.8 | 22.2 | 22.6 | 23.1 | 24.6 | 24.3 | 24.7 | 24.4 | 23.7 | 23.6 | 22.7 | 22.2 | 22 | 22.2 | 22 | 22.7 | 22.6 |  |  |  | 22.6952
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.4 | 26.3 | 25.9 | 25.8 | 26.8 | 27.3 | 27.8 | 28.2 | 29.3 | 29.1 | 29.3 | 29.2 | 28.4 | 28.3 | 27.4 | 25.7 | 25.6 | 26.1 | 25.7 | 26.8 | 26.6 |  |  |  | 27.2381
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  | 971
14 | TR Genrated by Chiller | TR |  | 2729.332 | 2536.6733 | 2344.0146 | 2408.2341 | 2536.6733 | 2568.7831 | 2633.0026 | 2600.8929 | 2536.6733 | 2408.2341 | 2536.6733 | 2504.5635 | 2472.4537 | 2472.4537 | 2504.5635 | 1990.8069 | 2022.9167 | 2055.0265 | 1926.5873 | 2215.5754 | 2055.0265 |  |  |  | 50059.1601
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1400 | 1500 | 1500 | 1700 | 1500 | 1500 | 1500 | 1500 | 1500 | 1600 | 1600 | 1300 | 1100 | 1200 | 1200 | 1200 | 1300 | 800 |  |  |  |  | 27900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.54959 | 0.59133 | 0.59727 | 0.62286 | 0.59133 | 0.66179 | 0.56969 | 0.57673 | 0.59133 | 0.62286 | 0.59133 | 0.63883 | 0.64713 | 0.52579 | 0.4392 | 0.60277 | 0.5932 | 0.58393 | 0.67477 | 0.36108 | 0 |  |  |  | 0.55394
17 | Average iKW/TR |  |  | Hours 7: 0.55394 | 0.55394
18 | COP of chiller |  |  | 6.3976 | 5.946 | 5.8868 | 5.6449 | 5.946 | 5.3128 | 6.1718 | 6.0965 | 5.946 | 5.6449 | 5.946 | 5.5038 | 5.4332 | 6.687 | 8.0055 | 5.8331 | 5.9271 | 6.0212 | 5.2107 | 9.7375 |  |  |  |  | 6.1649
19 | EER of Chiller |  |  | 21.8349 | 20.2936 | 20.0917 | 19.266 | 20.2936 | 18.1327 | 21.0642 | 20.8073 | 20.2936 | 19.266 | 20.2936 | 18.7844 | 18.5436 | 22.8229 | 27.3228 | 19.9082 | 20.2293 | 20.5504 | 17.784 | 33.2339 |  |  |  |  | 21.0408
20 | LMTD of Condenser | ºC |  | 7.7503 | 7.4618 | 6.6188 | 6.9074 | 7.5252 | 7.5657 | 7.9174 | 7.5657 | 7.403 | 7.3403 | 7.1552 | 7.1328 | 6.9886 | 6.9886 | 6.9886 | 5.7124 | 4.9852 | 5.8344 | 5.442 | 5.1825 | 5.8748 |  |  |  | 6.7781
21 | LMTD of Evaporator | ºC |  | 3.9235 | 3.4647 | 2.832 | 3.0478 | 3.4647 | 3.4913 | 3.5442 | 3.5178 | 3.3103 | 2.8816 | 2.9801 | 3.1241 | 3.0987 | 3.0987 | 3.1241 | 2.5538 | 2.4137 | 2.2589 | 2.164 | 2.5607 | 2.2589 |  |  |  | 3.0054

## 12-03-2023
Performance Sheet Chiller
Date :- 12/03/2023
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4.9 | 5.1 | 4.9 | 4.9 | 4.6 | 4 | 4 | 3.8 | 3.9 | 3.9 | 4.3 | 4.4 | 4.3 | 4.1 | 4.4 | 4.8 | 4.9 | 4.7 | 4.4 | 4.1 | 4.9 | 5 | 5 | 5.4 | 4.5292
2 | Small temperature difference of evaporator | ºC |  | 1 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 1.7 | 1.1 | 0.6 | 0.7 | 0.6 | 0.5 | 0.9 | 0.8 | 0.6 | 0.7 | 0.8 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 | 0.79583
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.3 | 14.7 | 15 | 15.2 | 15.1 | 13.9 | 13.6 | 13.3 | 13.6 | 13.6 | 13.6 | 13.2 | 12.9 | 12.7 | 12.8 | 14.2 | 14.7 | 14.6 | 13.3 | 12.3 | 12.3 | 13.8 | 14.3 | 14.6 | 13.8167
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.8 | 6.1 | 6.2 | 6.8 | 7.1 | 7.1 | 7.2 | 6.8 | 7 | 7.2 | 5.8 | 5.5 | 5.5 | 5.5 | 5.7 | 5.9 | 6.4 | 6.1 | 5.4 | 5.6 | 5.6 | 5.7 | 5.9 | 6.2 | 6.1708
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.7 | 21.3 | 22 | 22.1 | 23.6 | 23.4 | 23.4 | 24.2 | 25.1 | 24.3 | 24.1 | 24.2 | 23.7 | 23.3 | 22.7 | 22.6 | 22.7 | 23.5 | 23.5 | 23.2 | 22.4 | 22.6 | 22.6 | 22.3 | 23.1042
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.9 | 27.7 | 28.4 | 28.5 | 29.6 | 28.5 | 28.6 | 29.2 | 30.1 | 29.4 | 30 | 29.8 | 29.3 | 28.6 | 28.1 | 28.6 | 28.9 | 29.6 | 29.4 | 28.3 | 27.4 | 28.5 | 28.9 | 29.3 | 28.8583
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2729.332 | 2761.4418 | 2825.6614 | 2697.2222 | 2568.7831 | 2183.4656 | 2055.0265 | 2087.1362 | 2119.246 | 2055.0265 | 2504.5635 | 2472.4537 | 2376.1243 | 2311.9048 | 2279.795 | 2665.1124 | 2665.1124 | 2729.332 | 2536.6733 | 2151.3558 | 2151.3558 | 2600.8929 | 2697.2222 | 2697.2222 | 58921.4616
15 | Power Consumption of Chiller | KWH |  | 1600 | 1600 | 1500 | 1500 | 1300 | 1200 | 1300 | 1300 | 1300 | 1500 | 1500 | 1500 | 1300 | 1300 | 1600 | 1500 | 1700 | 1500 | 1300 | 1200 | 1500 | 1500 | 1700 | 1600 | 34800
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58622 | 0.57941 | 0.53085 | 0.55613 | 0.50608 | 0.54959 | 0.6326 | 0.62286 | 0.61343 | 0.72992 | 0.59891 | 0.60668 | 0.54711 | 0.56231 | 0.70182 | 0.56283 | 0.63787 | 0.54959 | 0.51248 | 0.55779 | 0.69723 | 0.57673 | 0.63028 | 0.5932 | 0.59341
17 | Average iKW/TR |  |  | Hours 7: 0.59341 | 0.59341
18 | COP of chiller |  |  | 5.9977 | 6.0683 | 6.6234 | 6.3223 | 6.9476 | 6.3976 | 5.5581 | 5.6449 | 5.7317 | 4.817 | 5.8707 | 5.7954 | 6.4265 | 6.2528 | 5.0098 | 6.247 | 5.5121 | 6.3976 | 6.8607 | 6.3035 | 5.0428 | 6.0965 | 5.5785 | 5.9271 | 5.9762
19 | EER of Chiller |  |  | 20.4702 | 20.711 | 22.6055 | 21.578 | 23.7121 | 21.8349 | 18.9696 | 19.266 | 19.5624 | 16.4404 | 20.0367 | 19.7798 | 21.9337 | 21.3409 | 17.0986 | 21.3211 | 18.8127 | 21.8349 | 23.4157 | 21.5138 | 17.211 | 20.8073 | 19.0394 | 20.2293 | 20.3969
20 | LMTD of Condenser | ºC |  | 7.5822 | 7.871 | 7.6595 | 7.6595 | 7.1874 | 6.2045 | 6.2432 | 5.9541 | 6.0601 | 6.0987 | 6.8305 | 6.8211 | 6.7153 | 6.3877 | 6.7434 | 7.3989 | 7.5822 | 7.3319 | 6.9368 | 6.3102 | 7.1093 | 7.5707 | 7.7266 | 8.4206 | 7.0169
21 | LMTD of Evaporator | ºC |  | 3.7756 | 3.6492 | 3.5414 | 3.5969 | 3.4913 | 3.1678 | 3.0575 | 2.6306 | 4.1624 | 3.334 | 2.9556 | 3.0987 | 2.8568 | 2.6332 | 3.2497 | 3.4136 | 3.0776 | 3.2998 | 3.3103 | 2.6814 | 2.6814 | 3.1998 | 3.2749 | 3.1019 | 3.2184
Performance Sheet Chiller
Date :- 12/03/2023
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 11: 1.6; Hours 12: 1.6; Hours 13: 1.5; Hours 14: 1.5; Hours 15: 1.5; Hours 16: 1.5; Hours 17: 1.6; Hours 18: 1.6; Hours 19: 1.6; Hours 20: 1.6; Hours 0: 1.7; Hours 1: 1.7; Hours 2: 1.7 | 1.5923
2 | Small temperature difference of evaporator | ºC |  | Hours 11: 1.8; Hours 12: 1.6; Hours 13: 1.5; Hours 14: 1.3; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 1.3; Hours 18: 1.3; Hours 19: 1.3; Hours 20: 1.3; Hours 0: 1.6; Hours 1: 1.4; Hours 2: 1.3 | 1.3308
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 11: 15.6; Hours 12: 14.2; Hours 13: 13.7; Hours 14: 13.6; Hours 15: 13.7; Hours 16: 13.9; Hours 17: 13.9; Hours 18: 13.4; Hours 19: 13.2; Hours 20: 12.9; Hours 0: 14.8; Hours 1: 13.5; Hours 2: 12.6 | 13.7692
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 11: 8.4; Hours 12: 7.2; Hours 13: 7.1; Hours 14: 7.1; Hours 15: 7.1; Hours 16: 7.1; Hours 17: 6.8; Hours 18: 6.5; Hours 19: 6.3; Hours 20: 6.1; Hours 0: 7.4; Hours 1: 5.9; Hours 2: 5.4 | 6.8
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 11: 23.8; Hours 12: 23.6; Hours 13: 23.6; Hours 14: 24.2; Hours 15: 25.3; Hours 16: 24.7; Hours 17: 24.5; Hours 18: 24.4; Hours 19: 24.1; Hours 20: 23.6; Hours 0: 23.7; Hours 1: 23.7; Hours 2: 23.4 | 24.0462
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 11: 29.3; Hours 12: 29; Hours 13: 28.9; Hours 14: 29.2; Hours 15: 30.3; Hours 16: 29.8; Hours 17: 29.9; Hours 18: 29.7; Hours 19: 29.4; Hours 20: 28.8; Hours 0: 29.5; Hours 1: 29.5; Hours 2: 28.9 | 29.4
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 11: 4.3; Hours 12: 4.3; Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 0: 4.3; Hours 1: 4.3; Hours 2: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 11: 2311.9048; Hours 12: 2247.6852; Hours 13: 2119.246; Hours 14: 2087.1362; Hours 15: 2119.246; Hours 16: 2183.4656; Hours 17: 2279.795; Hours 18: 2215.5754; Hours 19: 2215.5754; Hours 20: 2183.4656; Hours 0: 2376.1243; Hours 1: 2440.3439; Hours 2: 2311.9048 | 29091.4683
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 300 | 1600 | 1400 | 1400 | 1600 | 1300 | 1500 | 1500 | 1500 | 1500 | 1000 | 0 | 0 | 500 | 1600 | 1600 | 1100 | 0 | 0 | 0 | 600 | 1700 | 21700
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 11: 0.60556; Hours 12: 0.62286; Hours 13: 0.75499; Hours 14: 0.62286; Hours 15: 0.7078; Hours 16: 0.68698; Hours 17: 0.65795; Hours 18: 0.67703; Hours 19: 0.45135; Hours 20: 0; Hours 0: 0.67337; Hours 1: 0.45076; Hours 2: 0 | 0.53165
17 | Average iKW/TR |  |  | Hours 7: 0.53165 | 0.53165
18 | COP of chiller |  |  | Hours 11: 5.8062; Hours 12: 5.6449; Hours 13: 4.657; Hours 14: 5.6449; Hours 15: 4.9675; Hours 16: 5.118; Hours 17: 5.3438; Hours 18: 5.1933; Hours 19: 7.79; Hours 0: 5.2215; Hours 1: 7.8002 | 5.7443
19 | EER of Chiller |  |  | Hours 11: 19.8165; Hours 12: 19.266; Hours 13: 15.8945; Hours 14: 19.266; Hours 15: 16.9541; Hours 16: 17.4679; Hours 17: 18.2385; Hours 18: 17.7248; Hours 19: 26.5871; Hours 0: 17.8211; Hours 1: 26.6222 | 19.6053
20 | LMTD of Condenser | ºC |  | Hours 11: 3.691; Hours 12: 3.6588; Hours 13: 3.5065; Hours 14: 3.4099; Hours 15: 3.4099; Hours 16: 3.4422; Hours 17: 3.6588; Hours 18: 3.6264; Hours 19: 3.6264; Hours 20: 3.5938; Hours 0: 3.9076; Hours 1: 3.9076; Hours 2: 3.8103 | 3.6346
21 | LMTD of Evaporator | ºC |  | Hours 11: 4.4736; Hours 12: 4.1623; Hours 13: 3.9137; Hours 14: 3.6277; Hours 15: 2.9668; Hours 16: 3.0205; Hours 17: 3.8052; Hours 18: 3.7464; Hours 19: 3.7464; Hours 20: 3.7169; Hours 0: 4.2843; Hours 1: 4.0844; Hours 2: 3.8345 | 3.7987

## 13-03-2024
Performance Sheet Chiller
Date :- 13/03/2023
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4 | 4.2 | 3.9 |  |  |  |  | 4.9 | 4.5 | 4.4 | 4.3 | 4.7 | 4.7 | 4.4 | 4.4 | 4.8 | 5.4 | 4.8 | 4.7 | 4.5 | 4.2 | 4.4 | 4.3 | 4.4 | 4.495
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.8 |  |  |  |  | 0.7 | 0.7 | 0.6 | 0.8 | 0.7 | 0.7 | 0.7 | 0.9 | 0.8 | 0.4 | 0.7 | 0.8 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.705
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.9 | 12.8 | 12.2 |  |  |  |  | 16.2 | 15.4 | 14.7 | 14.3 | 14.1 | 13.6 | 13.2 | 12.9 | 14.4 | 15.2 | 14.8 | 14 | 13.1 | 12.4 | 12.9 | 13.9 | 14.6 | 13.93 |  |  | 1300
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.7 | 5.5 | 5.5 |  |  |  |  | 7.9 | 7.5 | 6.9 | 7.1 | 6 | 5.7 | 5.4 | 5.4 | 6.1 | 6.8 | 6.6 | 5.9 | 5.5 | 5.5 | 5.6 | 5.8 | 6.1 | 6.125 |  |  | 800
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.7 | 22.3 | 22.6 |  |  |  |  | 26.4 | 25.1 | 24.3 | 24.2 | 24.3 | 23.7 | 23.7 | 23.9 | 23.9 | 24.2 | 24.3 | 24.3 | 22.7 | 22.4 | 23.1 | 23.1 | 22.7 | 23.695
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.8 | 27.8 | 27.5 |  |  |  |  | 32.5 | 30.9 | 30.1 | 29.5 | 30.2 | 29.4 | 29.4 | 29.4 | 29.9 | 30.6 | 30.3 | 30.2 | 28.1 | 27.6 | 28.4 | 29 | 28.8 | 29.42
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 |  |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  | 400
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  | 1700
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  | 1500
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  | 1400
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 |  |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  | 1500
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 |  |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  | 1500
14 | TR Genrated by Chiller | TR |  | 2633.0026 | 2344.0146 | 2151.3558 |  |  |  |  | 2665.1124 | 2536.6733 | 2504.5635 | 2311.9048 | 2600.8929 | 2536.6733 | 2504.5635 | 2408.2341 | 2665.1124 | 2697.2222 | 2633.0026 | 2600.8929 | 2440.3439 | 2215.5754 | 2344.0146 | 2600.8929 | 2729.332 | 50123.3796 |  |  | 1500
15 | Power Consumption of Chiller | KWH |  | 1300 | 800 | 400 |  |  |  | 1700 | 1500 | 1400 | 1500 | 1500 | 1500 | 1400 | 1500 | 1500 | 1600 | 1600 | 1600 | 1400 | 1200 | 1400 | 1500 | 1600 | 1700 | 29600 |  |  | 1400
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.49373 | 0.34129 | 0.18593 |  |  |  |  | 0.56283 | 0.5519 | 0.59891 | 0.64882 | 0.57673 | 0.5519 | 0.59891 | 0.62286 | 0.60035 | 0.5932 | 0.60767 | 0.53828 | 0.49173 | 0.63189 | 0.63993 | 0.61517 | 0.62286 | 0.55374 |  |  | 1500
17 | Average iKW/TR |  |  | Hours 7: 0.55374 | 0.55374 |  |  | 1500
18 | COP of chiller |  |  | 7.1213 | 10.3019 | 18.9104 |  |  |  |  | 6.247 | 6.3707 | 5.8707 | 5.4191 | 6.0965 | 6.3707 | 5.8707 | 5.6449 | 5.8566 | 5.9271 | 5.786 | 6.532 | 7.1502 | 5.5643 | 5.4944 | 5.7155 | 5.6449 | 6.8947 |  |  | 1600
19 | EER of Chiller |  |  | 24.3049 | 35.1605 | 64.5413 |  |  |  |  | 21.3211 | 21.7431 | 20.0367 | 18.4954 | 20.8073 | 21.7431 | 20.0367 | 19.266 | 19.9885 | 20.2293 | 19.7477 | 22.2936 | 24.4037 | 18.9908 | 18.7523 | 19.5069 | 19.266 | 23.5317 |  |  | 1600
20 | LMTD of Condenser | ºC |  | 6.5858 | 6.5708 | 6.0213 |  |  |  |  | 7.5433 | 7.0043 | 6.8983 | 6.599 | 7.2545 | 7.1766 | 6.8598 | 6.7823 | 7.3989 | 8.1873 | 7.3989 | 7.2545 | 6.8488 | 6.4546 | 6.7044 | 6.8305 | 7.0133 | 6.9694 |  |  | 1600
21 | LMTD of Evaporator | ºC |  | 3.0533 | 2.832 | 2.9937 |  |  |  |  | 3.2499 | 3.1494 | 2.9556 | 3.1269 | 3.1998 | 3.1494 | 3.1241 | 3.3578 | 3.4136 | 2.7175 | 3.2249 | 3.3621 | 3.0733 | 2.8933 | 2.9966 | 3.3621 | 3.2998 | 3.1268 |  |  | 1400
Performance Sheet Chiller | [30 empty] | 1200
Date :- 13/03/2023 | [30 empty] | 1400
|  |  |  | Hours 7: CHILLER NO. 5 |  |  |  | 1500
Design Chilled Water Flow Qed(m3/hr): 971 | [30 empty] | 1600
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53 | [30 empty] | 1700
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.9 | 1.7 | 1.7 | 1.8 | 1.7 | 1.7 | 1.8 | 1.7 |  |  |  | 1.7 | 1.7 | 1.8 | 1.8 |  |  |  | 1.7444 | 28.7 | 23.1 | 14.3 | 6.8 | 1500
2 | Small temperature difference of evaporator | ºC |  | 1.6 | 1.6 | 1.4 | 1.4 | 1.5 | 1.7 | 1.4 | 1.5 | 1.6 | 1.6 | 1.4 | 1.4 | 1.3 | 1.4 |  |  |  | 1.6 | 1.3 | 1.4 | 1.3 |  |  |  | 1.4667 | 28.3 | 22.7 | 12.9 | 5.6 | 1500
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.3 | 12.9 | 12.4 | 12.5 | 14.1 | 14.9 | 15.7 | 16.5 | 15.6 | 15.1 | 14.6 | 14.4 | 13.8 | 13.4 |  |  |  | 15.2 | 14.3 | 13.4 | 12.7 |  |  |  | 14.2111 | 28.2 | 22.7 | 12.4 | 5.4 | 1400
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.8 | 5.6 | 5.4 | 5.6 | 6.8 | 7.7 | 8.3 | 9.4 | 8.5 | 7.8 | 7.4 | 7 | 6.6 | 6.2 |  |  |  | 7.9 | 7 | 6.2 | 5.7 |  |  |  | 6.9944 | 27.8 | 22.6 | 12.5 | 5.6 | 1700
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.1 | 22.7 | 22.7 | 22.6 | 22.8 | 23.2 | 24.9 | 26.7 | 25.3 | 24.6 | 24.6 | 24.6 | 24 | 24.1 |  |  |  | 24.6 | 24.7 | 23.1 | 22.7 |  |  |  | 23.9444 | 28.6 | 22.8 | 14.1 | 6.8 | 1600
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.7 | 28.3 | 28.2 | 27.8 | 28.6 | 28.9 | 30.7 | 32.2 | 30.9 | 30.1 | 30 | 30.1 | 29.6 | 29.6 |  |  |  | 30.1 | 30.1 | 28.4 | 28 |  |  |  | 29.4611 | 28.9 | 23.2 | 14.9 | 7.7 | 1500
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  | 4.3 | 30.7 | 24.9 | 15.7 | 8.3 | 1600
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 32.2 | 26.7 | 16.5 | 9.4 | 1500
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 30.9 | 25.3 | 15.6 | 8.5 | 1500
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3 | 3 | 3 | 3 |  |  |  | 3 | 30.1 | 24.6 | 15.1 | 7.8 | 1600
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 30 | 24.6 | 14.6 | 7.4 | 1500
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8 | 30.1 | 24.6 | 14.4 | 7 | 1600
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  | 971 | 971 | 971 | 971 |  |  |  | 971 | 29.6 | 24 | 13.8 | 6.6 | 1500
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2344.0146 | 2247.6852 | 2215.5754 | 2344.0146 | 2311.9048 | 2376.1243 | 2279.795 | 2279.795 | 2344.0146 | 2311.9048 | 2376.1243 | 2311.9048 | 2311.9048 |  |  |  | 2344.0146 | 2344.0146 | 2311.9048 | 2247.6852 |  |  |  | 41710.6151 | 29.6 | 24.1 | 13.4 | 6.2 | 200
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1400 | 1700 | 1600 | 1500 | 1600 | 1500 | 1500 | 1600 | 1500 | 1600 | 1500 | 200 | 0 | 0 | 500 | 1700 | 1500 | 1500 | 900 |  |  |  | 26300 | 23.9 | 24.2 | 13.1 | 13.2 | 0
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.62286 | 0.63993 | 0.62286 | 0.7673 | 0.68259 | 0.64882 | 0.67337 | 0.65795 | 0.65795 | 0.68259 | 0.64882 | 0.67337 | 0.64882 | 0.086509 |  |  |  | 0.72525 | 0.63993 | 0.64882 | 0.40041 |  |  |  | 0.61823 | 24.2 | 24.3 | 14.5 | 14.6 | 500
17 | Average iKW/TR |  |  | Hours 7: 0.61823 | 0.61823 | 24.5 | 24.3 | 15.3 | 15.3 | 1700
18 | COP of chiller |  |  | 5.6449 | 5.4944 | 5.6449 | 4.5823 | 5.151 | 5.4191 | 5.2215 | 5.3438 | 5.3438 | 5.151 | 5.4191 | 5.2215 | 5.4191 | 40.6433 |  |  |  | 4.848 | 5.4944 | 5.4191 | 8.781 |  |  |  | 7.4579 | 30.1 | 24.6 | 15.2 | 7.9 | 1500
19 | EER of Chiller |  |  | 19.266 | 18.7523 | 19.266 | 15.6395 | 17.5803 | 18.4954 | 17.8211 | 18.2385 | 18.2385 | 17.5803 | 18.4954 | 17.8211 | 18.4954 | 138.7155 |  |  |  | 16.5461 | 18.7523 | 18.4954 | 29.9694 |  |  |  | 25.4538 | 30.1 | 24.7 | 14.3 | 7 | 1500
20 | LMTD of Condenser | ºC |  | 3.9613 | 3.8429 | 3.8103 | 3.7119 | 3.9076 | 3.9941 | 4.1447 | 3.8103 | 3.8429 | 3.9283 | 3.7776 | 3.8103 | 3.9613 | 3.8103 |  |  |  | 3.8103 | 3.7776 | 3.8621 | 3.8621 |  |  |  | 3.8681 | 28.4 | 23.1 | 13.4 | 6.2 | 900
21 | LMTD of Evaporator | ºC |  | 4.3146 | 4.254 | 3.9068 | 3.8769 | 4.126 | 4.3493 | 4.0255 | 4.0657 | 4.1929 | 4.254 | 3.9663 | 4.0255 | 3.8345 | 3.9663 |  |  |  | 4.254 | 3.8637 | 3.9663 | 3.7758 |  |  |  | 4.0566 | 28 | 22.7 | 12.7 | 5.7 | 0
[29 empty] | 23.2 | 23.2 | 12.9 | 13 | 0
[29 empty] | 23.5 | 23.6 | 14.2 | 14.2 | 0
[29 empty] | 23.4 | 23.5 | 14.7 | 14.9 | 0

## 14-03-2023
Performance Sheet Chiller
Date :- 14/03/2023
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4.7 | 4.7 | 4.1 |  |  |  | 4.5 | 4.3 | 4.4 | 4.7 | 4.6 | 4.6 | 4.4 | 4.4 | 4.4 | 4.6 | 4.9 | 6.2 | 4.9 | 4.4 | 4.2 | 3.9 | 4.2 | 4.8 | 4.5667
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.7 |  |  |  | 0.7 | 0.8 | 1.1 | 0.6 | 0.7 | 0.6 | 0.7 | 0.6 | 0.5 | 0.6 | 0.7 | 0.4 | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.7 | 0.69048
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.8 | 13.4 | 12.6 |  |  |  | 15.3 | 14.4 | 14.1 | 14.1 | 13.9 | 13.9 | 13.5 | 13.3 | 13.4 | 13.1 | 14.6 | 15.2 | 14.7 | 13.1 | 12.4 | 12 | 12.9 | 14.1 | 13.7524
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 5.2 | 5.4 |  |  |  | 7.2 | 6.9 | 7 | 5.9 | 5.9 | 5.8 | 5.6 | 5.5 | 5.5 | 5.5 | 6.2 | 6.6 | 6.2 | 5.4 | 5.3 | 5.8 | 5.8 | 5.7 | 5.9381
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.8 | 21.9 | 21.9 |  |  |  | 24.3 | 25.1 | 25.2 | 25.2 | 26 | 25.1 | 24.9 | 24.4 | 24.4 | 23.9 | 23.5 | 24.2 | 23.1 | 23.2 | 23.2 | 23.2 | 23.2 | 23.2 | 23.9
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.8 | 27.6 | 27 |  |  |  | 30.1 | 30.6 | 30.4 | 30.8 | 31.8 | 30.8 | 30.6 | 29.9 | 30 | 29.4 | 29.4 | 30.3 | 29.1 | 28.6 | 28.1 | 27.9 | 28.4 | 29.1 | 29.4619
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2729.332 | 2633.0026 | 2311.9048 |  |  |  | 2600.8929 | 2408.2341 | 2279.795 | 2633.0026 | 2568.7831 | 2600.8929 | 2536.6733 | 2504.5635 | 2536.6733 | 2440.3439 | 2697.2222 | 2761.4418 | 2729.332 | 2472.4537 | 2279.795 | 1990.8069 | 2279.795 | 2697.2222 | 52692.1627
15 | Power Consumption of Chiller | KWH |  | 1400 | 900 | 0 | 0 | 0 | 1300 | 1400 | 1500 | 1500 | 1600 | 1400 | 1700 | 1400 | 1500 | 1400 | 1600 | 1500 | 1800 | 1400 | 1300 | 1200 | 1300 | 1500 | 1600 | 30200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.51295 | 0.34182 | 0 |  |  |  | 0.53828 | 0.62286 | 0.65795 | 0.60767 | 0.54501 | 0.65362 | 0.5519 | 0.59891 | 0.5519 | 0.65565 | 0.55613 | 0.65183 | 0.51295 | 0.52579 | 0.52636 | 0.653 | 0.65795 | 0.5932 | 0.54837
17 | Average iKW/TR |  |  | Hours 7: 0.54837 | 0.54837
18 | COP of chiller |  |  | 6.8545 | 10.2863 |  |  |  |  | 6.532 | 5.6449 | 5.3438 | 5.786 | 6.4513 | 5.3793 | 6.3707 | 5.8707 | 6.3707 | 5.3627 | 6.3223 | 5.394 | 6.8545 | 6.687 | 6.6798 | 5.3844 | 5.3438 | 5.9271 | 6.2423
19 | EER of Chiller |  |  | 23.3945 | 35.107 |  |  |  |  | 22.2936 | 19.266 | 18.2385 | 19.7477 | 22.0183 | 18.3594 | 21.7431 | 20.0367 | 21.7431 | 18.3027 | 21.578 | 18.4098 | 23.3945 | 22.8229 | 22.7982 | 18.3768 | 18.2385 | 20.2293 | 21.3049
20 | LMTD of Condenser | ºC |  | 7.2932 | 7.1766 | 6.3102 |  |  |  | 7.0043 | 6.6766 | 6.6653 | 7.1376 | 7.11 | 7.0712 | 6.8598 | 6.7823 | 6.8211 | 6.9932 | 7.4654 | 8.9045 | 7.5044 | 6.7434 | 6.3374 | 5.9435 | 6.4546 | 7.36 | 6.9817
21 | LMTD of Evaporator | ºC |  | 3.2998 | 3.2249 | 2.9709 |  |  |  | 3.1998 | 3.206 | 3.5344 | 3.0533 | 3.1746 | 3.029 | 3.1494 | 2.9556 | 2.8 | 2.9064 | 3.2749 | 2.7622 | 3.2998 | 3.0987 | 2.9451 | 2.8584 | 3.1004 | 3.2749 | 3.1009
Performance Sheet Chiller
Date :- 14/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.6 | 1.5 | 1.5 | 1.5 | 1.5 | 1.6 | 1.7 | 1.6 | 1.1 | 1.7 | 1.4 | 1.4 | 1.3 | 1.3 | 1.3 |  |  |  | 1.5 | 1.2 | 1.3 | 1.4 |  |  | 1.4421
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.8 | 0.8 | 0.8 | 0.9 | 0.7 | 0.7 | 0.7 | 0.8 |  |  |  | 0.8 | 0.7 | 0.7 | 0.7 |  |  | 0.74737
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.9 | 13.9 | 12.8 | 12.8 | 14.3 | 14.9 | 15.4 | 14.8 | 14.4 | 14.3 | 14 | 14.4 | 13.8 | 13.5 | 13.7 |  |  |  | 15.1 | 13.4 | 12.5 | 12.4 |  |  | 13.9632
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.9 | 5.9 | 5.5 | 5.6 | 6.2 | 6.8 | 7.9 | 7.3 | 6.9 | 6.8 | 6.8 | 6.6 | 6.3 | 6 | 6.1 |  |  |  | 7 | 6 | 5.6 | 5.8 |  |  | 6.4211
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.3 | 22.1 | 22.2 | 22.1 | 22.6 | 23.3 | 24.6 | 25.4 | 25.2 | 25.4 | 26.1 | 25.3 | 24.9 | 24.7 | 24.7 |  |  |  | 23.3 | 23.2 | 23.3 | 23.3 |  |  | 23.9474
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.2 | 28.1 | 27.7 | 27.3 | 28.6 | 29.4 | 30.2 | 31.1 | 31.1 | 31.1 | 31.9 | 31.3 | 31.2 | 30.4 | 30.6 |  |  |  | 29.6 | 29.1 | 28.6 | 28.3 |  |  | 29.7263
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  |  |  | 4.2 | 4.2 | 4.2 | 4.2 |  |  | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 |  |  |  | 3.6 | 3.6 | 3.6 | 3.6 |  |  | 3.6
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 |  |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3 | 3 | 3 | 3 |  |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  | 0.6 | 0.6 | 0.6 | 0.6 |  |  | 0.6
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 |  |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 |  |  |  | 1063.6772 | 1063.6772 | 1063.6772 | 1063.6772 |  |  | 1063.6772
14 | TR Genrated by Chiller | TR |  | 2813.9609 | 2813.9609 | 2567.7393 | 2532.5648 | 2849.1354 | 2849.1354 | 2638.0883 | 2638.0883 | 2638.0883 | 2638.0883 | 2532.5648 | 2743.6118 | 2638.0883 | 2638.0883 | 2673.2628 |  |  |  | 2849.1354 | 2602.9138 | 2427.0412 | 2321.5177 |  |  | 50405.074
15 | Power Consumption of Chiller | KWH |  | 1600 | 1400 | 1300 | 1600 | 1600 | 1600 | 1400 | 1600 | 1500 | 1600 | 1400 | 1600 | 1600 | 1400 | 0 | 0 | 0 | 400 | 1700 | 1400 | 1400 | 800 |  |  | 26900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.56859 | 0.49752 | 0.50628 | 0.63177 | 0.56157 | 0.56157 | 0.53069 | 0.6065 | 0.56859 | 0.6065 | 0.5528 | 0.58317 | 0.6065 | 0.53069 |  |  |  |  | 0.59667 | 0.53786 | 0.57683 | 0.3446 |  |  | 0.55382
17 | Average iKW/TR |  |  | Hours 7: 0.55382 | 0.55382
18 | COP of chiller |  |  | 6.1837 | 7.0671 | 6.9447 | 5.5653 | 6.261 | 6.261 | 6.6254 | 5.7972 | 6.1837 | 5.7972 | 6.3604 | 6.0291 | 5.7972 | 6.6254 |  |  |  |  | 5.8927 | 6.537 | 6.0953 | 10.2031 |  |  | 6.457
19 | EER of Chiller |  |  | 21.1049 | 24.1199 | 23.7024 | 18.9944 | 21.3687 | 21.3687 | 22.6124 | 19.7858 | 21.1049 | 19.7858 | 21.7079 | 20.5773 | 19.7858 | 22.6124 |  |  |  |  | 20.1117 | 22.3109 | 20.8034 | 34.8231 |  |  | 22.0378
20 | LMTD of Condenser | ºC |  | 3.819 | 3.728 | 3.5704 | 3.4744 | 3.728 | 3.8823 | 3.8429 | 3.7553 | 3.1882 | 3.8753 | 3.5417 | 3.6036 | 3.5678 | 3.3857 | 3.4468 |  |  |  | 3.8213 | 3.3188 | 3.2621 | 3.2899 |  |  | 3.5843
21 | LMTD of Evaporator | ºC |  | 3.3363 | 3.1746 | 2.9966 | 2.9709 | 3.1998 | 3.3621 | 3.0478 | 3.206 | 3.206 | 3.206 | 3.2769 | 3.1241 | 3.0478 | 3.0478 | 3.2322 |  |  |  | 3.3621 | 3.0222 | 2.8933 | 2.815 |  |  | 3.133

## 15-03-2023
Performance Sheet Chiller
Date :- 15/03/2023
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4.9 | 5.1 | 4.6 | 4.1 | 3.9 | 3.6 | 3.7 | 3.4 | 3.9 | 3.9 | 4.6 | 4.3 | 4.3 | 4.4 | 4.6 |  |  | 4.5 | 4.6 | 4.6 | 4.4 | 4.4 | 4.3 | 4.3 | 4.2909
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.8 | 0.7 | 0.7 | 0.9 | 1.3 | 1 | 1.1 | 1.1 | 1.1 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.73636
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.6 | 14.9 | 15.1 | 13.6 | 13.2 | 12.8 | 13 | 13.2 | 13.4 | 13.7 | 13.8 | 13.6 | 13.7 | 13.7 | 13.7 |  |  | 16.3 | 15.1 | 14.4 | 13.9 | 13.5 | 13.2 | 13.2 | 13.8909
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6 | 6.3 | 6.8 | 6.9 | 6.8 | 7.2 | 7 | 7.1 | 6.9 | 7 | 5.8 | 5.7 | 5.8 | 5.9 | 5.8 |  |  | 8.1 | 6.8 | 6.4 | 6 | 5.8 | 5.7 | 5.4 | 6.4182
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.1 | 22.7 | 23.1 | 22.7 | 23 | 23.1 | 23.1 | 24.8 | 24.7 | 25 | 25.5 | 26 | 26.2 | 26.8 | 26.3 |  |  | 26.7 | 26.4 | 26.2 | 26.4 | 26.7 | 26.6 | 26.2 | 25.0591
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.1 | 28.6 | 28.8 | 27.6 | 27.7 | 27.6 | 27.3 | 29.4 | 29.6 | 29.7 | 31.1 | 31.5 | 31.9 | 32.4 | 31.9 |  |  | 32.3 | 32.2 | 31.8 | 32.1 | 32.2 | 32.1 | 31.8 | 30.3955
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  |  | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 |  |  | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7 | 3.7
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2761.4418 | 2761.4418 | 2665.1124 | 2151.3558 | 2055.0265 | 1798.1481 | 1926.5873 | 1958.6971 | 2087.1362 | 2151.3558 | 2568.7831 | 2536.6733 | 2536.6733 | 2504.5635 | 2536.6733 |  |  | 2633.0026 | 2665.1124 | 2568.7831 | 2536.6733 | 2472.4537 | 2408.2341 | 2504.5635 | 52788.4921
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1200 | 1100 | 1200 | 1100 | 1200 | 1300 | 1300 | 1600 | 1500 | 1600 | 1500 | 1100 | 0 | 200 | 1600 | 1600 | 1500 | 1600 | 1500 | 1600 | 1400 | 1400 | 31200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.54319 | 0.57941 | 0.45026 | 0.51131 | 0.58393 | 0.61174 | 0.62286 | 0.66371 | 0.62286 | 0.74372 | 0.58393 | 0.63075 | 0.59133 | 0.4392 |  |  |  | 0.60767 | 0.56283 | 0.62286 | 0.59133 | 0.64713 | 0.58134 | 0.55898 | 0.58811
17 | Average iKW/TR |  |  | Hours 7: 0.58811 | 0.58811
18 | COP of chiller |  |  | 6.4728 | 6.0683 | 7.8088 | 6.8765 | 6.0212 | 5.7475 | 5.6449 | 5.2975 | 5.6449 | 4.7276 | 6.0212 | 5.5743 | 5.946 | 8.0055 |  |  |  | 5.786 | 6.247 | 5.6449 | 5.946 | 5.4332 | 6.0481 | 6.29 | 6.0596
19 | EER of Chiller |  |  | 22.0917 | 20.711 | 26.6514 | 23.4695 | 20.5504 | 19.6163 | 19.266 | 18.0804 | 19.266 | 16.1353 | 20.5504 | 19.0252 | 20.2936 | 27.3228 |  |  |  | 19.7477 | 21.3211 | 19.266 | 20.2936 | 18.5436 | 20.6422 | 21.4679 | 20.6815
20 | LMTD of Condenser | ºC |  | 7.5044 | 7.6757 | 7.0712 | 6.2322 | 5.9435 | 5.5492 | 5.537 | 5.3759 | 6.0213 | 5.9435 | 7.0322 | 6.6766 | 6.7538 | 6.8211 | 7.0322 |  |  | 6.9268 | 7.11 | 7.0322 | 6.8598 | 6.7823 | 6.6766 | 6.7153 | 6.6033
21 | LMTD of Evaporator | ºC |  | 3.3247 | 3.4905 | 3.2499 | 2.8412 | 3.0575 | 3.355 | 3.0834 | 3.2468 | 3.3629 | 3.4204 | 3.0046 | 2.9801 | 2.9801 | 2.9556 | 2.9801 |  |  | 2.6727 | 2.8941 | 3.0046 | 2.9801 | 2.931 | 2.7051 | 2.9556 | 3.0671
Performance Sheet Chiller
Date :- 15/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 1.6 | 1.4 | 1.4 | 1.1 | 1.5 | 1.4 | 1.4 | 1.3 | 1.7 | 1.5 | 1.4 | 1.3 | 1.5 | 1.7 | 1.5 | 1.4 | 1.4 | 1.3 | 1.4 | 1.4 | 1.7 | 1.4 | 1.4409
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.8 | 0.6 | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.8 | 0.7 | 0.8 | 0.7 | 0.8 | 0.8 | 0.7 | 0.75455
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 15.4 | 13.8 | 13.6 | 13.1 | 13.3 | 13.6 | 13.6 | 14 | 14.1 | 13.8 | 13.9 | 13.8 | 13.9 | 14.1 | 15.6 | 16.4 | 15.4 | 14.6 | 14.2 | 13.9 | 13.4 | 13.4 | 14.1318
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 7.8 | 6.9 | 6.9 | 6.9 | 7.1 | 6.9 | 7.2 | 7.1 | 6.9 | 6.9 | 6.8 | 6.7 | 6.4 | 6.6 | 8.1 | 8.7 | 7.8 | 7 | 6.7 | 6.4 | 6.3 | 6.1 | 7.0091
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 23.3 | 22.8 | 23.3 | 23.3 | 23.1 | 24.8 | 24.9 | 25.1 | 25.5 | 26.3 | 26.5 | 27 | 26.3 | 26.4 | 26.9 | 26.8 | 26.5 | 26.4 | 26.6 | 26.7 | 26.8 | 26.3 | 25.5273
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 29 | 28.3 | 28.2 | 28 | 27.9 | 30.2 | 29.9 | 30.4 | 30.9 | 31.5 | 32.2 | 32.6 | 32 | 32.2 | 32.8 | 32.7 | 32.4 | 32.2 | 32.3 | 32.6 | 32.2 | 32 | 31.0227
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2440.3439 | 2215.5754 | 2151.3558 | 1990.8069 | 1990.8069 | 2151.3558 | 2055.0265 | 2215.5754 | 2311.9048 | 2215.5754 | 2279.795 | 2279.795 | 2408.2341 | 2408.2341 | 2408.2341 | 2472.4537 | 2440.3439 | 2440.3439 | 2408.2341 | 2408.2341 | 2279.795 | 2344.0146 | 50316.0384
15 | Power Consumption of Chiller | KWH |  | 200 | 1500 | 1300 | 1300 | 1200 | 1200 | 1300 | 1500 | 1400 | 1500 | 1400 | 1600 | 1500 | 1600 | 1500 | 1700 | 1500 | 1600 | 1500 | 1600 | 1600 | 1600 | 1500 | 1500 | 34100
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.53271 | 0.58676 | 0.55779 | 0.60277 | 0.653 | 0.69723 | 0.68126 | 0.67703 | 0.60556 | 0.72216 | 0.65795 | 0.70182 | 0.62286 | 0.70591 | 0.62286 | 0.64713 | 0.61467 | 0.65565 | 0.66439 | 0.66439 | 0.65795 | 0.63993 | 0.64417
17 | Average iKW/TR |  |  | Hours 7: 0.64417 | 0.64417
18 | COP of chiller |  |  |  |  | 6.6002 | 5.9923 | 6.3035 | 5.8331 | 5.3844 | 5.0428 | 5.1611 | 5.1933 | 5.8062 | 4.8687 | 5.3438 | 5.0098 | 5.6449 | 4.9808 | 5.6449 | 5.4332 | 5.7202 | 5.3627 | 5.2921 | 5.2921 | 5.3438 | 5.4944 | 5.4886
19 | EER of Chiller |  |  |  |  | 22.5265 | 20.4516 | 21.5138 | 19.9082 | 18.3768 | 17.211 | 17.6147 | 17.7248 | 19.8165 | 16.617 | 18.2385 | 17.0986 | 19.266 | 16.9995 | 19.266 | 18.5436 | 19.5229 | 18.3027 | 18.0619 | 18.0619 | 18.2385 | 18.7523 | 18.7324
20 | LMTD of Condenser | ºC |  |  |  | 3.7553 | 3.4482 | 3.2578 | 2.827 | 3.3448 | 3.4167 | 3.2899 | 3.2621 | 3.7776 | 3.4744 | 3.5107 | 3.355 | 3.6338 | 3.9076 | 3.6967 | 3.5727 | 3.5727 | 3.4163 | 3.5107 | 3.5727 | 3.7776 | 3.5107 | 3.495
21 | LMTD of Evaporator | ºC |  |  |  | 3.2322 | 2.7319 | 2.8412 | 2.7096 | 2.7096 | 2.9937 | 2.9128 | 3.0472 | 3.1269 | 2.8933 | 3.1004 | 3.1004 | 3.206 | 3.206 | 3.0478 | 3.2583 | 3.0733 | 3.2322 | 3.0478 | 3.206 | 3.1004 | 2.9966 | 3.0351

## 16-03-2023
Performance Sheet Chiller
Date :- 16/03/2023
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 4.1 | 4.1 | 4.2 | 4.3 | 3.9 | 3.9 | 3.9 | 3.8 | 4.1 | 4 | 4.2 | 4.4 | 4.3 | 4.3 | 4.7 | 4.4 | 4.3 | 4 | [6 empty] | 4.1611
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.7 | 0.9 | 1 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.6 | 0.6 | 0.8 | 1.1 | [6 empty] | 0.68889
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.3 | 13.5 | 13.3 | 13.2 | 13.2 | 13.2 | 13.4 | 13.9 | 14.5 | 14.7 | 15.1 | 15.2 | 15.1 | 14.6 | 13.8 | 13.2 | 12.7 | [6 empty] | 13.8333
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.9 | 6.1 | 5.7 | 5.6 | 6.7 | 6.8 | 6.4 | 7 | 7.1 | 7.1 | 7.2 | 7.2 | 7.2 | 7.1 | 6.2 | 5.8 | 5.9 | 5.6 | [6 empty] | 6.4778
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.7 | 25.6 | 25.5 | 25.3 | 24.5 | 23.9 | 23.8 | 25.6 | 26.6 | 27.2 | 27.6 | 27.6 | 27.1 | 27.1 | 23.7 | 23.3 | 22.8 | 22.9 | [6 empty] | 25.3222
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.9 | 30.8 | 31.1 | 30.7 | 29.3 | 28.8 | 28.8 | 30.1 | 31.4 | 32.8 | 33.2 | 33.2 | 32.8 | 32.6 | 29.6 | 29 | 28.1 | 28.2 | [6 empty] | 30.6333
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [6 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [6 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [6 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [6 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [6 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [6 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [6 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2311.9048 | 2311.9048 | 2504.5635 | 2472.4537 | 2087.1362 | 2055.0265 | 2183.4656 | 2055.0265 | 2183.4656 | 2376.1243 | 2408.2341 | 2536.6733 | 2568.7831 | 2568.7831 | 2697.2222 | 2568.7831 | 2344.0146 | 2279.795 | [6 empty] | 42513.3598
15 | Power Consumption of Chiller | KWH |  | 1400 | 1600 | 1400 | 1200 | 1300 | 1200 | 1300 | 1300 | 1400 | 1600 | 1500 | 1600 | 1500 | 1600 | 1400 | 1400 | 1200 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 24900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.60556 | 0.69207 | 0.55898 | 0.48535 | 0.62286 | 0.58393 | 0.59538 | 0.6326 | 0.64118 | 0.67337 | 0.62286 | 0.63075 | 0.58393 | 0.62286 | 0.51905 | 0.54501 | 0.51194 | 0.43864 | [6 empty] | 0.58702
17 | Average iKW/TR |  |  | Hours 7: 0.58702 | 0.58702
18 | COP of chiller |  |  | 5.8062 | 5.0804 | 6.29 | 7.2443 | 5.6449 | 6.0212 | 5.9054 | 5.5581 | 5.4836 | 5.2215 | 5.6449 | 5.5743 | 6.0212 | 5.6449 | 6.7739 | 6.4513 | 6.868 | 8.0158 | [6 empty] | 6.0694
19 | EER of Chiller |  |  | 19.8165 | 17.3394 | 21.4679 | 24.7248 | 19.266 | 20.5504 | 20.1552 | 18.9696 | 18.7156 | 17.8211 | 19.266 | 19.0252 | 20.5504 | 19.266 | 23.1193 | 22.0183 | 23.4404 | 27.3578 | [6 empty] | 20.715
20 | LMTD of Condenser | ºC |  | 6.349 | 6.349 | 6.6092 | 6.6379 | 5.9825 | 6.0213 | 6.0601 | 5.76 | 6.193 | 6.3966 | 6.6092 | 6.8211 | 6.7538 | 6.6766 | 7.2545 | 6.8598 | 6.599 | 6.2817 | [6 empty] | 6.4564
21 | LMTD of Evaporator | ºC |  | 2.9709 | 2.9709 | 2.9556 | 2.931 | 2.6306 | 2.7625 | 3.1678 | 3.1976 | 2.8673 | 2.8568 | 2.8816 | 2.9801 | 2.8236 | 2.8236 | 3.1019 | 3.0046 | 3.1533 | 3.5344 | [6 empty] | 2.9786
Performance Sheet Chiller
Date :- 16/03/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | #DIV/0!
2 | Small temperature difference of evaporator | ºC | [25 empty] | #DIV/0!
3 | Entering Chilled Water Temp. (tchwe) | ºC | [25 empty] | #DIV/0!
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [25 empty] | #DIV/0!
5 | Entering Condenser Water Temp. (tcwe) | ºC | [25 empty] | #DIV/0!
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [25 empty] | #DIV/0!
7 | Chilled water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
8 | Chilled water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
9 | Condenser water inlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
10 | Condenser water outlet pressure | (Kg/Cm2) | [25 empty] | #DIV/0!
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [25 empty] | #DIV/0!
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [25 empty] | #DIV/0!
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [25 empty] | #DIV/0!
14 | TR Genrated by Chiller | TR | [25 empty] | 0
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1500 | 1800
16 | Specific power consumption of Chiller | (iKW/TR) | [25 empty] | #DIV/0!
17 | Average iKW/TR |  |  | Hours 7: #DIV/0! | #DIV/0!
18 | COP of chiller | [26 empty] | #DIV/0!
19 | EER of Chiller | [26 empty] | #DIV/0!
20 | LMTD of Condenser | ºC | [25 empty] | #DIV/0!
21 | LMTD of Evaporator | ºC | [25 empty] | #DIV/0!
Performance Sheet Chiller
Date :- 16/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.4 | 1.4 | 1.3 | 1.4 | 1.4 | 1.4 | 1.3 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.6 | 1.7 | 1.6 | 1.4 | 1.8 | 1.6 | 1.7 | 1.8 | 1.5 | 1.7 | 1.4917
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.6 | 0.7 | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.8 | 0.7 | 0.74167
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.2 | 13.7 | 13.7 | 13.6 | 13.2 | 13.6 | 13.3 | 13.6 | 14.2 | 14.7 | 15.2 | 15.2 | 15.3 | 15.4 | 14.4 | 14.1 | 13.5 | 12.9 | 12.7 | 12.7 | 13.9 | 14.7 | 15.1 | 15.4 | 14.0542
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.2 | 6.2 | 6.2 | 6.2 | 6.6 | 6.4 | 6.8 | 7 | 7 | 7.4 | 7.8 | 8.2 | 8.2 | 8.2 | 7.1 | 6.4 | 6.1 | 5.7 | 5.5 | 5.6 | 6.4 | 6.8 | 7.2 | 7.5 | 6.7792
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.9 | 25.7 | 25.4 | 25.6 | 24.7 | 23.9 | 24.2 | 25.4 | 26.4 | 27.3 | 27.9 | 27.6 | 27.4 | 27.3 | 23.8 | 23.5 | 22.9 | 23.2 | 23.2 | 23.2 | 23.6 | 23.5 | 23.2 | 23.4 | 24.925
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.3 | 31.2 | 31.4 | 31 | 29.9 | 29.4 | 29.3 | 30.5 | 32 | 33.1 | 33.3 | 33.1 | 32.6 | 33 | 29.7 | 29.3 | 28.4 | 28.7 | 28.9 | 28.8 | 29.5 | 29.3 | 28.9 | 29.3 | 30.4958
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2247.6852 | 2408.2341 | 2408.2341 | 2376.1243 | 2119.246 | 2311.9048 | 2087.1362 | 2119.246 | 2311.9048 | 2344.0146 | 2376.1243 | 2247.6852 | 2279.795 | 2311.9048 | 2344.0146 | 2472.4537 | 2376.1243 | 2311.9048 | 2311.9048 | 2279.795 | 2408.2341 | 2536.6733 | 2536.6733 | 2536.6733 | 56063.6905
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1500 | 1400 | 1400 | 1400 | 1300 | 1400 | 1600 | 1500 | 1500 | 1500 | 1500 | 1600 | 1400 | 1500 | 1400 | 1400 | 1600 | 1500 | 1400 | 1600 | 1500 | 1400 | 35400
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.66735 | 0.66439 | 0.62286 | 0.58919 | 0.66061 | 0.60556 | 0.62286 | 0.66061 | 0.69207 | 0.63993 | 0.63128 | 0.66735 | 0.65795 | 0.69207 | 0.59727 | 0.60668 | 0.58919 | 0.60556 | 0.69207 | 0.65795 | 0.58134 | 0.63075 | 0.59133 | 0.5519 | 0.63242
17 | Average iKW/TR |  |  | Hours 7: 0.63242 | 0.63242
18 | COP of chiller |  |  | 5.2686 | 5.2921 | 5.6449 | 5.9675 | 5.3223 | 5.8062 | 5.6449 | 5.3223 | 5.0804 | 5.4944 | 5.5696 | 5.2686 | 5.3438 | 5.0804 | 5.8868 | 5.7954 | 5.9675 | 5.8062 | 5.0804 | 5.3438 | 6.0481 | 5.5743 | 5.946 | 6.3707 | 5.5802
19 | EER of Chiller |  |  | 17.9816 | 18.0619 | 19.266 | 20.367 | 18.1651 | 19.8165 | 19.266 | 18.1651 | 17.3394 | 18.7523 | 19.0092 | 17.9816 | 18.2385 | 17.3394 | 20.0917 | 19.7798 | 20.367 | 19.8165 | 17.3394 | 18.2385 | 20.6422 | 19.0252 | 20.2936 | 21.7431 | 19.0453
20 | LMTD of Condenser | ºC |  | 3.4167 | 3.4482 | 3.4772 | 3.4167 | 3.3535 | 3.4482 | 3.1996 | 3.3218 | 3.4795 | 3.5417 | 3.4167 | 3.4482 | 3.3535 | 3.5107 | 3.819 | 3.9076 | 3.691 | 3.4482 | 3.9941 | 3.7232 | 3.9398 | 4.0268 | 3.6338 | 3.9398 | 3.5815
21 | LMTD of Evaporator | ºC |  | 3.0739 | 3.206 | 3.206 | 3.0222 | 2.815 | 2.8071 | 2.7888 | 2.656 | 2.9709 | 3.1533 | 3.1797 | 3.0739 | 3.1004 | 3.1269 | 3.1533 | 3.2583 | 3.0222 | 2.9709 | 2.9709 | 3.1004 | 3.0478 | 3.1494 | 3.3103 | 3.1494 | 3.0547

## 17-03-2023
Performance Sheet Chiller
Date :- 17/03/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.7 | 1.7 | 1.7 | 1.5 | 1.8 | 1.7 | 1.7 | 1.6 | 1.7 | 1.6 | 1.7 | 1.6 | 1.5 | 1.5 | 1.6 | 1.6 | 1.5 | 1.5 | 1.6 | 1.6 | 1.6 | 1.5 | 1.6 | 1.6 | 1.6125
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.7 | 0.7 | 0.9 | 0.7 | 0.8 | 0.7 | 0.8 | 0.8 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.7375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.8 | 14.3 | 13.2 | 12.6 | 13.7 | 14.7 | 15.4 | 15.3 | 15.1 | 15 | 14.9 | 14.9 | 14.8 | 14.7 | 14.6 | 14.2 | 14.1 | 13.9 | 13.7 | 13.5 | 13.2 | 13.1 | 14.6 | 15.4 | 14.3625
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.7 | 6.3 | 5.5 | 5.3 | 5.8 | 6.7 | 7.3 | 7.7 | 7.6 | 7.4 | 7.5 | 7.3 | 7.3 | 7.1 | 7 | 6.7 | 6.7 | 6.4 | 6.3 | 6 | 5.8 | 5.6 | 6.9 | 7.5 | 6.725
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.9 | 23.8 | 23.6 | 23.4 | 23.4 | 24.6 | 24.9 | 26.5 | 26.4 | 26.3 | 26.1 | 26.1 | 26.3 | 26.5 | 26.4 | 26.5 | 26.3 | 26.3 | 26.6 | 25.9 | 25.8 | 25.6 | 25.4 | 25.7 | 25.5125
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.3 | 29 | 28.6 | 28.1 | 28.5 | 29.8 | 30.2 | 31.4 | 31.3 | 31.2 | 30.9 | 31.1 | 31.2 | 31.5 | 31.3 | 31.4 | 31.2 | 31.2 | 31.3 | 30.7 | 30.6 | 30.3 | 30.4 | 30.8 | 30.4708
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2600.8929 | 2568.7831 | 2472.4537 | 2344.0146 | 2536.6733 | 2568.7831 | 2600.8929 | 2440.3439 | 2408.2341 | 2440.3439 | 2376.1243 | 2440.3439 | 2408.2341 | 2440.3439 | 2440.3439 | 2408.2341 | 2376.1243 | 2408.2341 | 2376.1243 | 2408.2341 | 2376.1243 | 2408.2341 | 2472.4537 | 2536.6733 | 58857.2421 | z
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1300 | 1500 | 1500 | 1500 | 1600 | 1500 | 1400 | 1600 | 1500 | 1500 | 1400 | 1600 | 1500 | 1500 | 1600 | 1400 | 1500 | 1500 | 1400 | 1600 | 1600 | 1500 | 36100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.57673 | 0.62286 | 0.52579 | 0.63993 | 0.59133 | 0.58393 | 0.61517 | 0.61467 | 0.58134 | 0.65565 | 0.63128 | 0.61467 | 0.58134 | 0.65565 | 0.61467 | 0.62286 | 0.67337 | 0.58134 | 0.63128 | 0.62286 | 0.58919 | 0.66439 | 0.64713 | 0.59133 | 0.6137
17 | Average iKW/TR |  |  | Hours 7: 0.6137 | 0.6137
18 | COP of chiller |  |  | 6.0965 | 5.6449 | 6.687 | 5.4944 | 5.946 | 6.0212 | 5.7155 | 5.7202 | 6.0481 | 5.3627 | 5.5696 | 5.7202 | 6.0481 | 5.3627 | 5.7202 | 5.6449 | 5.2215 | 6.0481 | 5.5696 | 5.6449 | 5.9675 | 5.2921 | 5.4332 | 5.946 | 5.7469
19 | EER of Chiller |  |  | 20.8073 | 19.266 | 22.8229 | 18.7523 | 20.2936 | 20.5504 | 19.5069 | 19.5229 | 20.6422 | 18.3027 | 19.0092 | 19.5229 | 20.6422 | 18.3027 | 19.5229 | 19.266 | 17.8211 | 20.6422 | 19.0092 | 19.266 | 20.367 | 18.0619 | 18.5436 | 20.2936 | 19.6141
20 | LMTD of Condenser | ºC |  | 3.7776 | 3.7119 | 3.6457 | 3.312 | 3.7954 | 3.7119 | 3.7448 | 3.4955 | 3.6124 | 3.4955 | 3.579 | 3.5284 | 3.3774 | 3.4099 | 3.4955 | 3.4955 | 3.3774 | 3.3774 | 3.4293 | 3.4625 | 3.4625 | 3.312 | 3.5284 | 3.5612 | 3.5291
21 | LMTD of Evaporator | ºC |  | 3.5178 | 3.3363 | 3.0987 | 2.9966 | 3.3103 | 3.3363 | 3.1998 | 3.0733 | 3.3578 | 3.0733 | 3.1797 | 3.0733 | 3.206 | 3.2322 | 3.0733 | 2.8816 | 2.8568 | 3.0478 | 3.0222 | 3.0478 | 3.0222 | 3.206 | 3.0987 | 3.1494 | 3.1415
Performance Sheet Chiller
Date :- 17/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.4 | 1.4 | [5 empty] | 1.8 | 1.3 | 1.5 | 1.5 | 1.4 | 1.5 | 1.3 | 1.2 | 1.7 | 1.4 | 1.4 | 1.4 | 1.5 |  |  |  |  | 1.4467
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.8 | [5 empty] | 0.9 | 0.8 | 0.8 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.8 | 0.8 | 0.7 |  |  |  |  | 0.8
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.6 | 14.3 | [5 empty] | 15.3 | 15 | 14.7 | 14.9 | 14.9 | 14.8 | 14.4 | 14.5 | 14 | 14 | 13.8 | 13.6 | 13.5 |  |  |  |  | 14.4867
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.8 | 6.7 | [5 empty] | 8.1 | 7.8 | 7.7 | 7.7 | 7.6 | 7.4 | 7.4 | 7.3 | 7 | 6.7 | 6.6 | 6.5 | 6.2 |  |  |  |  | 7.2333
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.7 | 23.7 | [5 empty] | 26.2 | 26.3 | 26.2 | 25.8 | 25.7 | 25.8 | 25.9 | 26.1 | 26.4 | 26.2 | 26.1 | 26.3 | 25.7 |  |  |  |  | 25.74
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.7 | 29.3 | [5 empty] | 31.8 | 31.7 | 31.6 | 31.4 | 31.4 | 31.6 | 31.9 | 31.8 | 31.8 | 31.7 | 31.6 | 31.8 | 31.3 |  |  |  |  | 31.36
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | [5 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  |  | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | [5 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | [5 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | [5 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | [5 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  |  | 971
14 | TR Genrated by Chiller | TR |  | 2504.5635 | 2440.3439 | [5 empty] | 2311.9048 | 2311.9048 | 2247.6852 | 2311.9048 | 2344.0146 | 2376.1243 | 2247.6852 | 2311.9048 | 2247.6852 | 2344.0146 | 2311.9048 | 2279.795 | 2344.0146 |  |  |  |  | 34935.4497
15 | Power Consumption of Chiller | KWH |  | 1400 | 1600 | 300 | 0 | 0 | 500 | 1500 | 1500 | 1400 | 1600 | 1500 | 1400 | 1500 | 1600 | 1400 | 1600 | 1500 | 1500 | 1500 | 1300 | 0 | 0 | 200 | 1500 | 26300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.55898 | 0.65565 | [5 empty] | 0.64882 | 0.60556 | 0.71184 | 0.64882 | 0.59727 | 0.63128 | 0.71184 | 0.60556 | 0.71184 | 0.63993 | 0.64882 | 0.65795 | 0.5546 |  |  |  |  | 0.63925
17 | Average iKW/TR |  |  | Hours 7: 0.63925 | 0.63925
18 | COP of chiller |  |  | 6.29 | 5.3627 | [5 empty] | 5.4191 | 5.8062 | 4.9393 | 5.4191 | 5.8868 | 5.5696 | 4.9393 | 5.8062 | 4.9393 | 5.4944 | 5.4191 | 5.3438 | 6.3397 |  |  |  |  | 5.5316
19 | EER of Chiller |  |  | 21.4679 | 18.3027 | [5 empty] | 18.4954 | 19.8165 | 16.8578 | 18.4954 | 20.0917 | 19.0092 | 16.8578 | 19.8165 | 16.8578 | 18.7523 | 18.4954 | 18.2385 | 21.6373 |  |  |  |  | 18.8795
20 | LMTD of Condenser | ºC |  | 3.6036 | 3.4795 | [5 empty] | 3.9613 | 3.2932 | 3.5385 | 3.6021 | 3.5107 | 3.6653 | 3.4772 | 3.2586 | 3.7776 | 3.4482 | 3.4482 | 3.4482 | 3.6021 |  |  |  |  | 3.541
21 | LMTD of Evaporator | ºC |  | 3.2843 | 3.2322 | [5 empty] | 3.2769 | 3.1269 | 3.0739 | 3.2769 | 3.1533 | 3.1797 | 3.0739 | 3.1269 | 3.0739 | 2.9966 | 3.1269 | 3.1004 | 2.9966 |  |  |  |  | 3.1399

## 18-03-2023
Performance Sheet Chiller
Date :- 18/03/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.7 | 1.7 | 1.7 | 1.6 | 1.4 | 1.4 | 1.6 | 1.5 | 1.6 | 1.7 | 1.7 | 1.5 | 1.6 | 1.5 | 1.4 | 1.4 | 1.4 | 1.5 | 1.3 | 1.3 | 1.3 | 1.2 | 1.3 | 1.2 | 1.4792
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.67917
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.9 | 14.8 | 14.2 | 13.6 | 13.3 | 13.4 | 13.7 | 13.8 | 14.2 | 14.5 | 14.6 | 14.6 | 14.5 | 14.5 | 14.6 | 14.6 | 14.4 | 14.1 | 13.7 | 13.5 | 13.2 | 13.1 | 12.9 | 12.8 | 14.0208
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 8.3 | 7.2 | 6.5 | 6.1 | 7.1 | 7.1 | 7.1 | 7.2 | 7.1 | 6.9 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7 | 6.8 | 6.4 | 7.1 | 6.9 | 7.1 | 7.1 | 7.1 | 7.1 | 7.0292
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.7 | 25.2 | 25.2 | 25.1 | 25.7 | 26.2 | 26.2 | 26.3 | 26.1 | 26.3 | 26.4 | 26.4 | 26.4 | 26.6 | 26.6 | 26.3 | 25.6 | 25.2 | 24.9 | 24.9 | 24.8 | 24.6 | 24.6 | 24.5 | 25.6583
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.6 | 30.2 | 30.2 | 30 | 29.6 | 30.2 | 30.4 | 30.7 | 30.7 | 31.2 | 31.3 | 31.3 | 31.3 | 31.3 | 31.4 | 31.2 | 30.6 | 30.2 | 29.2 | 29.3 | 28.7 | 28.4 | 28.4 | 28.2 | 30.1917
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2440.3439 | 2472.4537 | 2408.2341 | 1990.8069 | 2022.9167 | 2119.246 | 2119.246 | 2279.795 | 2440.3439 | 2408.2341 | 2408.2341 | 2376.1243 | 2376.1243 | 2408.2341 | 2440.3439 | 2440.3439 | 2472.4537 | 2119.246 | 2119.246 | 1958.6971 | 1926.5873 | 1862.3677 | 1830.2579 | 53880.2249
15 | Power Consumption of Chiller | KWH |  | 1400 | 1500 | 1500 | 1300 | 1300 | 1400 | 1300 | 1400 | 1600 | 1400 | 1600 | 1400 | 1400 | 1600 | 1400 | 1600 | 1500 | 1200 | 1400 | 1200 | 1200 | 1200 | 1200 | 1200 | 33200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.57369 | 0.61467 | 0.60668 | 0.53981 | 0.653 | 0.69207 | 0.61343 | 0.66061 | 0.70182 | 0.57369 | 0.66439 | 0.58134 | 0.58919 | 0.67337 | 0.58134 | 0.65565 | 0.61467 | 0.48535 | 0.66061 | 0.56624 | 0.61265 | 0.62286 | 0.64434 | 0.65565 | 0.61821
17 | Average iKW/TR |  |  | Hours 7: 0.61821 | 0.61821
18 | COP of chiller |  |  | 6.1287 | 5.7202 | 5.7954 | 6.5133 | 5.3844 | 5.0804 | 5.7317 | 5.3223 | 5.0098 | 6.1287 | 5.2921 | 6.0481 | 5.9675 | 5.2215 | 6.0481 | 5.3627 | 5.7202 | 7.2443 | 5.3223 | 6.2094 | 5.739 | 5.6449 | 5.4567 | 5.3627 | 5.7273
19 | EER of Chiller |  |  | 20.9174 | 19.5229 | 19.7798 | 22.2301 | 18.3768 | 17.3394 | 19.5624 | 18.1651 | 17.0986 | 20.9174 | 18.0619 | 20.6422 | 20.367 | 17.8211 | 20.6422 | 18.3027 | 19.5229 | 24.7248 | 18.1651 | 21.1927 | 19.5871 | 19.266 | 18.6238 | 18.3027 | 19.5472
20 | LMTD of Condenser | ºC |  | 3.6124 | 3.6457 | 3.6457 | 3.4955 | 2.9296 | 2.9631 | 3.2612 | 3.2129 | 3.396 | 3.6124 | 3.6124 | 3.3774 | 3.4955 | 3.312 | 3.2256 | 3.2578 | 3.2899 | 3.4099 | 2.9444 | 2.9768 | 2.8133 | 2.6627 | 2.7801 | 2.6299 | 3.2318
21 | LMTD of Evaporator | ºC |  | 3.0733 | 3.0733 | 3.0987 | 2.8816 | 2.5538 | 2.5795 | 2.656 | 2.815 | 2.9451 | 3.0733 | 2.8816 | 2.8816 | 2.8568 | 3.0222 | 3.0478 | 3.0733 | 3.0733 | 3.0987 | 2.9668 | 2.815 | 2.683 | 2.8037 | 2.6027 | 2.5757 | 2.8805
Performance Sheet Chiller
Date :- 18/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.3 | 1.7 | 1.6 | 1.6 | 1.3 | 1.4 | 1.5 | 1.1 | 1.6 | 2 | 2 | 1.5 | 1.5 | 1.4 | 1.6 | 1.6 | 1.6 | 1.5 | 1.3 | 1.2 | 1.2 | 1.1 | 1.2 | 1.1 | 1.4542
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.8 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.6 | 0.7 | 0.7 | 0.8 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 | 0.70833
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.7 | 14.7 | 14 | 13.6 | 13.1 | 13.3 | 13.5 | 13.8 | 14.2 | 14.3 | 14.7 | 14.5 | 14.4 | 14.6 | 14.6 | 14.5 | 14.3 | 13.9 | 13.5 | 13.4 | 13.1 | 12.8 | 12.8 | 12.5 | 13.9083
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 8.3 | 7.3 | 6.8 | 6.4 | 7 | 7 | 6.9 | 7.1 | 7.3 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.5 | 7.3 | 6.8 | 6.5 | 7 | 7.2 | 7.1 | 7 | 7.2 | 7 | 7.1542
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.4 | 25.1 | 25.2 | 24.9 | 25.3 | 25.9 | 25.9 | 26 | 25.9 | 26.1 | 26.3 | 26.3 | 26.3 | 26.2 | 26.2 | 26.1 | 25.4 | 25.1 | 24.7 | 24.8 | 24.6 | 24.4 | 24.4 | 24.2 | 25.4458
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.2 | 30.8 | 30.6 | 30.6 | 30.2 | 31 | 31.3 | 31.2 | 31.4 | 31.6 | 31.8 | 31.3 | 31.7 | 31.8 | 31.7 | 31.7 | 31.1 | 30.6 | 29.7 | 29.6 | 29.2 | 29 | 28.9 | 28.7 | 30.6958
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2376.1243 | 2376.1243 | 2311.9048 | 2311.9048 | 1958.6971 | 2022.9167 | 2119.246 | 2151.3558 | 2215.5754 | 2215.5754 | 2344.0146 | 2279.795 | 2247.6852 | 2311.9048 | 2279.795 | 2311.9048 | 2408.2341 | 2376.1243 | 2087.1362 | 1990.8069 | 1926.5873 | 1862.3677 | 1798.1481 | 1766.0384 | 52049.9669
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1400 | 1400 | 1300 | 1400 | 1400 | 1300 | 1600 | 1400 | 1600 | 1400 | 1400 | 1500 | 1500 | 1600 | 1500 | 1300 | 1300 | 1300 | 1200 | 1200 | 1200 | 1200 | 33400
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.63128 | 0.63128 | 0.60556 | 0.60556 | 0.66371 | 0.69207 | 0.66061 | 0.60427 | 0.72216 | 0.63189 | 0.68259 | 0.61409 | 0.62286 | 0.64882 | 0.65795 | 0.69207 | 0.62286 | 0.54711 | 0.62286 | 0.653 | 0.62286 | 0.64434 | 0.66735 | 0.67949 | 0.64278
17 | Average iKW/TR |  |  | Hours 7: 0.64278 | 0.64278
18 | COP of chiller |  |  | 5.5696 | 5.5696 | 5.8062 | 5.8062 | 5.2975 | 5.0804 | 5.3223 | 5.8186 | 4.8687 | 5.5643 | 5.151 | 5.7255 | 5.6449 | 5.4191 | 5.3438 | 5.0804 | 5.6449 | 6.4265 | 5.6449 | 5.3844 | 5.6449 | 5.4567 | 5.2686 | 5.1745 | 5.4881
19 | EER of Chiller |  |  | 19.0092 | 19.0092 | 19.8165 | 19.8165 | 18.0804 | 17.3394 | 18.1651 | 19.8588 | 16.617 | 18.9908 | 17.5803 | 19.5413 | 19.266 | 18.4954 | 18.2385 | 17.3394 | 19.266 | 21.9337 | 19.266 | 18.3768 | 19.266 | 18.6238 | 17.9816 | 17.6605 | 18.7308
20 | LMTD of Condenser | ºC |  | 3.4163 | 3.8753 | 3.6588 | 3.7553 | 3.1366 | 3.3218 | 3.5385 | 2.9795 | 3.691 | 4.1611 | 4.1611 | 3.4099 | 3.5385 | 3.4795 | 3.691 | 3.7232 | 3.7553 | 3.5704 | 3.1682 | 2.9824 | 2.9196 | 2.7961 | 2.8881 | 2.7651 | 3.4326
21 | LMTD of Evaporator | ºC |  | 3.0222 | 3.1797 | 3.2769 | 2.9709 | 2.683 | 2.7361 | 2.815 | 2.8412 | 2.7319 | 2.8933 | 2.832 | 2.9451 | 2.9192 | 3.1269 | 2.9451 | 3.1269 | 3.206 | 3.1797 | 2.7888 | 2.5538 | 2.5022 | 2.6027 | 2.5487 | 2.3716 | 2.8666

## 19-03-2023
Performance Sheet Chiller
Date :- 19/03/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.4 | 1.3 | 1.4 | 1.3 | 1.4 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 1.4 | 1.3 | 1.4 | 1.1 | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.3 | 1.2458
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.9 | 1 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.8 | 0.7 | 0.8 | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.7 | 0.9 | 0.75833
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 12.8 | 12.9 | 12.6 | 13.3 | 13.3 | 13.3 | 15.5 | 14.6 | 14.1 | 14 | 14 | 13.9 | 13.8 | 13.7 | 13.4 | 13.3 | 13.2 | 13.1 | 12.9 | 12.6 | 13.2 | 14.2 | 15 | 15.3 | 11.8889
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.9 | 5.7 | 5.6 | 5.8 | 6.8 | 7.9 | 7.7 | 7 | 6.4 | 6.4 | 6.2 | 6.2 | 6.2 | 6 | 5.8 | 6.6 | 6.6 | 5.9 | 5.5 | 5.5 | 5.7 | 6.2 | 6.9 | 7.3 | 5.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.5 | 25.1 | 25.2 | 24.8 | 25.2 | 25.3 | 25.8 | 25.4 | 25.4 | 25.4 | 25.2 | 25.6 | 25.4 | 25.2 | 25.1 | 24.8 | 24.8 | 24.7 | 24.8 | 24.7 | 24.1 | 24.2 | 24.2 | 24.1 | 24.9444
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.3 | 29.8 | 29.8 | 29.7 | 30.3 | 31.3 | 30.9 | 30.4 | 30.4 | 30.4 | 30.2 | 30.5 | 30.4 | 30.2 | 30 | 29.2 | 29 | 29.3 | 29.6 | 29.2 | 29 | 29.5 | 29.6 | 29.3 | 29.6111
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 1894.4775 | 2311.9048 | 2247.6852 | 2408.2341 | 2087.1362 | 1733.9286 | 2504.5635 | 2440.3439 | 2472.4537 | 2440.3439 | 2504.5635 | 2472.4537 | 2440.3439 | 2472.4537 | 2440.3439 | 2151.3558 | 2119.246 | 2311.9048 | 2376.1243 | 2279.795 | 2408.2341 | 2568.7831 | 2600.8929 | 2568.7831 | 56256.3492
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1400 | 1500 | 1500 | 1600 | 1500 | 1500 | 1500 | 1400 | 1500 | 1600 | 1500 | 1400 | 1400 | 1200 | 1400 | 1500 | 1400 | 1400 | 1500 | 1500 | 1500 | 1600 | 35100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.73899 | 0.60556 | 0.62286 | 0.62286 | 0.71869 | 0.92276 | 0.59891 | 0.61467 | 0.60668 | 0.57369 | 0.59891 | 0.64713 | 0.61467 | 0.56624 | 0.57369 | 0.55779 | 0.66061 | 0.64882 | 0.58919 | 0.61409 | 0.62286 | 0.58393 | 0.57673 | 0.62286 | 0.6293
17 | Average iKW/TR |  |  | Hours 7: 0.6293 | 0.6293
18 | COP of chiller |  |  | 4.7578 | 5.8062 | 5.6449 | 5.6449 | 4.8922 | 3.8103 | 5.8707 | 5.7202 | 5.7954 | 6.1287 | 5.8707 | 5.4332 | 5.7202 | 6.2094 | 6.1287 | 6.3035 | 5.3223 | 5.4191 | 5.9675 | 5.7255 | 5.6449 | 6.0212 | 6.0965 | 5.6449 | 5.6491
19 | EER of Chiller |  |  | 16.2385 | 19.8165 | 19.266 | 19.266 | 16.6972 | 13.0046 | 20.0367 | 19.5229 | 19.7798 | 20.9174 | 20.0367 | 18.5436 | 19.5229 | 21.1927 | 20.9174 | 21.5138 | 18.1651 | 18.4954 | 20.367 | 19.5413 | 19.266 | 20.5504 | 20.8073 | 19.266 | 19.2805
20 | LMTD of Condenser | ºC |  | 2.6627 | 3.1933 | 3.0411 | 3.2578 | 3.1996 | 3.6036 | 3.1996 | 3.0446 | 3.0446 | 3.0446 | 3.0446 | 3.1366 | 3.2899 | 3.1682 | 3.2578 | 2.7339 | 2.7924 | 2.9196 | 2.8578 | 2.7651 | 2.8884 | 3.0097 | 3.1676 | 3.2309 | 3.0648
21 | LMTD of Evaporator | ºC |  | 2.6295 | 2.9709 | 2.9192 | 3.0478 | 2.7888 | 2.7751 | 3.5866 | 3.3847 | 3.0987 | 3.0733 | 3.1241 | 3.0987 | 3.2322 | 3.0987 | 3.2322 | 2.8412 | 2.9668 | 2.9709 | 3.0222 | 2.9451 | 3.206 | 3.3363 | 3.1998 | 3.4913 | 3.085
Performance Sheet Chiller
Date :- 19/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.2; Hours 13: 1.2; Hours 14: 1.7; Hours 15: 1.2; Hours 16: 1.1; Hours 17: 1.4; Hours 18: 1.6; Hours 19: 1.5; Hours 20: 1.4; Hours 21: 1.4; Hours 22: 1.2; Hours 23: 1.2; Hours 0: 1.2; Hours 1: 1.2 | 1.3214
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.6; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.7; Hours 16: 0.8; Hours 17: 0.7; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.7; Hours 23: 0.8; Hours 0: 0.7; Hours 1: 0.8 | 0.75714
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 12.7; Hours 13: 15.5; Hours 14: 14.6; Hours 15: 14.2; Hours 16: 13.9; Hours 17: 13.9; Hours 18: 13.8; Hours 19: 13.7; Hours 20: 13.5; Hours 21: 13.3; Hours 22: 13.2; Hours 23: 13.2; Hours 0: 13; Hours 1: 12.7 | 11.8889
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 7.1; Hours 13: 7.8; Hours 14: 6.9; Hours 15: 6.5; Hours 16: 6.6; Hours 17: 6.3; Hours 18: 6.4; Hours 19: 6.3; Hours 20: 6.2; Hours 21: 5.9; Hours 22: 6.4; Hours 23: 6.7; Hours 0: 6.1; Hours 1: 5.7 | 5.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 24.3; Hours 13: 25.4; Hours 14: 25.3; Hours 15: 25.3; Hours 16: 25.3; Hours 17: 25; Hours 18: 25.2; Hours 19: 25.4; Hours 20: 24.9; Hours 21: 24.8; Hours 22: 24.8; Hours 23: 24.6; Hours 0: 24.6; Hours 1: 24.7 | 24.9444
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 28.3; Hours 13: 31.5; Hours 14: 31.1; Hours 15: 31.1; Hours 16: 31; Hours 17: 30.8; Hours 18: 31.1; Hours 19: 30.9; Hours 20: 30.7; Hours 21: 30.6; Hours 22: 29.9; Hours 23: 29.4; Hours 0: 29.8; Hours 1: 30.1 | 29.6111
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3; Hours 0: 4.3; Hours 1: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 1798.1481; Hours 13: 2472.4537; Hours 14: 2472.4537; Hours 15: 2472.4537; Hours 16: 2344.0146; Hours 17: 2440.3439; Hours 18: 2376.1243; Hours 19: 2376.1243; Hours 20: 2344.0146; Hours 21: 2376.1243; Hours 22: 2183.4656; Hours 23: 2087.1362; Hours 0: 2215.5754; Hours 1: 2247.6852 | 32206.1177
15 | Power Consumption of Chiller | KWH |  | 1500 | 800 | 0 | 0 | 600 | 1600 | 1600 | 1600 | 1500 | 1500 | 1500 | 1600 | 1600 | 1400 | 1400 | 1300 | 1400 | 1400 | 900 | 0 | 0 | 0 | 0 | 1400 | 24600
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.83419; Hours 13: 0.64713; Hours 14: 0.64713; Hours 15: 0.60668; Hours 16: 0.63993; Hours 17: 0.61467; Hours 18: 0.67337; Hours 19: 0.67337; Hours 20: 0.59727; Hours 21: 0.58919; Hours 22: 0.59538; Hours 23: 0.67078; Hours 0: 0.63189; Hours 1: 0.40041 | 0.6301
17 | Average iKW/TR |  |  | Hours 7: 0.6301 | 0.6301
18 | COP of chiller |  |  | Hours 7: 4.2149; Hours 13: 5.4332; Hours 14: 5.4332; Hours 15: 5.7954; Hours 16: 5.4944; Hours 17: 5.7202; Hours 18: 5.2215; Hours 19: 5.2215; Hours 20: 5.8868; Hours 21: 5.9675; Hours 22: 5.9054; Hours 23: 5.2417; Hours 0: 5.5643; Hours 1: 8.781 | 5.7058
19 | EER of Chiller |  |  | Hours 7: 14.3853; Hours 13: 18.5436; Hours 14: 18.5436; Hours 15: 19.7798; Hours 16: 18.7523; Hours 17: 19.5229; Hours 18: 17.8211; Hours 19: 17.8211; Hours 20: 20.0917; Hours 21: 20.367; Hours 22: 20.1552; Hours 23: 17.8899; Hours 0: 18.9908; Hours 1: 29.9694 | 19.4738
20 | LMTD of Condenser | ºC |  | Hours 7: 2.7279; Hours 13: 3.3785; Hours 14: 3.9076; Hours 15: 3.2887; Hours 16: 3.1291; Hours 17: 3.5417; Hours 18: 3.819; Hours 19: 3.5704; Hours 20: 3.5417; Hours 21: 3.5417; Hours 22: 3.0756; Hours 23: 2.9824; Hours 0: 3.1064; Hours 1: 3.1676 | 3.3413
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.3979; Hours 13: 3.2583; Hours 14: 3.2583; Hours 15: 3.0987; Hours 16: 3.1533; Hours 17: 3.0733; Hours 18: 3.1797; Hours 19: 3.1797; Hours 20: 3.1533; Hours 21: 3.1797; Hours 22: 2.8673; Hours 23: 2.9398; Hours 0: 2.8933; Hours 1: 3.0739 | 3.0505

## 20-03-2023
Performance Sheet Chiller
Date :- 20/03/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.3 | 1.2 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.4 | 1.3 | 1.2 | 1.2 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2167
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.8 | 0.8 | 0.7 | 0.8 | 0.7 | 0.8 | 0.9 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.9 | 1.1 | 1.2 | 1.2 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.9 | 0.825
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.7 | 14.5 | 13.6 | 13.1 | 13.5 | 14.4 | 15.2 | 15.1 | 14.3 | 13.7 | 13.2 | 13 | 12.7 | 14 | 15 | 15.8 | 16.2 | 14.5 | 13.2 | 12.2 | 12.6 | 13.7 | 14.4 | 14.7 | 14.0958
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.7 | 6.5 | 5.8 | 5.5 | 5.7 | 6.4 | 7.5 | 7.3 | 6.4 | 5.9 | 5.7 | 5.6 | 5.4 | 6 | 7 | 7.7 | 7.9 | 6.4 | 5.5 | 5.5 | 5.7 | 5.8 | 6.3 | 6.7 | 6.3292
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.4 | 24 | 24.1 | 24.1 | 24.4 | 24.7 | 25 | 25.1 | 24.9 | 24.5 | 24.4 | 24.1 | 24.2 | 23.7 | 23.9 | 23.9 | 24.2 | 24.1 | 23.5 | 23.5 | 23.6 | 23.8 | 24.1 | 24.1 | 24.9444
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.7 | 29.3 | 29.2 | 29.1 | 29.5 | 29.8 | 32.4 | 30.2 | 30 | 29.6 | 29.3 | 29.1 | 28.8 | 28.9 | 29.2 | 29.3 | 29.7 | 29.4 | 28.5 | 27.9 | 28.1 | 29.1 | 29.3 | 29.4 | 29.6111
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2568.7831 | 2504.5635 | 2440.3439 | 2504.5635 | 2568.7831 | 2472.4537 | 2504.5635 | 2536.6733 | 2504.5635 | 2408.2341 | 2376.1243 | 2344.0146 | 2568.7831 | 2568.7831 | 2600.8929 | 2665.1124 | 2600.8929 | 2472.4537 | 2151.3558 | 2215.5754 | 2536.6733 | 2600.8929 | 2568.7831 | 59852.6455
15 | Power Consumption of Chiller | KWH |  | 1500 | 1400 | 1500 | 1500 | 1500 | 1600 | 1500 | 1500 | 1500 | 1400 | 1500 | 1400 | 1400 | 1600 | 1400 | 1700 | 1400 | 1600 | 1300 | 1200 | 1600 | 1500 | 1500 | 1600 | 35600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58393 | 0.54501 | 0.59891 | 0.61467 | 0.59891 | 0.62286 | 0.60668 | 0.59891 | 0.59133 | 0.55898 | 0.62286 | 0.58919 | 0.59727 | 0.62286 | 0.54501 | 0.65362 | 0.52531 | 0.61517 | 0.52579 | 0.55779 | 0.72216 | 0.59133 | 0.57673 | 0.62286 | 0.59534
17 | Average iKW/TR |  |  | Hours 7: 0.59534 | 0.59534
18 | COP of chiller |  |  | 6.0212 | 6.4513 | 5.8707 | 5.7202 | 5.8707 | 5.6449 | 5.7954 | 5.8707 | 5.946 | 6.29 | 5.6449 | 5.9675 | 5.8868 | 5.6449 | 6.4513 | 5.3793 | 6.6932 | 5.7155 | 6.687 | 6.3035 | 4.8687 | 5.946 | 6.0965 | 5.6449 | 5.9338
19 | EER of Chiller |  |  | 20.5504 | 22.0183 | 20.0367 | 19.5229 | 20.0367 | 19.266 | 19.7798 | 20.0367 | 20.2936 | 21.4679 | 19.266 | 20.367 | 20.0917 | 19.266 | 22.0183 | 18.3594 | 22.844 | 19.5069 | 22.8229 | 21.5138 | 16.617 | 20.2936 | 20.8073 | 19.266 | 20.252
20 | LMTD of Condenser | ºC |  | 3.1371 | 3.1371 | 3.1996 | 3.1682 | 3.1996 | 3.0756 | 3.7574 | 3.1996 | 3.0756 | 2.9493 | 3.0136 | 3.0446 | 2.9196 | 3.1064 | 3.1371 | 3.4167 | 3.3241 | 3.1371 | 3.0446 | 2.7339 | 2.7651 | 3.1371 | 3.1064 | 3.1371 | 3.1218
21 | LMTD of Evaporator | ºC |  | 3.3363 | 3.3363 | 3.2843 | 3.0733 | 3.2843 | 3.1746 | 3.2583 | 3.4381 | 3.1494 | 3.1241 | 3.0478 | 3.1797 | 2.9966 | 3.4913 | 3.7862 | 3.9557 | 4.0117 | 3.3621 | 3.2583 | 2.8412 | 2.8933 | 3.3103 | 3.3621 | 3.4913 | 3.3103
Performance Sheet Chiller
Date :- 20/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.4; Hours 8: 1.4; Hours 14: 1.3; Hours 15: 1.6; Hours 16: 1.3; Hours 17: 1.2; Hours 23: 1.3; Hours 0: 1.4 | 1.3625
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.7; Hours 8: 0.7; Hours 14: 0.9; Hours 15: 0.7; Hours 16: 0.6; Hours 17: 0.8; Hours 23: 0.9; Hours 0: 0.9 | 0.775
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 15.6; Hours 8: 14.4; Hours 14: 15.2; Hours 15: 14.2; Hours 16: 13.6; Hours 17: 12.9; Hours 23: 15.9; Hours 0: 14.4 | 14.525
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 7.8; Hours 8: 6.6; Hours 14: 7.4; Hours 15: 6.7; Hours 16: 6.1; Hours 17: 5.9; Hours 23: 7.9; Hours 0: 6.6 | 6.875
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 24.3; Hours 8: 23.8; Hours 14: 24.9; Hours 15: 24.7; Hours 16: 24.4; Hours 17: 24.3; Hours 23: 24; Hours 0: 23.9 | 24.9444
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 30.3; Hours 8: 29.8; Hours 14: 30.7; Hours 15: 30.4; Hours 16: 29.9; Hours 17: 29.7; Hours 23: 29.9; Hours 0: 29.8 | 29.6111
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 8: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 23: 4.3; Hours 0: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 23: 3.8; Hours 0: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 23: 3.8; Hours 0: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 23: 3; Hours 0: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 23: 0.5; Hours 0: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 23: 0.8; Hours 0: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 23: 971; Hours 0: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2504.5635; Hours 8: 2504.5635; Hours 14: 2504.5635; Hours 15: 2408.2341; Hours 16: 2408.2341; Hours 17: 2247.6852; Hours 23: 2568.7831; Hours 0: 2504.5635 | 19651.1905
15 | Power Consumption of Chiller | KWH |  | 1600 | 1500 | 900 | 0 | 0 | 700 | 1500 | 1500 | 1500 | 1400 | 1500 | 200 | 0 | 0 | 0 | 1500 | 1400 | 1700 | 800 | 0 | 0 | 0 | 0 | 1400 | 19100
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.63883; Hours 8: 0.59891; Hours 14: 0.59891; Hours 15: 0.62286; Hours 16: 0.58134; Hours 17: 0.66735; Hours 23: 0.54501; Hours 0: 0.67876 | 0.6165
17 | Average iKW/TR |  |  | Hours 7: 0.6165 | 0.6165
18 | COP of chiller |  |  | Hours 7: 5.5038; Hours 8: 5.8707; Hours 14: 5.8707; Hours 15: 5.6449; Hours 16: 6.0481; Hours 17: 5.2686; Hours 23: 6.4513; Hours 0: 5.18 | 5.7298
19 | EER of Chiller |  |  | Hours 7: 18.7844; Hours 8: 20.0367; Hours 14: 20.0367; Hours 15: 19.266; Hours 16: 20.6422; Hours 17: 17.9816; Hours 23: 22.0183; Hours 0: 17.6794 | 19.5557
20 | LMTD of Condenser | ºC |  | Hours 7: 3.6036; Hours 8: 3.6036; Hours 14: 3.4163; Hours 15: 3.7553; Hours 16: 3.3241; Hours 17: 3.1676; Hours 23: 3.4468; Hours 0: 3.5727 | 3.4863
21 | LMTD of Evaporator | ºC |  | Hours 7: 3.1241; Hours 8: 3.1241; Hours 14: 3.4381; Hours 15: 3.0478; Hours 16: 2.8816; Hours 17: 3.0739; Hours 23: 3.4913; Hours 0: 3.4381 | 3.2024

## 21-03-2023
Performance Sheet Chiller
Date :- 21/03/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.1 | 1.2 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1.1 | 1.1 | 1 | 1.1 | 1.1 | 1.1 | 1 | 1 | 1.1 | 1.0917
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.8 | 0.7 | 0.9 | 0.8 | 0.8 | 0.7 | 0.8 | 0.9 | 0.9 | 1.1 | 1 | 0.8 | 0.8 | 0.9 | 0.9 | 0.8 | 1 | 1.1 | 1
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.2 | 13.7 | 12.7 | 13.1 | 14.2 | 14.8 | 15.4 | 15.4 | 14.2 | 13.5 | 13.9 | 13.8 | 13.5 | 13.1 | 14.7 | 15.2 | 15.8 | 15.4 | 14.2 | 13.1 | 12.2 | 13.3 | 13.9 | 14.3 | 14.1083
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7 | 5.9 | 5.4 | 5.8 | 6.3 | 6.7 | 7.4 | 7.4 | 6.7 | 7.1 | 6.9 | 6 | 5.7 | 5.6 | 6.7 | 7.3 | 7.9 | 7.3 | 6.2 | 5.4 | 5.3 | 5.7 | 6.1 | 6.4 | 6.425
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.7 | 23.6 | 23.6 | 23.7 | 23.9 | 24.4 | 24.7 | 24.8 | 24.6 | 24.6 | 24.6 | 24.6 | 24.7 | 24.9 | 24.8 | 24.7 | 24.8 | 25 | 24.9 | 24.8 | 24.9 | 24.8 | 24.9 | 24.9 | 24.5375
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.1 | 28.8 | 28.3 | 28.6 | 29.1 | 29.7 | 29.8 | 30.1 | 29.4 | 28.8 | 29.1 | 29.7 | 29.8 | 29.8 | 30.1 | 29.9 | 31.9 | 30.4 | 30.1 | 29.9 | 29.6 | 29.8 | 30.2 | 30.2 | 29.675
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2633.0026 | 2504.5635 | 2344.0146 | 2344.0146 | 2536.6733 | 2600.8929 | 2568.7831 | 2568.7831 | 2408.2341 | 2055.0265 | 2247.6852 | 2504.5635 | 2504.5635 | 2408.2341 | 2568.7831 | 2536.6733 | 2536.6733 | 2600.8929 | 2568.7831 | 2472.4537 | 2215.5754 | 2440.3439 | 2504.5635 | 2536.6733 | 59210.4497
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1500 | 1400 | 1500 | 1500 | 1500 | 1500 | 1200 | 1400 | 1500 | 1600 | 1400 | 1600 | 1500 | 1500 | 1600 | 1600 | 1500 | 1400 | 1500 | 1500 | 1600 | 1600 | 35700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53171 | 0.55898 | 0.63993 | 0.59727 | 0.59133 | 0.57673 | 0.58393 | 0.58393 | 0.49829 | 0.68126 | 0.66735 | 0.63883 | 0.55898 | 0.66439 | 0.58393 | 0.59133 | 0.63075 | 0.61517 | 0.58393 | 0.56624 | 0.67703 | 0.61467 | 0.63883 | 0.63075 | 0.6044
17 | Average iKW/TR |  |  | Hours 7: 0.6044 | 0.6044
18 | COP of chiller |  |  | 6.6126 | 6.29 | 5.4944 | 5.8868 | 5.946 | 6.0965 | 6.0212 | 6.0212 | 7.0561 | 5.1611 | 5.2686 | 5.5038 | 6.29 | 5.2921 | 6.0212 | 5.946 | 5.5743 | 5.7155 | 6.0212 | 6.2094 | 5.1933 | 5.7202 | 5.5038 | 5.5743 | 5.8508
19 | EER of Chiller |  |  | 22.5688 | 21.4679 | 18.7523 | 20.0917 | 20.2936 | 20.8073 | 20.5504 | 20.5504 | 24.0826 | 17.6147 | 17.9816 | 18.7844 | 21.4679 | 18.0619 | 20.5504 | 20.2936 | 19.0252 | 19.5069 | 20.5504 | 21.1927 | 17.7248 | 19.5229 | 18.7844 | 19.0252 | 19.9688
20 | LMTD of Condenser | ºC |  | 3.1676 | 2.9795 | 2.827 | 2.8884 | 2.9795 | 3.1371 | 2.9493 | 3.1371 | 2.7306 | 2.6711 | 2.7651 | 2.9493 | 2.9493 | 2.8884 | 2.8796 | 2.9795 | 3.5344 | 2.909 | 2.9795 | 2.9493 | 2.827 | 2.7906 | 2.8796 | 3.0097 | 2.9482
21 | LMTD of Evaporator | ºC |  | 3.2249 | 3.1241 | 2.9966 | 3.1533 | 3.3103 | 3.3621 | 3.4913 | 3.4913 | 3.206 | 2.7625 | 3.2225 | 3.2843 | 3.2843 | 3.0478 | 3.3363 | 3.4647 | 3.4647 | 3.8138 | 3.641 | 3.2583 | 3.0472 | 3.3847 | 3.4381 | 3.3103 | 3.2967
Performance Sheet Chiller
Date :- 21/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.6; Hours 14: 1.2; Hours 15: 1.4; Hours 16: 1.2; Hours 17: 1.3; Hours 18: 1.4; Hours 0: 1.4; Hours 1: 1.4 | 1.3625
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.9; Hours 14: 0.7; Hours 15: 0.8; Hours 16: 0.7; Hours 17: 0.8; Hours 18: 0.9; Hours 0: 0.9; Hours 1: 0.9 | 0.825
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 15.1; Hours 14: 15.3; Hours 15: 14.1; Hours 16: 13.4; Hours 17: 13.7; Hours 18: 13.9; Hours 0: 15.3; Hours 1: 14.2 | 14.375
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 6.8; Hours 14: 7.6; Hours 15: 6.9; Hours 16: 7.1; Hours 17: 7.1; Hours 18: 6.3; Hours 0: 7.6; Hours 1: 6.4 | 6.975
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 23.7; Hours 14: 24.6; Hours 15: 24.3; Hours 16: 24.4; Hours 17: 24.4; Hours 18: 24.4; Hours 0: 24.8; Hours 1: 24.4 | 24.375
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 29.9; Hours 14: 30.6; Hours 15: 29.9; Hours 16: 29.3; Hours 17: 29.6; Hours 18: 30.1; Hours 0: 30.9; Hours 1: 30.6 | 30.1125
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 0: 4.3; Hours 1: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 0: 3.8; Hours 1: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 0: 3.8; Hours 1: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 0: 3; Hours 1: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 0: 0.5; Hours 1: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 0: 0.8; Hours 1: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 0: 971; Hours 1: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2665.1124; Hours 14: 2472.4537; Hours 15: 2311.9048; Hours 16: 2022.9167; Hours 17: 2119.246; Hours 18: 2440.3439; Hours 0: 2472.4537; Hours 1: 2504.5635 | 19008.9947
15 | Power Consumption of Chiller | KWH |  | 1500 | 900 | 0 | 0 | 0 | 400 | 1500 | 1500 | 1300 | 1400 | 1500 | 1700 | 100 | 0 | 0 | 400 | 1600 | 1600 | 1500 | 200 | 0 | 0 | 0 | 1100 | 18200
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.56283; Hours 14: 0.60668; Hours 15: 0.56231; Hours 16: 0.69207; Hours 17: 0.7078; Hours 18: 0.69662; Hours 0: 0.64713; Hours 1: 0.59891 | 0.63429
17 | Average iKW/TR |  |  | Hours 7: 0.63429 | 0.63429
18 | COP of chiller |  |  | Hours 7: 6.247; Hours 14: 5.7954; Hours 15: 6.2528; Hours 16: 5.0804; Hours 17: 4.9675; Hours 18: 5.0472; Hours 0: 5.4332; Hours 1: 5.8707 | 5.5868
19 | EER of Chiller |  |  | Hours 7: 21.3211; Hours 14: 19.7798; Hours 15: 21.3409; Hours 16: 17.3394; Hours 17: 16.9541; Hours 18: 17.2261; Hours 0: 18.5436; Hours 1: 20.0367 | 19.0677
20 | LMTD of Condenser | ºC |  | Hours 7: 3.9138; Hours 14: 3.3487; Hours 15: 3.4795; Hours 16: 3.0136; Hours 17: 3.2309; Hours 18: 3.5107; Hours 0: 3.6343; Hours 1: 3.665 | 3.4746
21 | LMTD of Evaporator | ºC |  | Hours 7: 3.5706; Hours 14: 3.0987; Hours 15: 3.1269; Hours 16: 2.7361; Hours 17: 2.9668; Hours 18: 3.3847; Hours 0: 3.4114; Hours 1: 3.4381 | 3.2167

## 22-03-2023
Performance Sheet Chiller
Date :- 22/03/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.1 | 1.1 | 1.1 | 1 | 1 | 1.1 | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 0.9 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.1 | 1.1 | 1 | 1 | 1 | 1.0708
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 1.2 | 1.1 | 0.9 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.9 | 1 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.9 | 0.825
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.8 | 14.1 | 13.4 | 12.8 | 13.3 | 14.4 | 15.3 | 15.9 | 15.7 | 14.4 | 13.7 | 13.5 | 13.4 | 13.8 | 15.3 | 16 | 16.3 | 14.7 | 13.8 | 13.1 | 12.6 | 13.8 | 14.4 | 14.9 | 11.8333
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.8 | 6.2 | 5.6 | 5.5 | 5.7 | 6.4 | 7.4 | 7.9 | 7.4 | 6.2 | 6.1 | 5.8 | 5.8 | 6.1 | 7.2 | 8.1 | 8.3 | 6.6 | 5.9 | 5.6 | 5.4 | 6 | 6.5 | 7 | 5.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.6 | 25.1 | 25.2 | 25.2 | 24.7 | 24.6 | 24.8 | 24.7 | 24.1 | 24.1 | 24.9 | 25.2 | 25.3 | 25.2 | 25.2 | 25.1 | 25 | 24.8 | 24.7 | 24.8 | 24.6 | 24.7 | 24.7 | 24.8 | 25.1111
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.9 | 30.2 | 30.2 | 30.1 | 29.7 | 29.9 | 30.2 | 32.4 | 29.6 | 29.5 | 30.1 | 30.3 | 30.3 | 30.3 | 30.6 | 30.5 | 30.6 | 30.2 | 29.9 | 29.7 | 29.3 | 29.8 | 30 | 30.1 | 29.1111
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2536.6733 | 2504.5635 | 2344.0146 | 2440.3439 | 2568.7831 | 2536.6733 | 2568.7831 | 2665.1124 | 2633.0026 | 2440.3439 | 2472.4537 | 2440.3439 | 2472.4537 | 2600.8929 | 2536.6733 | 2568.7831 | 2600.8929 | 2536.6733 | 2408.2341 | 2311.9048 | 2504.5635 | 2536.6733 | 2536.6733 | 60334.2923
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1400 | 1600 | 1500 | 1600 | 1600 | 1500 | 1600 | 1500 | 1600 | 1400 | 1500 | 1500 | 1700 | 1500 | 1500 | 1600 | 1500 | 1400 | 1400 | 1700 | 1500 | 1500 | 36600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58393 | 0.59133 | 0.55898 | 0.68259 | 0.61467 | 0.62286 | 0.63075 | 0.58393 | 0.60035 | 0.56969 | 0.65565 | 0.56624 | 0.61467 | 0.60668 | 0.65362 | 0.59133 | 0.58393 | 0.61517 | 0.59133 | 0.58134 | 0.60556 | 0.67876 | 0.59133 | 0.59133 | 0.60692
17 | Average iKW/TR |  |  | Hours 7: 0.60692 | 0.60692
18 | COP of chiller |  |  | 6.0212 | 5.946 | 6.29 | 5.151 | 5.7202 | 5.6449 | 5.5743 | 6.0212 | 5.8566 | 6.1718 | 5.3627 | 6.2094 | 5.7202 | 5.7954 | 5.3793 | 5.946 | 6.0212 | 5.7155 | 5.946 | 6.0481 | 5.8062 | 5.18 | 5.946 | 5.946 | 5.8091
19 | EER of Chiller |  |  | 20.5504 | 20.2936 | 21.4679 | 17.5803 | 19.5229 | 19.266 | 19.0252 | 20.5504 | 19.9885 | 21.0642 | 18.3027 | 21.1927 | 19.5229 | 19.7798 | 18.3594 | 20.2936 | 20.5504 | 19.5069 | 20.2936 | 20.6422 | 19.8165 | 17.6794 | 20.2936 | 20.2936 | 19.8265
20 | LMTD of Condenser | ºC |  | 3.0097 | 2.9493 | 2.9189 | 2.7606 | 2.7906 | 3.0097 | 3.1676 | 3.7029 | 3.0696 | 3.0397 | 2.9795 | 2.8203 | 2.6591 | 2.8203 | 3.0397 | 3.0397 | 3.0994 | 3.0397 | 3.1064 | 2.8884 | 2.827 | 2.8203 | 2.8796 | 2.8796 | 2.9716
21 | LMTD of Evaporator | ºC |  | 3.3363 | 3.3103 | 3.1241 | 2.9966 | 3.2322 | 3.3363 | 3.8994 | 3.7862 | 3.5706 | 3.3879 | 3.2322 | 3.0987 | 3.0733 | 3.2583 | 3.3621 | 3.4647 | 3.641 | 3.3621 | 3.3103 | 3.0478 | 2.9709 | 3.2843 | 3.3103 | 3.4647 | 3.3275
Performance Sheet Chiller
Date :- 22/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.4; Hours 8: 1.4; Hours 9: 1.3; Hours 14: 1.4; Hours 15: 1.4; Hours 16: 1.1; Hours 17: 1; Hours 18: 1.2; Hours 22: 1.4; Hours 23: 1.4; Hours 0: 1.4; Hours 1: 1.1; Hours 6: 1.1 | 1.2769
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.9; Hours 8: 0.8; Hours 9: 0.8; Hours 14: 0.9; Hours 15: 0.8; Hours 16: 0.7; Hours 17: 0.8; Hours 18: 0.7; Hours 22: 0.7; Hours 23: 0.8; Hours 0: 0.9; Hours 1: 0.9; Hours 6: 0.9 | 0.81538
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 13.3; Hours 8: 13.3; Hours 9: 13.3; Hours 14: 13.4; Hours 15: 13.4; Hours 16: 13.4; Hours 17: 13.4; Hours 18: 13.4; Hours 22: 13.7; Hours 23: 13.7; Hours 0: 13.7; Hours 1: 13.7; Hours 6: 13.7 | 11.8333
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 5.8; Hours 8: 5.8; Hours 9: 5.8; Hours 14: 6.2; Hours 15: 6.2; Hours 16: 6.2; Hours 17: 6.2; Hours 18: 6.2; Hours 22: 6.6; Hours 23: 6.6; Hours 0: 6.6; Hours 1: 6.6; Hours 6: 6.6 | 5.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 24.7; Hours 8: 24.7; Hours 9: 24.7; Hours 14: 25.1; Hours 15: 25.1; Hours 16: 25.1; Hours 17: 25.1; Hours 18: 25.1; Hours 22: 24.3; Hours 23: 24.3; Hours 0: 24.3; Hours 1: 24.3; Hours 6: 24.3 | 25.1111
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 30.6; Hours 8: 30.6; Hours 9: 30.6; Hours 14: 30.6; Hours 15: 30.6; Hours 16: 30.6; Hours 17: 30.6; Hours 18: 30.6; Hours 22: 30; Hours 23: 30; Hours 0: 30; Hours 1: 30; Hours 6: 30 | 29.1111
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 8: 4.3; Hours 9: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 22: 4.3; Hours 23: 4.3; Hours 0: 4.3; Hours 1: 4.3; Hours 6: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 6: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2408.2341; Hours 8: 2408.2341; Hours 9: 2408.2341; Hours 14: 2311.9048; Hours 15: 2311.9048; Hours 16: 2311.9048; Hours 17: 2311.9048; Hours 18: 2311.9048; Hours 22: 2279.795; Hours 23: 2279.795; Hours 0: 2279.795; Hours 1: 2279.795; Hours 6: 2279.795 | 30183.2011
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1000 | 0 | 0 | 0 | 500 | 1500 | 1700 | 1500 | 1500 | 1000 | 0 | 0 | 100 | 1500 | 1500 | 1600 | 1400 | 300 | 0 | 0 | 0 | 1300 | 19500
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.62286; Hours 8: 0.66439; Hours 9: 0.41524; Hours 14: 0.64882; Hours 15: 0.73532; Hours 16: 0.64882; Hours 17: 0.64882; Hours 18: 0.43254; Hours 22: 0.65795; Hours 23: 0.65795; Hours 0: 0.70182; Hours 1: 0.61409; Hours 6: 0.57023 | 0.61683
17 | Average iKW/TR |  |  | Hours 7: 0.61683 | 0.61683
18 | COP of chiller |  |  | Hours 7: 5.6449; Hours 8: 5.2921; Hours 9: 8.4674; Hours 14: 5.4191; Hours 15: 4.7816; Hours 16: 5.4191; Hours 17: 5.4191; Hours 18: 8.1287; Hours 22: 5.3438; Hours 23: 5.3438; Hours 0: 5.0098; Hours 1: 5.7255; Hours 6: 6.166 | 5.8585
19 | EER of Chiller |  |  | Hours 7: 19.266; Hours 8: 18.0619; Hours 9: 28.8991; Hours 14: 18.4954; Hours 15: 16.3195; Hours 16: 18.4954; Hours 17: 18.4954; Hours 18: 27.7431; Hours 22: 18.2385; Hours 23: 18.2385; Hours 0: 17.0986; Hours 1: 19.5413; Hours 6: 21.0445 | 19.9952
20 | LMTD of Condenser | ºC |  | Hours 7: 3.5727; Hours 8: 3.5727; Hours 9: 3.4468; Hours 14: 3.4482; Hours 15: 3.4482; Hours 16: 3.0696; Hours 17: 2.9383; Hours 18: 3.1981; Hours 22: 3.5107; Hours 23: 3.5107; Hours 0: 3.5107; Hours 1: 3.1291; Hours 6: 3.1291 | 3.345
21 | LMTD of Evaporator | ºC |  | Hours 7: 3.3578; Hours 8: 3.206; Hours 9: 3.206; Hours 14: 3.2769; Hours 15: 3.1269; Hours 16: 2.9709; Hours 17: 3.1269; Hours 18: 2.9709; Hours 22: 2.9451; Hours 23: 3.1004; Hours 0: 3.2497; Hours 1: 3.2497; Hours 6: 3.2497 | 3.1567

## 23-03-2023
Performance Sheet Chiller
Date :- 23/03/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.9 | 0.9 | 1 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 0.9 | 1.1 | 1.1 | 1 | 0.9 | 1 | 1.1 | 0.9 | 1 | 1 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 0.99583
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 0.8 | 0.8 | 0.7 | 0.7 | 0.9 | 0.9 | 0.8 | 1.1 | 0.8 | 0.7 | 0.8 | 0.8 | 0.8 | 0.8 | 1.1 | 1 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.825
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.2 | 13.8 | 13.2 | 13.7 | 15.1 | 15.8 | 15.8 | 14.9 | 14.4 | 14.3 | 13.9 | 13.7 | 13.6 | 14.1 | 15.2 | 15.9 | 16.3 | 14.8 | 13.7 | 12.8 | 12.4 | 13.8 | 14.4 | 15 | 14.4083
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.1 | 6.1 | 5.7 | 6.1 | 7.2 | 7.7 | 7.9 | 7.2 | 7 | 6.6 | 6.3 | 6.1 | 5.9 | 6.2 | 7.4 | 8 | 8.2 | 6.8 | 5.9 | 5.4 | 5.5 | 6.1 | 6.6 | 7.2 | 6.675
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.9 | 24.9 | 24.7 | 24.9 | 25.2 | 25.2 | 25.6 | 25.1 | 25.4 | 25.4 | 25.2 | 24.8 | 24.8 | 24.6 | 24.9 | 24.8 | 25.4 | 24.9 | 24.8 | 24.8 | 24.7 | 24.6 | 24.7 | 24.8 | 24.9625
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.2 | 30 | 29.6 | 30 | 30.4 | 31.7 | 30.8 | 30.2 | 30.4 | 30.5 | 30.2 | 29.8 | 29.7 | 29.7 | 30.2 | 30.2 | 30.8 | 30.2 | 29.9 | 29.6 | 29.3 | 29.8 | 30 | 30 | 30.1333
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2600.8929 | 2472.4537 | 2408.2341 | 2440.3439 | 2536.6733 | 2600.8929 | 2536.6733 | 2472.4537 | 2376.1243 | 2472.4537 | 2440.3439 | 2440.3439 | 2472.4537 | 2536.6733 | 2504.5635 | 2536.6733 | 2600.8929 | 2568.7831 | 2504.5635 | 2376.1243 | 2215.5754 | 2472.4537 | 2504.5635 | 2504.5635 | 59595.7672
15 | Power Consumption of Chiller | KWH |  | 1600 | 1400 | 1500 | 1500 | 1600 | 1600 | 1400 | 1500 | 1500 | 1500 | 1400 | 1600 | 1500 | 1500 | 1500 | 1600 | 1500 | 1500 | 1500 | 1300 | 1600 | 1500 | 1600 | 1500 | 36200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.61517 | 0.56624 | 0.62286 | 0.61467 | 0.63075 | 0.61517 | 0.5519 | 0.60668 | 0.63128 | 0.60668 | 0.57369 | 0.65565 | 0.60668 | 0.59133 | 0.59891 | 0.63075 | 0.57673 | 0.58393 | 0.59891 | 0.54711 | 0.72216 | 0.60668 | 0.63883 | 0.59891 | 0.60799
17 | Average iKW/TR |  |  | Hours 7: 0.60799 | 0.60799
18 | COP of chiller |  |  | 5.7155 | 6.2094 | 5.6449 | 5.7202 | 5.5743 | 5.7155 | 6.3707 | 5.7954 | 5.5696 | 5.7954 | 6.1287 | 5.3627 | 5.7954 | 5.946 | 5.8707 | 5.5743 | 6.0965 | 6.0212 | 5.8707 | 6.4265 | 4.8687 | 5.7954 | 5.5038 | 5.8707 | 5.8018
19 | EER of Chiller |  |  | 19.5069 | 21.1927 | 19.266 | 19.5229 | 19.0252 | 19.5069 | 21.7431 | 19.7798 | 19.0092 | 19.7798 | 20.9174 | 18.3027 | 19.7798 | 20.2936 | 20.0367 | 19.0252 | 20.8073 | 20.5504 | 20.0367 | 21.9337 | 16.617 | 19.7798 | 18.7844 | 20.0367 | 19.8014
20 | LMTD of Condenser | ºC |  | 2.7462 | 2.6883 | 2.7606 | 2.8203 | 2.9795 | 3.3629 | 2.9795 | 2.9493 | 2.6591 | 2.9493 | 2.9189 | 2.7906 | 2.6299 | 2.8203 | 3.0097 | 2.7751 | 2.909 | 2.8796 | 2.6883 | 2.6005 | 2.5413 | 2.85 | 2.8796 | 2.85 | 2.8349
21 | LMTD of Evaporator | ºC |  | 3.5178 | 3.2583 | 3.206 | 3.0733 | 3.1494 | 3.5178 | 3.4647 | 3.2583 | 3.619 | 3.2583 | 3.0733 | 3.2322 | 3.2583 | 3.3103 | 3.2843 | 3.7585 | 3.668 | 3.3363 | 3.2843 | 3.1797 | 2.8933 | 3.0987 | 3.2843 | 3.2843 | 3.3029
Performance Sheet Chiller
Date :- 23/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.3; Hours 8: 1.4; Hours 12: 1.4; Hours 13: 1.2; Hours 14: 1.1; Hours 15: 1.3; Hours 16: 1.4; Hours 17: 1.2; Hours 18: 1.3; Hours 22: 1.3; Hours 23: 1.6; Hours 0: 1.5; Hours 1: 1.5; Hours 6: 1.4 | 1.35
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.8; Hours 8: 0.9; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.7; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 22: 0.9; Hours 23: 0.8; Hours 0: 0.7; Hours 1: 0.9; Hours 6: 0.8 | 0.80714
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 15.1; Hours 8: 13.7; Hours 12: 13.8; Hours 13: 13.8; Hours 14: 13.8; Hours 15: 13.8; Hours 16: 13.8; Hours 17: 13.8; Hours 18: 13.8; Hours 22: 13.5; Hours 23: 13.5; Hours 0: 13.5; Hours 1: 13.5; Hours 6: 13.5 | 13.7786
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 7.3; Hours 8: 6.3; Hours 12: 6.3; Hours 13: 6.3; Hours 14: 6.3; Hours 15: 6.3; Hours 16: 6.3; Hours 17: 6.3; Hours 18: 6.3; Hours 22: 6.2; Hours 23: 6.2; Hours 0: 6.2; Hours 1: 6.2; Hours 6: 6.2 | 6.3357
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 24.6; Hours 8: 24.8; Hours 12: 24.4; Hours 13: 24.4; Hours 14: 24.4; Hours 15: 24.4; Hours 16: 24.4; Hours 17: 24.4; Hours 18: 24.4; Hours 22: 24.8; Hours 23: 24.8; Hours 0: 24.8; Hours 1: 24.8; Hours 6: 24.8 | 24.5857
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 30.7; Hours 8: 30.7; Hours 12: 30.4; Hours 13: 30.4; Hours 14: 30.4; Hours 15: 30.4; Hours 16: 30.4; Hours 17: 30.4; Hours 18: 30.4; Hours 22: 30.5; Hours 23: 30.5; Hours 0: 30.5; Hours 1: 30.5; Hours 6: 30.5 | 30.4786
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 8: 4.3; Hours 12: 4.3; Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 22: 4.3; Hours 23: 4.3; Hours 0: 4.3; Hours 1: 4.3; Hours 6: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 6: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2504.5635; Hours 8: 2376.1243; Hours 12: 2408.2341; Hours 13: 2408.2341; Hours 14: 2408.2341; Hours 15: 2408.2341; Hours 16: 2408.2341; Hours 17: 2408.2341; Hours 18: 2408.2341; Hours 22: 2344.0146; Hours 23: 2344.0146; Hours 0: 2344.0146; Hours 1: 2344.0146; Hours 6: 2344.0146 | 33458.3995
15 | Power Consumption of Chiller | KWH |  | 1700 | 900 | 0 | 0 | 600 | 1600 | 1500 | 1500 | 1600 | 1500 | 1500 | 1000 | 0 | 0 | 0 | 1400 | 1500 | 1600 | 1500 | 100 | 0 | 0 | 0 | 1200 | 20700
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.67876; Hours 8: 0.37877; Hours 12: 0.66439; Hours 13: 0.62286; Hours 14: 0.62286; Hours 15: 0.66439; Hours 16: 0.62286; Hours 17: 0.62286; Hours 18: 0.41524; Hours 22: 0.59727; Hours 23: 0.63993; Hours 0: 0.68259; Hours 1: 0.63993; Hours 6: 0.51194 | 0.59748
17 | Average iKW/TR |  |  | Hours 7: 0.59748 | 0.59748
18 | COP of chiller |  |  | Hours 7: 5.18; Hours 8: 9.2827; Hours 12: 5.2921; Hours 13: 5.6449; Hours 14: 5.6449; Hours 15: 5.2921; Hours 16: 5.6449; Hours 17: 5.6449; Hours 18: 8.4674; Hours 22: 5.8868; Hours 23: 5.4944; Hours 0: 5.151; Hours 1: 5.4944; Hours 6: 6.868 | 6.0706
19 | EER of Chiller |  |  | Hours 7: 17.6794; Hours 8: 31.6819; Hours 12: 18.0619; Hours 13: 19.266; Hours 14: 19.266; Hours 15: 18.0619; Hours 16: 19.266; Hours 17: 19.266; Hours 18: 28.8991; Hours 22: 20.0917; Hours 23: 18.7523; Hours 0: 17.5803; Hours 1: 18.7523; Hours 6: 23.4404 | 20.719
20 | LMTD of Condenser | ºC |  | Hours 7: 3.5075; Hours 8: 3.5727; Hours 12: 3.6036; Hours 13: 3.3487; Hours 14: 3.2175; Hours 15: 3.4772; Hours 16: 3.6036; Hours 17: 3.3487; Hours 18: 3.4772; Hours 22: 3.3857; Hours 23: 3.7553; Hours 0: 3.6338; Hours 1: 3.6338; Hours 6: 3.5107 | 3.5054
21 | LMTD of Evaporator | ºC |  | Hours 7: 3.2843; Hours 8: 3.3309; Hours 12: 3.206; Hours 13: 3.206; Hours 14: 3.0478; Hours 15: 3.206; Hours 16: 3.206; Hours 17: 3.206; Hours 18: 3.206; Hours 22: 3.3039; Hours 23: 3.1533; Hours 0: 2.9966; Hours 1: 3.3039; Hours 6: 3.1533 | 3.2007

## 24-03-2023
Performance sheet of Chiller
Date :- 24/3/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.9 | 1 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.8 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.8 | 0.9 | 0.7 | 0.87826
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.9 | 0.8 | 0.7 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.9 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.78696
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.5 | 14.3 | 13.5 | 13.2 | 13.5 | 13.8 | 14.1 | 14.1 | 14.1 | 14.2 | 14.3 | 14.1 | 13.8 | 13.5 | 13.3 | 13.9 | 15.2 | 15.7 | 14.2 | 13.2 | 12.6 | 13.8 | 14.4 | 14.9 | 14.05
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.6 | 6.4 | 6 | 5.9 | 7.1 | 7.1 | 7.1 | 6.9 | 7.1 | 6.4 | 6.6 | 6.4 | 6.3 | 6.3 | 6.2 | 6.3 | 7.4 | 7.7 | 6.5 | 5.8 | 5.6 | 6.2 | 6.6 | 7 | 6.6042
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.2 | 24.8 | 24.9 | 25.3 | 25.1 | 25.3 | 25.2 | 25.2 | 25.4 | 25.4 | 25.1 | 25.2 | 25.3 | 25.6 | 25.3 | 25.1 | 25.7 | 25.7 | 25.4 | 24.5 | 23.8 | 23.6 | 23.7 | 23.7 | 24.9792
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.4 | 29.9 | 29.8 | 29.9 | 29.3 | 29.7 | 29.8 | 29.9 | 30.1 | 30.5 | 30.3 | 30.2 | 30.2 | 30.4 | 31.9 | 30.1 | 30.8 | 30.9 | 30.4 | 29.3 | 28.3 | 28.7 | 28.8 | 28.9 | 29.9375
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2536.6733 | 2408.2341 | 2344.0146 | 2055.0265 | 2151.3558 | 2247.6852 | 2311.9048 | 2247.6852 | 2504.5635 | 2472.4537 | 2472.4537 | 2408.2341 | 2311.9048 | 2279.795 | 2440.3439 | 2504.5635 | 2568.7831 | 2472.4537 | 2376.1243 | 2247.6852 | 2440.3439 | 2504.5635 | 2536.6733 | 57380.1918
15 | Power Consumption of Chiller | KWH |  | 1500 | 1400 | 1400 | 1300 | 1300 | 1500 | 1300 | 1400 | 1400 | 1500 | 1600 | 1500 | 1400 | 1500 | 1500 | 1400 | 1500 | 1500 | 1400 | 1400 | 1400 | 1600 | 1300 | 1500 | 34500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.59133 | 0.5519 | 0.58134 | 0.5546 | 0.6326 | 0.69723 | 0.57837 | 0.60556 | 0.62286 | 0.59891 | 0.64713 | 0.60668 | 0.58134 | 0.64882 | 0.65795 | 0.57369 | 0.59891 | 0.58393 | 0.56624 | 0.58919 | 0.62286 | 0.65565 | 0.51905 | 0.59133 | 0.6024
17 | Average iKW/TR |  |  | Hours 7: 0.6024 | 0.6024
18 | COP of chiller |  |  | 5.946 | 6.3707 | 6.0481 | 6.3397 | 5.5581 | 5.0428 | 6.0791 | 5.8062 | 5.6449 | 5.8707 | 5.4332 | 5.7954 | 6.0481 | 5.4191 | 5.3438 | 6.1287 | 5.8707 | 6.0212 | 6.2094 | 5.9675 | 5.6449 | 5.3627 | 6.7739 | 5.946 | 5.8613
19 | EER of Chiller |  |  | 20.2936 | 21.7431 | 20.6422 | 21.6373 | 18.9696 | 17.211 | 20.748 | 19.8165 | 19.266 | 20.0367 | 18.5436 | 19.7798 | 20.6422 | 18.4954 | 18.2385 | 20.9174 | 20.0367 | 20.5504 | 21.1927 | 20.367 | 19.266 | 18.3027 | 23.1193 | 20.2936 | 20.0046
20 | LMTD of Condenser | ºC |  | 2.85 | 2.8203 | 2.6299 | 2.5413 | 2.4213 | 2.4816 | 2.5413 | 2.4379 | 2.5709 | 2.6883 | 2.7173 | 2.6591 | 2.4954 | 2.6005 | 2.9668 | 2.6591 | 2.6883 | 2.5808 | 2.6591 | 2.6005 | 2.3799 | 2.6883 | 2.4119 | 2.688 | 2.6157
21 | LMTD of Evaporator | ºC |  | 3.3103 | 3.4647 | 3.206 | 2.9966 | 3.0575 | 2.9937 | 3.0739 | 3.1269 | 3.2225 | 3.2843 | 3.2583 | 3.2583 | 3.0478 | 2.9709 | 3.1004 | 3.2322 | 3.4381 | 3.1746 | 3.0987 | 3.1797 | 2.9192 | 3.0733 | 3.2843 | 3.3103 | 3.1701
Performance S+A34:AC65heet Chiller
Date :- 24/3/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.2 | 1.1 | 1 | 1.2 | 1.4 | 1.2 | 1.3 | 1.2 | 1 | 1.2 | 1.3 | 1.1 |  |  |  | 1.2 | 1.4 | 1.4 |  |  |  |  | 1.4 | 1.225
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.9 | 0.8 | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.7 | 0.6 |  |  |  | 0.9 | 0.8 | 0.8 |  |  |  |  | 0.8 | 0.74375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.4 | 14.1 | 13.6 | 13.1 | 13.6 | 13.6 | 13.9 | 13.9 | 13.7 | 13.7 | 14.1 | 14 | 13.7 |  |  |  | 13.9 | 13.9 | 13.9 |  |  |  |  | 13.9 | 13.8824
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.7 | 6.6 | 5.9 | 5.9 | 7.1 | 6.9 | 7.1 | 6.9 | 7.2 | 6.8 | 6.9 | 6.7 | 6.6 |  |  |  | 6.4 | 6.4 | 6.4 |  |  |  |  | 6.4 | 6.7
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.9 | 24.6 | 24.7 | 24.8 | 24.8 | 25.1 | 25.1 | 25.1 | 25.2 | 25.4 | 25 | 24.9 | 25.2 |  |  |  | 25.1 | 25.1 | 25.1 |  |  |  |  | 25.1 | 25.0118
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 31.1 | 30.3 | 30.5 | 30.7 | 29.8 | 30.6 | 30.3 | 30.4 | 30.6 | 31.1 | 30.7 | 30.8 | 30.6 |  |  |  | 31.1 | 31.1 | 31.1 |  |  |  |  | 31.1 | 30.7
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  | 4.3 | 4.3 | 4.3 |  |  |  |  | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3 | 3 | 3 |  |  |  |  | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 |  |  |  |  | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8 | 0.8 | 0.8 |  |  |  |  | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  | 971 | 971 | 971 |  |  |  |  | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2472.4537 | 2408.2341 | 2472.4537 | 2311.9048 | 2087.1362 | 2151.3558 | 2183.4656 | 2247.6852 | 2087.1362 | 2215.5754 | 2311.9048 | 2344.0146 | 2279.795 |  |  |  | 2408.2341 | 2408.2341 | 2408.2341 |  |  |  |  | 2408.2341 | 39206.0516
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1400 | 1300 | 1400 | 1500 | 1400 | 1400 | 1500 | 1500 | 1600 | 1400 | 1500 | 700 | 0 | 400 | 1600 | 1600 | 1600 | 200 | 0 | 0 | 0 | 1200 | 26300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.60668 | 0.66439 | 0.56624 | 0.56231 | 0.67078 | 0.69723 | 0.64118 | 0.62286 | 0.71869 | 0.67703 | 0.69207 | 0.59727 | 0.65795 |  |  |  | 0.66439 | 0.66439 | 0.66439 |  |  |  |  | 0.49829 | 0.63918
17 | Average iKW/TR |  |  | Hours 7: 0.63918 | 0.63918
18 | COP of chiller |  |  | 5.7954 | 5.2921 | 6.2094 | 6.2528 | 5.2417 | 5.0428 | 5.4836 | 5.6449 | 4.8922 | 5.1933 | 5.0804 | 5.8868 | 5.3438 |  |  |  | 5.2921 | 5.2921 | 5.2921 |  |  |  |  | 7.0561 | 5.5466
19 | EER of Chiller |  |  | 19.7798 | 18.0619 | 21.1927 | 21.3409 | 17.8899 | 17.211 | 18.7156 | 19.266 | 16.6972 | 17.7248 | 17.3394 | 20.0917 | 18.2385 |  |  |  | 18.0619 | 18.0619 | 18.0619 |  |  |  |  | 24.0826 | 18.9305
20 | LMTD of Condenser | ºC |  | 3.4082 | 3.1291 | 3.0257 | 3.3188 | 3.2899 | 3.1981 | 3.2309 | 3.1371 | 2.909 | 3.2586 | 3.3857 | 3.1882 | 2.909 |  |  |  | 3.6036 | 3.6036 | 3.0834 |  |  |  |  | 3.381 | 3.2388
21 | LMTD of Evaporator | ºC |  | 3.2583 | 3.3578 | 3.2583 | 2.9709 | 2.7888 | 2.9937 | 2.8673 | 2.9192 | 2.9398 | 2.8933 | 2.6332 | 2.9966 | 2.7821 |  |  |  | 3.3578 | 3.206 | 3.206 |  |  |  |  | 3.206 | 3.0373

## 02-02-2019 (hidden)
Performance Sheet Chiller
Date :- 02/02/2019
CHILLER NO. 02
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 14: 2.4; Hours 15: 2.4; Hours 16: 2.4; Hours 17: 2.3; Hours 18: 2.2; Hours 19: 2.2; Hours 20: 2.1; Hours 21: 2.1 | 2.2625
2 | Small temperature difference of evaporator | ºC |  | Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.3; Hours 18: 0.3; Hours 19: 0.3; Hours 20: 0.6; Hours 21: 0.6 | 0.45
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 14: 14.7; Hours 15: 14.7; Hours 16: 14.7; Hours 17: 13.8; Hours 18: 13.7; Hours 19: 13.5; Hours 20: 13.5; Hours 21: 13.2 | 13.975
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 14: 8.1; Hours 15: 8.1; Hours 16: 8.1; Hours 17: 7.8; Hours 18: 7.9; Hours 19: 7.9; Hours 20: 8; Hours 21: 7.8 | 7.9625
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 14: 25.1; Hours 15: 25.1; Hours 16: 25.1; Hours 17: 25.2; Hours 18: 25; Hours 19: 24.7; Hours 20: 24.2; Hours 21: 23.8 | 24.775
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 14: 30; Hours 15: 30; Hours 16: 30; Hours 17: 29.7; Hours 18: 29.3; Hours 19: 28.9; Hours 20: 28.3; Hours 21: 28 | 29.275
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 14: 2119.246; Hours 15: 2119.246; Hours 16: 2119.246; Hours 17: 1926.5873; Hours 18: 1862.3677; Hours 19: 1798.1481; Hours 20: 1766.0384; Hours 21: 1733.9286 | 15444.8082
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 1400 | 1400 | 1200 | 1200 | 1200 | 1200 | 1100 | 1400 | [9 empty] | 10400
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 14: 0.66061; Hours 15: 0.66061; Hours 16: 0.56624; Hours 17: 0.62286; Hours 18: 0.64434; Hours 19: 0.66735; Hours 20: 0.62286; Hours 21: 0.80742 | 0.65654
17 | Average iKW/TR |  |  | Hours 7: 0.65654 | 0.65654
18 | COP of chiller |  |  | Hours 14: 5.3223; Hours 15: 5.3223; Hours 16: 6.2094; Hours 17: 5.6449; Hours 18: 5.4567; Hours 19: 5.2686; Hours 20: 5.6449; Hours 21: 4.3546 | 5.403
19 | EER of Chiller |  |  | Hours 14: 18.1651; Hours 15: 18.1651; Hours 16: 21.1927; Hours 17: 19.266; Hours 18: 18.6238; Hours 19: 17.9816; Hours 20: 19.266; Hours 21: 14.8624 | 18.4404
20 | LMTD of Condenser | ºC |  | Hours 14: 4.4049; Hours 15: 4.4049; Hours 16: 4.4049; Hours 17: 4.1512; Hours 18: 3.9692; Hours 19: 3.9332; Hours 20: 3.7871; Hours 21: 3.823 | 4.1098
21 | LMTD of Evaporator | ºC |  | Hours 14: 2.4875; Hours 15: 2.4875; Hours 16: 2.4875; Hours 17: 1.9708; Hours 18: 1.9255; Hours 19: 1.8799; Hours 20: 2.3716; Hours 21: 2.3452 | 2.2444
Performance Sheet Chiller
Date :- 02/02/2019
CHILLER NO. 06
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 3.5 | 3.3 | 3.3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 2.7 | 2.4 | 2.5 | 2.3 | 2.4 | 2.3 | 2.3 | 2.7 | 2.7 | 2.9 | 2.5 | 2.7 | 2.6 | 2.8 | 2.9 | 3.2 | 2.8333
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.2 | 0.3 | 0.2 | 0.2 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.4 | 0.3 | 0.4 | 0.34583
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.3 | 13.7 | 13.7 | 13.7 | 13.8 | 13.8 | 14.3 | 15 | 14.6 | 13.8 | 13.8 | 13.6 | 13.5 | 13.2 | 13.3 | 13 | 12.3 | 13 | 13.3 | 13.5 | 13.6 | 13.6 | 13.7 | 13.5917
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.6 | 5.6 | 5.6 | 5.5 | 5.6 | 5.7 | 6 | 6.5 | 7.9 | 8 | 8 | 8.1 | 8 | 7.9 | 7.1 | 5.9 | 5.6 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.5 | 6.3083
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.2 | 19.8 | 19.8 | 20.1 | 20 | 20.7 | 22 | 22.7 | 22.9 | 24.9 | 25.4 | 25.1 | 24.8 | 24.3 | 24 | 23.6 | 24.4 | 22.3 | 21.1 | 20.9 | 21.3 | 22 | 21.9 | 22.1 | 22.3458
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 25.4 | 25 | 25.1 | 25.5 | 25.4 | 26.3 | 27.7 | 28.5 | 28.7 | 30 | 29.6 | 29 | 28.6 | 28.1 | 27.7 | 28 | 29.5 | 27 | 26.1 | 26.1 | 26.6 | 27.3 | 27.3 | 27.6 | 27.3375
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | `
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2472.4537 | 2600.8929 | 2600.8929 | 2633.0026 | 2633.0026 | 2600.8929 | 2665.1124 | 2729.332 | 2151.3558 | 1862.3677 | 1862.3677 | 1766.0384 | 1766.0384 | 1701.8188 | 1990.8069 | 2279.795 | 2151.3558 | 2408.2341 | 2504.5635 | 2568.7831 | 2568.7831 | 2568.7831 | 2633.0026 | 56127.9101
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1400 | 1500 | 1400 | 1600 | 1500 | 1300 | 1300 | 1100 | 1200 | 1000 | 1100 | 1200 | 1300 | 1400 | 1300 | 1300 | 1300 | 1500 | 1500 | 1600 | 1400 | 1500 | 32500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58134 | 0.56624 | 0.53828 | 0.57673 | 0.53171 | 0.60767 | 0.57673 | 0.48778 | 0.47631 | 0.51131 | 0.64434 | 0.53695 | 0.62286 | 0.67949 | 0.76389 | 0.70323 | 0.57023 | 0.60427 | 0.53981 | 0.59891 | 0.58393 | 0.62286 | 0.54501 | 0.56969 | 0.58498
17 | Average iKW/TR |  |  | Hours 7: 0.58498 | 0.58498
18 | COP of chiller |  |  | 6.0481 | 6.2094 | 6.532 | 6.0965 | 6.6126 | 5.786 | 6.0965 | 7.2081 | 7.3818 | 6.8765 | 5.4567 | 6.5481 | 5.6449 | 5.1745 | 4.6028 | 4.9998 | 6.166 | 5.8186 | 6.5133 | 5.8707 | 6.0212 | 5.6449 | 6.4513 | 6.1718 | 6.0805
19 | EER of Chiller |  |  | 20.6422 | 21.1927 | 22.2936 | 20.8073 | 22.5688 | 19.7477 | 20.8073 | 24.6013 | 25.1941 | 23.4695 | 18.6238 | 22.3486 | 19.266 | 17.6605 | 15.7092 | 17.0642 | 21.0445 | 19.8588 | 22.2301 | 20.0367 | 20.5504 | 19.266 | 22.0183 | 21.0642 | 20.7528
20 | LMTD of Condenser | ºC |  | 5.7108 | 5.496 | 5.5333 | 5.4622 | 5.4622 | 5.5358 | 5.5724 | 5.6089 | 5.0575 | 4.4759 | 4.2604 | 3.9329 | 4.0039 | 3.8959 | 3.8588 | 4.5509 | 4.8074 | 4.8784 | 4.5512 | 4.8435 | 4.769 | 4.9894 | 5.1353 | 5.4991 | 4.9121
21 | LMTD of Evaporator | ºC |  | 2.5141 | 2.5597 | 2.6502 | 2.6502 | 2.6727 | 2.6727 | 2.6502 | 2.6951 | 2.5157 | 2.1271 | 2.1161 | 1.7053 | 1.857 | 1.6418 | 1.5992 | 2.2116 | 2.215 | 2.1271 | 2.5141 | 2.5824 | 2.4095 | 2.6277 | 2.4095 | 2.6727 | 2.3499

## 03-02-2019 (hidden)
Performance Sheet Chiller
Date :- 03/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 13: 2.6; Hours 14: 2.4; Hours 15: 2.4; Hours 16: 2.4; Hours 17: 2.2; Hours 18: 2.2; Hours 19: 2.2; Hours 20: 2.2; Hours 21: 2.1; Hours 22: 2.1; Hours 23: 2.2 | 2.2727
2 | Small temperature difference of evaporator | ºC |  | Hours 13: 0.3; Hours 14: 0.3; Hours 15: 0.3; Hours 16: 0.3; Hours 17: 0.3; Hours 18: 0.3; Hours 19: 0.4; Hours 20: 0.3; Hours 21: 0.3; Hours 22: 0.3; Hours 23: 0.3 | 0.30909
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 13: 14.3; Hours 14: 15; Hours 15: 14.4; Hours 16: 14.3; Hours 17: 14.3; Hours 18: 14.3; Hours 19: 14.3; Hours 20: 14; Hours 21: 13.9; Hours 22: 13.8; Hours 23: 13.8 | 14.2182
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 13: 10.1; Hours 14: 8.1; Hours 15: 7.8; Hours 16: 8; Hours 17: 8; Hours 18: 7.9; Hours 19: 7.9; Hours 20: 8; Hours 21: 8; Hours 22: 7.9; Hours 23: 7.9 | 8.1455
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 13: 19.3; Hours 14: 25.1; Hours 15: 26.6; Hours 16: 26.6; Hours 17: 26.2; Hours 18: 26.6; Hours 19: 26; Hours 20: 25.7; Hours 21: 25.5; Hours 22: 25; Hours 23: 25 | 25.2364
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 13: 24.3; Hours 14: 29.3; Hours 15: 30.8; Hours 16: 30.6; Hours 17: 30.2; Hours 18: 30.7; Hours 19: 30.1; Hours 20: 29.6; Hours 21: 29.3; Hours 22: 28.8; Hours 23: 28.7 | 29.3091
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 13: 1348.6111; Hours 14: 2215.5754; Hours 15: 2119.246; Hours 16: 2022.9167; Hours 17: 2022.9167; Hours 18: 2055.0265; Hours 19: 2055.0265; Hours 20: 1926.5873; Hours 21: 1894.4775; Hours 22: 1894.4775; Hours 23: 1894.4775 | 21449.3386
15 | Power Consumption of Chiller | KWH |  | Hours 13: 1400; Hours 14: 1400; Hours 15: 1300; Hours 16: 1300; Hours 17: 1300; Hours 18: 1300; Hours 19: 1300; Hours 20: 1300; Hours 21: 1400; Hours 22: 1400; Hours 23: 1400 | 14800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 13: 1.0381; Hours 14: 0.63189; Hours 15: 0.61343; Hours 16: 0.64264; Hours 17: 0.64264; Hours 18: 0.6326; Hours 19: 0.6326; Hours 20: 0.67477; Hours 21: 0.73899; Hours 22: 0.73899; Hours 23: 0.73899 | 0.70233
17 | Average iKW/TR |  |  | Hours 7: 0.70233 | 0.70233
18 | COP of chiller |  |  | Hours 13: 3.3869; Hours 14: 5.5643; Hours 15: 5.7317; Hours 16: 5.4712; Hours 17: 5.4712; Hours 18: 5.5581; Hours 19: 5.5581; Hours 20: 5.2107; Hours 21: 4.7578; Hours 22: 4.7578; Hours 23: 4.7578 | 5.1114
19 | EER of Chiller |  |  | Hours 13: 11.5596; Hours 14: 18.9908; Hours 15: 19.5624; Hours 16: 18.6732; Hours 17: 18.6732; Hours 18: 18.9696; Hours 19: 18.9696; Hours 20: 17.784; Hours 21: 16.2385; Hours 22: 16.2385; Hours 23: 16.2385 | 17.4453
20 | LMTD of Condenser | ºC |  | Hours 13: 4.6614; Hours 14: 4.1518; Hours 15: 4.1518; Hours 16: 4.0782; Hours 17: 3.8607; Hours 18: 3.897; Hours 19: 3.897; Hours 20: 3.8242; Hours 21: 3.6786; Hours 22: 3.6786; Hours 23: 3.7507 | 3.9663
21 | LMTD of Evaporator | ºC |  | Hours 13: 1.5509; Hours 14: 2.1711; Hours 15: 2.1049; Hours 16: 2.0381; Hours 17: 2.0381; Hours 18: 2.0605; Hours 19: 2.2589; Hours 20: 1.9708; Hours 21: 1.9481; Hours 22: 1.9481; Hours 23: 1.9481 | 2.0034
Performance Sheet Chiller
Date :- 03/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 3.2 | 3.4 | 3.4 | 3.3 | 3.3 | 3.3 | 2.7 | 2.7 | 2.7 | 2.5 | 2.8 | 2.8 | 2.8 | 2.6 | 2.6 | 2.8 | 2.9 | 2.5 | 2.9 | 2.9 | 3 | 3.1 | 3.1 | 3.2 | 2.9375
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.46667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.6 | 13.7 | 14 | 14 | 14.2 | 14.3 | 14.8 | 15 | 14.4 | 14.3 | 14.2 | 14.2 | 14.2 | 14 | 13.8 | 13.7 | 13.7 | 13.5 | 12.1 | 12.7 | 13.4 | 13.7 | 13.7 | 13.7 | 13.8708
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.5 | 5.6 | 5.7 | 5.7 | 5.9 | 6.3 | 8 | 8 | 8 | 7.9 | 8 | 8 | 7.8 | 8 | 8 | 8 | 6.1 | 5.3 | 5.6 | 5.5 | 5.6 | 5.5 | 5.6 | 6.6333
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.9 | 22 | 21.6 | 21.2 | 21.5 | 22.2 | 22.4 | 24.7 | 26.5 | 26.3 | 26.1 | 26.4 | 25.7 | 25.6 | 25.1 | 24.8 | 24.7 | 25.6 | 25.3 | 22.6 | 22.4 | 22.2 | 22 | 21.9 | 23.7792
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.5 | 27.5 | 27.2 | 27 | 27.1 | 27.7 | 28.1 | 29.6 | 31.1 | 30.8 | 30.5 | 30.8 | 30.3 | 30 | 29.3 | 29.1 | 28.8 | 30.7 | 30.1 | 27.4 | 27.7 | 27.7 | 27.4 | 27.6 | 28.7917
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2568.7831 | 2633.0026 | 2697.2222 | 2665.1124 | 2729.332 | 2697.2222 | 2729.332 | 2247.6852 | 2055.0265 | 2022.9167 | 2022.9167 | 1990.8069 | 1990.8069 | 1990.8069 | 1862.3677 | 1830.2579 | 1830.2579 | 2376.1243 | 2183.4656 | 2279.795 | 2536.6733 | 2600.8929 | 2633.0026 | 2600.8929 | 55774.7024
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1300 | 1300 | 1300 | 1300 | 1300 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 33100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.54501 | 0.53171 | 0.51905 | 0.52531 | 0.51295 | 0.51905 | 0.47631 | 0.57837 | 0.6326 | 0.64264 | 0.64264 | 0.70323 | 0.70323 | 0.70323 | 0.75173 | 0.76492 | 0.76492 | 0.58919 | 0.64118 | 0.61409 | 0.5519 | 0.53828 | 0.53171 | 0.53828 | 0.60506
17 | Average iKW/TR |  |  | Hours 7: 0.60506 | 0.60506
18 | COP of chiller |  |  | 6.4513 | 6.6126 | 6.7739 | 6.6932 | 6.8545 | 6.7739 | 7.3818 | 6.0791 | 5.5581 | 5.4712 | 5.4712 | 4.9998 | 4.9998 | 4.9998 | 4.6772 | 4.5966 | 4.5966 | 5.9675 | 5.4836 | 5.7255 | 6.3707 | 6.532 | 6.6126 | 6.532 | 5.9256
19 | EER of Chiller |  |  | 22.0183 | 22.5688 | 23.1193 | 22.844 | 23.3945 | 23.1193 | 25.1941 | 20.748 | 18.9696 | 18.6732 | 18.6732 | 17.0642 | 17.0642 | 17.0642 | 15.9633 | 15.6881 | 15.6881 | 20.367 | 18.7156 | 19.5413 | 21.7431 | 22.2936 | 22.5688 | 22.2936 | 20.2241
20 | LMTD of Condenser | ºC |  | 5.5358 | 5.7156 | 5.7527 | 5.7179 | 5.6444 | 5.6075 | 5.0221 | 4.7348 | 4.6249 | 4.3705 | 4.6587 | 4.6587 | 4.7332 | 4.4427 | 4.3686 | 4.6213 | 4.6527 | 4.5869 | 4.9155 | 4.9155 | 5.2081 | 5.3903 | 5.3536 | 5.5724 | 5.0335
21 | LMTD of Evaporator | ºC |  | 2.6277 | 2.6727 | 2.7175 | 2.8941 | 2.9408 | 2.7175 | 2.7399 | 2.1931 | 2.0605 | 2.0381 | 2.0381 | 2.0158 | 5.5328 | 2.0158 | 1.9255 | 1.9027 | 1.9027 | 2.2803 | 2.3526 | 2.4222 | 2.6051 | 2.4308 | 2.4521 | 2.6502 | 2.5054

## 04-02-2019 (hidden)
Performance Sheet Chiller
Date :- 04/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 2.5 | 1.9 | 2 | 2.1 | 2.1 | 2.1 | 2.1 | 2.6 | 2.6 | 2.6 | 2.4 | 2.2 | 2.3 | 2.3 | 2.3 | 2.2 | 2.3 | 2.3 | 2.3 | 2.3 | 2.4 | 2.5 | 2.2909
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.6 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.4 | 0.3 | 0.2 | 0.4 | 0.3 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.8 | 0.9 | 0.9 | 0.44545
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 14.3 | 14.3 | 12.8 | 13 | 13.2 | 13.3 | 13.6 | 13.7 | 13.8 | 13.9 | 14.1 | 14.2 | 14.2 | 14.1 | 13.6 | 13 | 12.3 | 13.1 | 13.6 | 13.8 | 14 | 14.1 | 13.6364
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 8 | 8 | 7.9 | 8 | 8 | 8.1 | 8.1 | 8.1 | 8.1 | 8 | 8 | 8 | 8 | 7.2 | 7 | 6.1 | 5.5 | 5.7 | 6 | 6.2 | 6.3 | 6.4 | 7.3045
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 23.8 | 23.8 | 24.1 | 24.2 | 24.5 | 24.7 | 25.3 | 25.2 | 26.9 | 27.1 | 27.2 | 27.2 | 27 | 27.2 | 27.2 | 27.3 | 26 | 24.2 | 23.9 | 23.8 | 23.6 | 23.5 | 25.35
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 28.5 | 28.5 | 27.8 | 28.1 | 28.3 | 28.7 | 29.5 | 29.5 | 31.3 | 31.8 | 31.8 | 31.8 | 31.7 | 32.4 | 32.2 | 32.5 | 31.1 | 29.7 | 29.6 | 29.5 | 29.3 | 29.3 | 30.1318
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2022.9167 | 2022.9167 | 1573.3796 | 1605.4894 | 1669.709 | 1669.709 | 1766.0384 | 1798.1481 | 1830.2579 | 1894.4775 | 1958.6971 | 1990.8069 | 1990.8069 | 2215.5754 | 2119.246 | 2215.5754 | 2183.4656 | 2376.1243 | 2440.3439 | 2440.3439 | 2472.4537 | 2472.4537 | 44728.9352
15 | Power Consumption of Chiller | KWH |  |  |  | 1500 | 1600 | 1000 | 700 | 1200 | 1200 | 1300 | 1300 | 1400 | 1300 | 1600 | 1400 | 1600 | 1600 | 1500 | 1400 | 1700 | 1600 | 1600 | 1600 | 1600 | 1700 | 31400
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.7415 | 0.79094 | 0.63557 | 0.436 | 0.71869 | 0.71869 | 0.73611 | 0.72297 | 0.76492 | 0.68621 | 0.81687 | 0.70323 | 0.80369 | 0.72216 | 0.7078 | 0.63189 | 0.77858 | 0.67337 | 0.65565 | 0.65565 | 0.64713 | 0.68758 | 0.7016
17 | Average iKW/TR |  |  | Hours 7: 0.7016 | 0.7016
18 | COP of chiller |  |  |  |  | 4.7417 | 4.4454 | 5.532 | 8.0641 | 4.8922 | 4.8922 | 4.7765 | 4.8633 | 4.5966 | 5.1238 | 4.3042 | 4.9998 | 4.3748 | 4.8687 | 4.9675 | 5.5643 | 4.5159 | 5.2215 | 5.3627 | 5.3627 | 5.4332 | 5.1136 | 5.0917
19 | EER of Chiller |  |  |  |  | 16.1835 | 15.172 | 18.8807 | 27.5229 | 16.6972 | 16.6972 | 16.302 | 16.5984 | 15.6881 | 17.4876 | 14.6904 | 17.0642 | 14.9312 | 16.617 | 16.9541 | 18.9908 | 15.4128 | 17.8211 | 18.3027 | 18.3027 | 18.5436 | 17.4528 | 17.3779
20 | LMTD of Condenser | ºC |  |  |  | 4.4432 | 3.7744 | 3.5328 | 3.7149 | 3.6786 | 3.7511 | 3.823 | 4.4057 | 4.4427 | 4.5527 | 4.2973 | 4.0763 | 4.2228 | 4.3993 | 4.3291 | 4.2868 | 4.3643 | 4.5037 | 4.5727 | 4.5727 | 4.686 | 4.8335 | 4.2393
21 | LMTD of Evaporator | ºC |  |  |  | 2.5795 | 2.0381 | 1.7177 | 1.7411 | 1.7877 | 1.7877 | 2.0437 | 1.8799 | 1.9027 | 2.1401 | 1.9933 | 1.7889 | 2.2116 | 2.1711 | 2.1049 | 2.3759 | 2.7067 | 2.8568 | 2.9064 | 3.2322 | 3.4114 | 3.4114 | 2.3086
Performance Sheet Chiller
Date :- 04/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 3.2 | 3.2 | 2.6 | 2.1 | 2.2 | 2.3 | 2.3 | 2.2 | 2.4 | 2.5 | 2.5 | 2.5 | 2.6 | 2.6 | 2.3 | 2.3 | [8 empty] | 2.4875
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.2 | 0.2 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | [8 empty] | 0.2875 | 1
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.8 | 14 | 14.4 | 14.6 | 12.9 | 13.1 | 13.4 | 13.5 | 13.7 | 13.8 | 13.8 | 14 | 14.2 | 14.3 | 14.3 | 14.2 | [8 empty] | 13.875
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.6 | 5.9 | 8.1 | 8 | 7.8 | 8.1 | 8 | 8 | 8 | 8.1 | 8.1 | 7.9 | 8 | 8 | 7.1 | [8 empty] | 7.5187
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.9 | 22 | 21.7 | 23.7 | 24.2 | 24.3 | 24.6 | 24.7 | 25.2 | 25.3 | 26.5 | 27.2 | 27.2 | 27.2 | 27.1 | 27.3 | [8 empty] | 25.0063
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.4 | 27.3 | 27.3 | 28.2 | 27.7 | 28 | 28.2 | 28.6 | 29.2 | 29.5 | 30.8 | 31.8 | 31.6 | 31.7 | 31.5 | 32.3 | [8 empty] | 29.4438
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2633.0026 | 2697.2222 | 2729.332 | 2087.1362 | 1573.3796 | 1701.8188 | 1701.8188 | 1766.0384 | 1830.2579 | 1862.3677 | 1830.2579 | 1894.4775 | 2022.9167 | 2022.9167 | 2022.9167 | 2279.795 | [8 empty] | 32655.6548
15 | Power Consumption of Chiller | KWH |  | 1400 | 1200 | 1100 | 1100 | 1100 | 1000 | 1100 | 1100 | 1100 | 1300 | 1400 | 1200 | 1500 | 1300 | 1500 | 1500 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53171 | 0.4449 | 0.40303 | 0.52704 | 0.69913 | 0.58761 | 0.64637 | 0.62286 | 0.60101 | 0.69804 | 0.76492 | 0.63342 | 0.7415 | 0.64264 | 0.7415 | 0.65795 | [8 empty] | 0.62148
17 | Average iKW/TR |  |  | Hours 7: 0.62148 | 0.62148
18 | COP of chiller |  |  | 6.6126 | 7.9029 | 8.7239 | 6.6712 | 5.0291 | 5.9836 | 5.4396 | 5.6449 | 5.8502 | 5.037 | 4.5966 | 5.5508 | 4.7417 | 5.4712 | 4.7417 | 5.3438 | [8 empty] | 5.8338
19 | EER of Chiller |  |  | 22.5688 | 26.9725 | 29.7748 | 22.769 | 17.1643 | 20.422 | 18.5655 | 19.266 | 19.9666 | 17.1912 | 15.6881 | 18.9449 | 16.1835 | 18.6732 | 16.1835 | 18.2385 | [8 empty] | 19.9108
20 | LMTD of Condenser | ºC |  | 5.4991 | 5.4252 | 4.8754 | 3.9297 | 3.6764 | 3.8588 | 3.8215 | 3.8242 | 4.0782 | 4.2604 | 4.2973 | 4.407 | 4.4427 | 4.4795 | 4.1152 | 4.3291 | [8 empty] | 4.3325
21 | LMTD of Evaporator | ºC |  | 2.6727 | 2.7175 | 2.253 | 1.851 | 1.7177 | 1.5992 | 1.8109 | 1.857 | 1.9027 | 1.9255 | 1.9027 | 1.9481 | 2.0381 | 2.0381 | 1.8097 | 2.215 | [8 empty] | 2.0162

## 05-02-2019 (hidden)
Performance Sheet Chiller
Date :- 05/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.5 | 2.5 | 2.5 | 2.6 | 2.1 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 2 | 1.9 | 1.9 | 1.8 | 1.8 | 1.8 | 1.7 | [7 empty] | 2.0059
2 | Small temperature difference of evaporator | ºC |  | 1.1 | 1.2 | 1.2 | 1.3 | 0.7 | 0.5 | 0.5 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | [7 empty] | 0.58824
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.1 | 14.1 | 14.6 | 14.7 | 15 | 15 | 14 | 13.7 | 13.9 | 14.1 | 14.3 | 14.4 | 14.1 | 14 | 13.7 | 13.6 | 13.3 | [7 empty] | 14.1529
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.5 | 6.5 | 6.8 | 7 | 7.1 | 8 | 7.8 | 8 | 8 | 8 | 7.2 | 7.2 | 7 | 7 | 7 | 6.6 | 6.4 | [7 empty] | 7.1824
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.4 | 22.8 | 22.4 | 22.4 | 22.5 | 25 | 25.5 | 25 | 26.8 | 27.1 | 27.4 | 27.2 | 27.4 | 27.5 | 27.3 | 27.4 | 27.7 | [7 empty] | 25.5765
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.2 | 28.6 | 28.3 | 28.3 | 28.5 | 30.2 | 30 | 29.5 | 31.3 | 31.7 | 32.8 | 32.6 | 32.7 | 32.7 | 32.4 | 32.7 | 32.9 | [7 empty] | 30.8471
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2440.3439 | 2504.5635 | 2472.4537 | 2536.6733 | 2247.6852 | 1990.8069 | 1830.2579 | 1894.4775 | 1958.6971 | 2279.795 | 2311.9048 | 2279.795 | 2247.6852 | 2151.3558 | 2247.6852 | 2215.5754 | [7 empty] | 38050.0992
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1400 | 1300 | 1600 | 1500 | 1800 | 1600 | [7 empty] | 25700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.61467 | 0.61467 | 0.59891 | 0.60668 | 0.59133 | 0.66735 | 0.75346 | 0.81956 | 0.79178 | 0.76582 | 0.65795 | 0.60556 | 0.57023 | 0.71184 | 0.69723 | 0.80082 | 0.72216 | [7 empty] | 0.68177
17 | Average iKW/TR |  |  | Hours 7: 0.68177 | 0.68177
18 | COP of chiller |  |  | 5.7202 | 5.7202 | 5.8707 | 5.7954 | 5.946 | 5.2686 | 4.6665 | 4.2901 | 4.4407 | 4.5912 | 5.3438 | 5.8062 | 6.166 | 4.9393 | 5.0428 | 4.3905 | 4.8687 | [7 empty] | 5.2275
19 | EER of Chiller |  |  | 19.5229 | 19.5229 | 20.0367 | 19.7798 | 20.2936 | 17.9816 | 15.9266 | 14.6422 | 15.156 | 15.6697 | 18.2385 | 19.8165 | 21.0445 | 16.8578 | 17.211 | 14.9847 | 16.617 | [7 empty] | 17.8413
20 | LMTD of Condenser | ºC |  | 4.8335 | 4.8335 | 4.8682 | 4.9808 | 4.4447 | 3.8288 | 3.5921 | 3.5921 | 3.5921 | 3.6263 | 4.1274 | 4.0118 | 3.9783 | 3.8288 | 3.7954 | 3.8621 | 3.7119 | [7 empty] | 4.0887
21 | LMTD of Evaporator | ºC |  | 3.675 | 3.8144 | 3.8712 | 3.9796 | 3.1494 | 2.5849 | 2.389 | 2.0921 | 1.9481 | 1.9933 | 2.4222 | 2.4453 | 2.215 | 2.1931 | 2.1271 | 2.3991 | 2.3759 | [7 empty] | 2.6867
Performance Sheet Chiller
Date :- 05/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [5 empty] | 2.4 | 2.1 | 2.1 | 2.1 | 2.1 | 2.3 | 2.3 | 2.1 | 2.3 | 2.4 | 2.4 | 2.1 | 2.3 | 2.4 | 2.6 | 2.6 | 2.5 | 2.6 | 2.7 | 2.6 | 2.35
2 | Small temperature difference of evaporator | ºC | [5 empty] | 0.3 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.34
3 | Entering Chilled Water Temp. (tchwe) | ºC | [5 empty] | 14.4 | 15.1 | 14.1 | 13.9 | 14 | 14.3 | 14.4 | 14.5 | 14.3 | 14.2 | 14 | 13.8 | 13.4 | 12.8 | 13.2 | 14.1 | 14.5 | 14.8 | 15 | 15.1 | 14.195
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [5 empty] | 10 | 8.1 | 8 | 8 | 8.1 | 8 | 8.1 | 7.5 | 7.3 | 7.2 | 7.1 | 6.7 | 6.5 | 6.1 | 5.8 | 6.3 | 6.6 | 6.7 | 6.7 | 6.7 | 7.275
5 | Entering Condenser Water Temp. (tcwe) | ºC | [5 empty] | 21.1 | 25.2 | 25.6 | 25.3 | 27.1 | 27.3 | 27.5 | 27.3 | 27.6 | 27.7 | 27.5 | 27.6 | 27.9 | 27.8 | 25.2 | 24.7 | 24.4 | 24.1 | 24.2 | 24 | 25.955
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [5 empty] | 26.8 | 29.6 | 29.5 | 29.1 | 30.7 | 31.3 | 31.6 | 31.9 | 32.1 | 32.1 | 32 | 32.2 | 32.3 | 32.2 | 29.8 | 29.5 | 29.3 | 29.2 | 29.4 | 29.1 | 30.485
7 | Chilled water inlet pressure | (Kg/Cm2) | [5 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4320
8 | Chilled water outlet pressure | (Kg/Cm2) | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [5 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [5 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [5 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [5 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [5 empty] | 1412.8307 | 2247.6852 | 1958.6971 | 1894.4775 | 1894.4775 | 2022.9167 | 2022.9167 | 2247.6852 | 2247.6852 | 2247.6852 | 2215.5754 | 2279.795 | 2215.5754 | 2151.3558 | 2376.1243 | 2504.5635 | 2536.6733 | 2600.8929 | 2665.1124 | 2697.2222 | 44439.9471
15 | Power Consumption of Chiller | KWH | [5 empty] | 1400 | 1500 | 1500 | 1500 | 1600 | 1600 | 1400 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 30000
16 | Specific power consumption of Chiller | (iKW/TR) | [5 empty] | 0.99092 | 0.66735 | 0.76582 | 0.79178 | 0.84456 | 0.79094 | 0.69207 | 0.66735 | 0.66735 | 0.66735 | 0.67703 | 0.65795 | 0.67703 | 0.69723 | 0.63128 | 0.59891 | 0.59133 | 0.57673 | 0.56283 | 0.55613 | 0.6886
17 | Average iKW/TR |  |  | Hours 7: 0.6886 | 0.6886
18 | COP of chiller | [6 empty] | 3.5482 | 5.2686 | 4.5912 | 4.4407 | 4.1631 | 4.4454 | 5.0804 | 5.2686 | 5.2686 | 5.2686 | 5.1933 | 5.3438 | 5.1933 | 5.0428 | 5.5696 | 5.8707 | 5.946 | 6.0965 | 6.247 | 6.3223 | 5.2084
19 | EER of Chiller | [6 empty] | 12.1101 | 17.9816 | 15.6697 | 15.156 | 14.2087 | 15.172 | 17.3394 | 17.9816 | 17.9816 | 17.9816 | 17.7248 | 18.2385 | 17.7248 | 17.211 | 19.0092 | 20.0367 | 20.2936 | 20.8073 | 21.3211 | 21.578 | 17.7764
20 | LMTD of Condenser | ºC | [5 empty] | 4.686 | 3.8943 | 3.7149 | 3.6786 | 3.6053 | 3.9697 | 4.0063 | 3.9649 | 4.1512 | 4.2249 | 4.2612 | 3.9649 | 4.1152 | 4.2249 | 4.5161 | 4.589 | 4.5153 | 4.6974 | 4.8435 | 4.6974 | 4.216
21 | LMTD of Evaporator | ºC | [5 empty] | 1.5991 | 1.9534 | 1.7681 | 1.9481 | 2.1401 | 2.2353 | 2.0381 | 2.1931 | 2.1931 | 2.1931 | 2.3759 | 2.215 | 2.3759 | 2.3293 | 2.4912 | 2.5824 | 2.6051 | 2.4308 | 2.6951 | 2.7175 | 2.254

## 06-02-2019 (hidden)
Performance Sheet Chiller
Date :- 06/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.7 | 2.6 | 2.4 | 2.1 | 1.9 | 1.7 | 1.9 | 1.8 | 1.8 | 1.9 | 1.9 | 2.1 | 1.9 | 1.9 | 2 | [9 empty] | 2.04
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | [9 empty] | 0.34
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.0845 | 15.3932 | 15.5446 | 14.4497 | 13.9903 | 13.9903 | 14.1398 | 14.2934 | 14.4422 | 14.4422 | 14.4422 | 14.29 | 13.6903 | 13.3921 | 13.0912 | [9 empty] | 14.3117
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 9.8 | 9.8 | 9.7697 | 9.3069 | 9.3069 | 9.3069 | 9.3069 | 9.4558 | 9.4558 | 9.4558 | 9.4558 | 8.8296 | 8.6767 | 8.5248 | 7.7152 | [9 empty] | 9.2111
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.3666 | 23.3641 | 24.4118 | 25.3502 | 25.3468 | 25.9653 | 26.2753 | 26.4268 | 26.1085 | 25.0244 | 24.2474 | 24.2437 | 23.9296 | 23.6217 | 23.7714 | [9 empty] | 24.7636
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.7897 | 28.6301 | 29.317 | 29.8025 | 29.1853 | 29.8057 | 30.419 | 30.5743 | 30.4158 | 29.1735 | 28.569 | 29.0259 | 28.2603 | 27.8042 | 28.2803 | [9 empty] | 29.2035
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [9 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [9 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [9 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [9 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [9 empty] | 971
14 | TR Genrated by Chiller | TR |  | 1696.8386 | 1795.9647 | 1854.2796 | 1651.346 | 1503.8401 | 1503.8401 | 1551.8442 | 1553.337 | 1601.1324 | 1601.1324 | 1601.1324 | 1753.3116 | 1609.8519 | 1562.8858 | 1726.2033 | [9 empty] | 24566.9403
15 | Power Consumption of Chiller | KWH |  | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | 1273 | [9 empty] | 19095
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.75022 | 0.70881 | 0.68652 | 0.77089 | 0.8465 | 0.8465 | 0.82031 | 0.81953 | 0.79506 | 0.79506 | 0.79506 | 0.72605 | 0.79076 | 0.81452 | 0.73746 | [9 empty] | 0.78022
17 | Average iKW/TR |  |  | Hours 7: 0.78022 | 0.78022
18 | COP of chiller |  |  | 4.6866 | 4.9604 | 5.1215 | 4.561 | 4.1536 | 4.1536 | 4.2862 | 4.2903 | 4.4223 | 4.4223 | 4.4223 | 4.8426 | 4.4464 | 4.3167 | 4.7677 | [9 empty] | 4.5236
19 | EER of Chiller |  |  | 15.9955 | 16.9299 | 17.4796 | 15.5666 | 14.1762 | 14.1762 | 14.6287 | 14.6427 | 15.0933 | 15.0933 | 15.0933 | 16.5278 | 15.1755 | 14.7328 | 16.2723 | [9 empty] | 15.4389
20 | LMTD of Condenser | ºC |  | 4.9236 | 4.7568 | 4.4067 | 3.9128 | 3.4727 | 3.2506 | 3.5809 | 3.4702 | 3.5257 | 3.5828 | 3.6433 | 4.0288 | 3.6465 | 3.5946 | 3.821 | [9 empty] | 3.8411
21 | LMTD of Evaporator | ºC |  | 1.9911 | 2.0663 | 2.1101 | 1.7744 | 1.6666 | 1.6666 | 1.8796 | 1.703 | 1.738 | 1.738 | 1.9177 | 2.034 | 1.7443 | 1.71 | 1.8284 | [9 empty] | 1.8379
Performance Sheet Chiller
Date :- 06/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 2.3 | 1.9 | 2.1 | 1.7 | 2 | 2.1 | 2.1 | 1.7 | 1.7 | 1.8 | 1.8 | 1.7 | 1.8 | 1.7 | 1.9 | 2 | 2.1 | 2.1 | 2 | 2 | 2.1 | 2.1 | 1.9409
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.32273
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 15.5446 | 14.4497 | 13.9903 | 13.9903 | 14.1398 | 14.2934 | 14.4422 | 14.4422 | 14.4422 | 14.29 | 13.6903 | 13.3921 | 13.0912 | 12.4809 | 13.101 | 13.5529 | 13.8571 | 14.0096 | 14.0096 | 14.0096 | 14.0096 | 14.0096 | 13.9654
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 9.7697 | 9.3069 | 9.3069 | 9.3069 | 9.3069 | 9.4558 | 9.4558 | 9.4558 | 9.4558 | 8.8296 | 8.6767 | 8.5248 | 7.7152 | 8.9153 | 9.2206 | 9.5321 | 9.6843 | 9.8339 | 9.8339 | 9.8339 | 9.8339 | 9.8339 | 9.3222
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 24.4118 | 25.3502 | 25.3468 | 25.9653 | 26.2753 | 26.4268 | 26.1085 | 25.0244 | 24.2474 | 24.2437 | 23.9296 | 23.6217 | 23.7714 | 22.6867 | 21.2457 | 21.8578 | 22.0094 | 22.3171 | 22.3171 | 22.3171 | 22.3171 | 22.4754 | 23.8303
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 29.317 | 29.8025 | 29.1853 | 29.8057 | 30.419 | 30.5743 | 30.4158 | 29.1735 | 28.569 | 29.0259 | 28.2603 | 27.8042 | 28.2803 | 27.927 | 25.81 | 26.7365 | 27.1917 | 27.6682 | 27.5162 | 27.5162 | 27.6663 | 27.8257 | 28.4769
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 1854.2796 | 1651.346 | 1503.8401 | 1503.8401 | 1551.8442 | 1553.337 | 1601.1324 | 1601.1324 | 1601.1324 | 1753.3116 | 1609.8519 | 1562.8858 | 1726.2033 | 1144.8915 | 1245.9879 | 1291.0739 | 1339.8933 | 1340.786 | 1340.786 | 1340.786 | 1340.786 | 1340.786 | 32799.9134
15 | Power Consumption of Chiller | KWH |  |  |  | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 1390.91 | 30600.02
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.75011 | 0.84229 | 0.92491 | 0.92491 | 0.89629 | 0.89543 | 0.8687 | 0.8687 | 0.8687 | 0.7933 | 0.864 | 0.88996 | 0.80576 | 1.2149 | 1.1163 | 1.0773 | 1.0381 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 1.0374 | 0.94666
17 | Average iKW/TR |  |  | Hours 7: 0.94666 | 0.94666
18 | COP of chiller |  |  |  |  | 4.6873 | 4.1743 | 3.8015 | 3.8015 | 3.9228 | 3.9266 | 4.0474 | 4.0474 | 4.0474 | 4.4321 | 4.0695 | 3.9507 | 4.3636 | 2.8941 | 3.1497 | 3.2636 | 3.387 | 3.3893 | 3.3893 | 3.3893 | 3.3893 | 3.3893 | 3.7688
19 | EER of Chiller |  |  |  |  | 15.9978 | 14.247 | 12.9744 | 12.9744 | 13.3886 | 13.4015 | 13.8138 | 13.8138 | 13.8138 | 15.1267 | 13.889 | 13.4838 | 14.8929 | 9.8776 | 10.7498 | 11.1388 | 11.56 | 11.5677 | 11.5677 | 11.5677 | 11.5677 | 11.5677 | 12.8628
20 | LMTD of Condenser | ºC |  |  |  | 4.2957 | 3.6888 | 3.6926 | 3.2506 | 3.6922 | 3.8042 | 3.8613 | 3.3578 | 3.417 | 3.6883 | 3.5337 | 3.3693 | 3.5951 | 3.7252 | 3.7277 | 3.9495 | 4.1675 | 4.2253 | 4.0592 | 4.0592 | 4.2247 | 4.2251 | 3.8005
21 | LMTD of Evaporator | ºC |  |  |  | 1.9197 | 1.7744 | 1.6666 | 1.6666 | 1.2397 | 1.703 | 1.738 | 1.738 | 1.738 | 2.034 | 1.7443 | 1.71 | 1.6154 | 1.3949 | 1.473 | 1.6735 | 1.7127 | 1.7134 | 1.7134 | 1.7134 | 1.7134 | 1.7134 | 1.6868

## 07-02-2019 (hidden)
Performance Sheet Chiller
Date :- 07/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2 | 1.9 | 2 | 2.1 | 2.1 | 2 | 2 | 1.9 | 1.8 | 1.8 | 1.9 | 1.9 | 1.9 | 1.9 | 1.8 | 1.8 | 1.8 | 1.9 | 1.9 | 1.8 | 1.9 | 1.9 | 1.8 | 1.7 | 1.8958
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.42083
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.0096 | 14.0096 | 14.4628 | 14.6113 | 14.7594 | 14.4486 | 14.1418 | 13.8336 | 13.6815 | 13.9903 | 14.6091 | 15.2223 | 15.6821 | 15.6821 | 15.8307 | 15.8307 | 15.6725 | 15.367 | 15.0684 | 14.7655 | 14.461 | 14.1534 | 13.8532 | 13.7025 | 14.6604
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 9.8339 | 9.8339 | 10.1385 | 10.2873 | 10.4362 | 10.2847 | 9.9761 | 9.8238 | 9.6747 | 9.8301 | 10.2955 | 10.7454 | 11.0441 | 11.202 | 11.3548 | 11.3548 | 11.1985 | 10.8923 | 10.5867 | 10.2827 | 10.1338 | 9.8331 | 9.6817 | 9.6817 | 10.3503
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.1739 | 22.0247 | 21.8671 | 21.717 | 21.2523 | 21.4098 | 21.4098 | 21.4098 | 21.5584 | 21.4015 | 21.4015 | 21.5516 | 21.2414 | 21.084 | 21.2332 | 21.22 | 20.6094 | 20.4729 | 19.857 | 19.2453 | 19.3954 | 18.618 | 19.2416 | 19.3903 | 20.8661
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.5169 | 27.2163 | 27.2163 | 27.3654 | 26.9031 | 26.901 | 26.901 | 26.5887 | 26.733 | 26.4206 | 26.8772 | 27.0284 | 27.0102 | 26.855 | 27.0075 | 27.1566 | 26.5444 | 26.3836 | 25.766 | 25.0099 | 24.8713 | 24.0804 | 24.3892 | 24.3892 | 26.3805
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2704.795 | 2747.326 | 2766.03 | 2887.04 | 2820.556 | 2737.653 | 2729.095 | 2614.262 | 2639.521 | 2768.235 | 2842.169 | 3028.007 | 3096.169 | 2988.283 | 2957.869 | 2947.825 | 2971.645 | 2943.651 | 2981.607 | 2949.21 | 2801.469 | 2811.995 | 2707.899 | 2631.616 | 68073.927
15 | Power Consumption of Chiller | KWH |  | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.167 | 1479.159 | 35500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.54687 | 0.5384 | 0.53476 | 0.51235 | 0.52442 | 0.5403 | 0.542 | 0.56581 | 0.56039 | 0.53434 | 0.52044 | 0.4885 | 0.47774 | 0.49499 | 0.50008 | 0.50178 | 0.49776 | 0.50249 | 0.4961 | 0.50155 | 0.528 | 0.52602 | 0.54624 | 0.56207 | 0.52264
17 | Average iKW/TR |  |  | Hours 7: 0.52264 | 0.52264
18 | COP of chiller |  |  | 6.4293 | 6.5304 | 6.5749 | 6.8625 | 6.7045 | 6.5074 | 6.4871 | 6.2141 | 6.2742 | 6.5801 | 6.7559 | 7.1976 | 7.3596 | 7.1032 | 7.0309 | 7.007 | 7.0636 | 6.9971 | 7.0873 | 7.0103 | 6.6591 | 6.6842 | 6.4367 | 6.2554 | 6.7422
19 | EER of Chiller |  |  | 21.9433 | 22.2884 | 22.4401 | 23.4218 | 22.8825 | 22.2099 | 22.1405 | 21.2088 | 21.4138 | 22.458 | 23.0578 | 24.5655 | 25.1184 | 24.2432 | 23.9964 | 23.915 | 24.1082 | 23.8811 | 24.189 | 23.9262 | 22.7276 | 22.813 | 21.9685 | 21.3498 | 23.0111
20 | LMTD of Condenser | ºC |  | 4.1081 | 3.9418 | 4.1102 | 4.3265 | 4.3273 | 4.1582 | 4.1582 | 3.9375 | 3.8203 | 3.7683 | 4.0371 | 4.0375 | 4.1344 | 4.1352 | 4.0184 | 4.0712 | 4.0707 | 4.1812 | 4.1806 | 4.0152 | 4.0372 | 4.0327 | 3.8113 | 3.6453 | 4.0444
21 | LMTD of Evaporator | ºC |  | 1.7134 | 1.7134 | 1.7514 | 1.9076 | 1.9074 | 1.7104 | 1.7108 | 1.6707 | 1.6699 | 1.8637 | 1.9048 | 1.9482 | 1.8308 | 1.791 | 1.7899 | 1.9479 | 1.7895 | 1.7896 | 1.7914 | 1.9498 | 1.7522 | 1.7504 | 1.544 | 1.5074 | 1.7794

## 08-02-2019 (hidden)
Performance Sheet Chiller
Date :- 08/02/2019
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [6 empty] | 1.1 | [18 empty] | 1.1
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.2 | [18 empty] | 0.2
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 13.6 | [18 empty] | 13.6
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 5.5 | [18 empty] | 5.5
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 19.3 | [18 empty] | 19.3
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 24.6 | [18 empty] | 24.6
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | [18 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | [18 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | [18 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | [18 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | [18 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | [18 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | [18 empty] | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 1300 | [18 empty] | 1300
15 | Power Consumption of Chiller | KWH | [6 empty] | 700 | [18 empty] | 700
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.53846 | [18 empty] | 0.53846
17 | Average iKW/TR |  |  | 0.53846 | [23 empty] | 0.53846
18 | COP of chiller | [7 empty] | 6.5297 | [18 empty] | 6.5297
19 | EER of Chiller | [7 empty] | 22.2859 | [18 empty] | 22.2859
20 | LMTD of Condenser | ºC | [6 empty] | 3.0097 | [18 empty] | 3.0097
21 | LMTD of Evaporator | ºC | [6 empty] | 2.1741 | [18 empty] | 2.1741
Performance Sheet Chiller
Date :- 08/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.7 | 1.7 | 1.8 | 2 | 1.1 | 1.7 | 1.7 | 1 | 1.8 | 1.8 | 1.9 | 1.9 | 1.8 | 1.8 | 1.9 | 1.8 | 1.9 | 1.9 | 1.8 | 1.8 | 1.8 | 1.8 | 1.7 | 1.7458
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.3 | 0.4 | 0.3 | 0.4 | 0.2 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.3 | 0.3 | 0.4
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.5 | 13.4 | 13.6 | 13.5 | 13.5 | 13.6 | 13.8 | 13.3 | 13.9 | 14.2 | 14.5 | 14.3 | 14.3 | 14.4 | 14.2 | 13.8 | 13.6 | 13.5 | 13 | 12.6 | 12.5 | 12.3 | 12.1 | 11.8 | 13.4667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.4 | 5.3 | 5.5 | 5.5 | 5.6 | 5.5 | 6.9 | 5.6 | 5.6 | 5.5 | 5.5 | 5.5 | 5.6 | 5.4 | 5.6 | 5.4 | 5.4 | 5.5 | 5.5 | 5.5 | 5.6 | 5.5 | 5.5 | 5.4 | 5.5542
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 19.7 | 20.2 | 19 | 19 | 18.6 | 19.3 | 20 | 19.6 | 20 | 19.6 | 19.2 | 18.5 | 18.5 | 18.5 | 18.4 | 18.4 | 17 | 16.1 | 16.4 | 15.1 | 14.8 | 14.7 | 15 | 14.7 | 17.9292
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 25.1 | 25.6 | 24.3 | 24 | 23.9 | 24.6 | 24.7 | 24.6 | 25.6 | 25.3 | 24.8 | 24.3 | 24.3 | 24.4 | 23.9 | 24 | 22.3 | 21.2 | 21.2 | 19.8 | 19.1 | 19.1 | 19.4 | 18.9 | 23.1
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2615.985 | 2681.725 | 2717.21 | 2567.604 | 2674.935 | 4643.944 | 2389.636 | 2787.846 | 2843.38 | 2809.673 | 2892.838 | 2930.524 | 2926.163 | 2923.301 | 2820.71 | 2678.736 | 2671.518 | 2513.723 | 2284.683 | 2320.102 | 2206.934 | 2164.419 | 2220.954 | 2085.003 | 64371.546
15 | Power Consumption of Chiller | KWH |  | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.83 | 1220.91 | 29300 | `
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.46668 | 0.45524 | 0.4493 | 0.47547 | 0.4564 | 0.26289 | 0.51089 | 0.43791 | 0.42936 | 0.43451 | 0.42202 | 0.41659 | 0.41721 | 0.41762 | 0.43281 | 0.45575 | 0.45698 | 0.48567 | 0.53435 | 0.5262 | 0.55318 | 0.56405 | 0.54969 | 0.58557 | 0.46651
17 | Average iKW/TR |  |  | 0.46651 | [23 empty] | 0.46651
18 | COP of chiller |  |  | 7.5341 | 7.7234 | 7.8256 | 7.3947 | 7.7038 | 13.3746 | 6.8822 | 8.029 | 8.189 | 8.0919 | 8.3314 | 8.4399 | 8.4274 | 8.4191 | 8.1237 | 7.7148 | 7.694 | 7.2395 | 6.5799 | 6.6819 | 6.356 | 6.2335 | 6.3964 | 6.0044 | 7.7246
19 | EER of Chiller |  |  | 25.7137 | 26.3599 | 26.7087 | 25.2382 | 26.2932 | 45.6475 | 23.4888 | 27.403 | 27.9489 | 27.6176 | 28.4351 | 28.8055 | 28.7626 | 28.7345 | 27.7261 | 26.3305 | 26.2596 | 24.7086 | 22.4572 | 22.8054 | 21.693 | 21.2751 | 21.8308 | 20.4931 | 26.364
20 | LMTD of Condenser | ºC |  | 3.8953 | 3.7776 | 3.7448 | 3.7618 | 4.0935 | 3.0097 | 3.5454 | 3.6457 | 2.9676 | 3.9941 | 3.9613 | 4.1447 | 4.1447 | 4.0594 | 3.9283 | 4.0785 | 3.8621 | 3.9109 | 3.8088 | 3.6604 | 3.5231 | 3.5577 | 3.5577 | 3.3753 | 3.7503
21 | LMTD of Evaporator | ºC |  | 2.6502 | 2.4308 | 2.6502 | 2.4095 | 2.6051 | 2.1741 | 2.1711 | 2.5597 | 2.6951 | 2.7844 | 3.2461 | 3.1982 | 2.9873 | 3.0566 | 2.7622 | 2.9175 | 2.8707 | 2.6277 | 2.5141 | 2.4222 | 2.1711 | 2.3526 | 2.1049 | 2.0605 | 2.6009

## 09-02-2019 (hidden)
Performance Sheet Chiller
Date :- 09/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.7 | 1.7 | 1.6 | 1.4 | 1.5 | 1.6 | 1.6 | 1.4 | 1.4 | 1.5 | 1.7 | 1.8 | 1.8 | 1.9 | 1.8 | 1.8 | 1.8 | 1.9 | 1.9 | 1.8 | 1.7 | 1.8 | 1.8 | 1.8 | 1.6958
2 | Small temperature difference of evaporator | ºC |  | 0.2 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.29167
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 11.9 | 11.7 | 11.8 | 11.8 | 12.1 | 12.2 | 11.7 | 11.5 | 11.3 | 11.3 | 11.5 | 12.3 | 13.3 | 13.8 | 13.8 | 14 | 13.5 | 13.5 | 13.3 | 13 | 12.8 | 12.8 | 12.5 | 12.4 | 12.4917
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.4 | 5.5 | 5.4 | 5.5 | 5.4 | 5.6 | 5.4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.6 | 5.6 | 5.6 | 5.5 | 5.5 | 5.5 | 5.4 | 5.5 | 5.5 | 5.4 | 5.5 | 5.6 | 5.5 | 5.4958
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 14.7 | 14.5 | 16 | 17.3 | 18 | 18.6 | 19.2 | 19.3 | 18.4 | 17.2 | 17.6 | 18.7 | 20 | 19.2 | 19.6 | 21.4 | 22.4 | 20.6 | 19 | 18.7 | 18.3 | 17.3 | 15.9 | 15.2 | 18.2125
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 18.8 | 18.3 | 20.2 | 21.6 | 22.3 | 22.9 | 23.1 | 23.3 | 22.2 | 21.2 | 21.4 | 23.2 | 24.8 | 24.6 | 25 | 27.1 | 27.8 | 25.7 | 24.2 | 23.6 | 23 | 22 | 20.3 | 19.7 | 22.7625
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2107.483 | 2075.459 | 2082.909 | 2171.181 | 2206.338 | 2062.525 | 2059.86 | 1948.581 | 1965.538 | 2002.774 | 2330.778 | 2548.849 | 2756.417 | 2730.439 | 2728.636 | 2660.282 | 2541.769 | 2585.251 | 2468.669 | 2344.403 | 2381.509 | 2408.323 | 2302.843 | 2319.441 | 55790.257
15 | Power Consumption of Chiller | KWH |  | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 1137.5 | 27300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53974 | 0.54807 | 0.54611 | 0.52391 | 0.51556 | 0.55151 | 0.55222 | 0.58376 | 0.57872 | 0.56796 | 0.48803 | 0.44628 | 0.41267 | 0.4166 | 0.41687 | 0.42759 | 0.44752 | 0.44 | 0.46077 | 0.4852 | 0.47764 | 0.47232 | 0.49395 | 0.49042 | 0.49514
17 | Average iKW/TR |  |  | Hours 7: 0.49514 | 0.49514
18 | COP of chiller |  |  | 6.5142 | 6.4152 | 6.4382 | 6.7111 | 6.8198 | 6.3752 | 6.367 | 6.023 | 6.0755 | 6.1906 | 7.2044 | 7.8785 | 8.5201 | 8.4398 | 8.4342 | 8.2229 | 7.8566 | 7.991 | 7.6306 | 7.2465 | 7.3612 | 7.4441 | 7.1181 | 7.1694 | 7.1853
19 | EER of Chiller |  |  | 22.233 | 21.8951 | 21.9737 | 22.905 | 23.2759 | 21.7587 | 21.7306 | 20.5566 | 20.7355 | 21.1284 | 24.5886 | 26.8892 | 29.0789 | 28.8049 | 28.7859 | 28.0648 | 26.8145 | 27.2732 | 26.0433 | 24.7324 | 25.1238 | 25.4067 | 24.2939 | 24.469 | 24.5234
20 | LMTD of Condenser | ºC |  | 3.3409 | 3.2365 | 3.2612 | 3.0627 | 3.1795 | 3.2951 | 3.1585 | 2.9631 | 2.8959 | 3.0786 | 3.2365 | 3.5921 | 3.6943 | 4.0118 | 3.8953 | 3.9941 | 3.8953 | 3.9109 | 3.9447 | 3.7282 | 3.5454 | 3.6604 | 3.5577 | 3.5921 | 3.4888
21 | LMTD of Evaporator | ºC |  | 1.851 | 2.0158 | 1.8304 | 1.8097 | 1.8921 | 2.1049 | 1.8097 | 1.7472 | 1.7053 | 1.9255 | 1.9708 | 2.1271 | 2.3451 | 2.6727 | 2.4734 | 2.5157 | 2.4095 | 2.6502 | 2.5824 | 2.302 | 2.2803 | 2.4683 | 2.3759 | 2.1711 | 2.1682
6.9

## 10-02-2019 (hidden)
Performance Sheet Chiller
Date :- 10/02/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.1 | 2.1 | 1.9 | 1.9 | 1.9 | 2 | 2.2 | 2.1 | 2.1 | 2.2 | 2.4 | 2.4 | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.1625
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.3 | 0.3 | 0.4 | 0.3 | 0.4 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.5 | 0.5 | 0.6 | 0.5 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 12.3 | 12.3 | 12.5 | 12.3 | 12.5 | 12.7 | 13.1 | 13.7 | 13.8 | 14.2 | 14.5 | 14.5 | 14.8 | 14.9 | 14.9 | 14.8 | 14.7 | 14.2 | 14 | 13.7 | 13.6 | 13.4 | 13.2 | 13.1 | 13.6542
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.5 | 5.6 | 5.5 | 5.6 | 5.6 | 5.5 | 5.5 | 5.5 | 5.6 | 5.5 | 5.6 | 5.8 | 6 | 5.8 | 5.7 | 5.6 | 5.5 | 5.5 | 5.4 | 5.5 | 5.4 | 5.5 | 5.6 | 5.575
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 15.8 | 15.8 | 16.6 | 17.2 | 18.3 | 18.6 | 19.3 | 19.4 | 19.2 | 20 | 20.3 | 19.9 | 20.6 | 20.9 | 20.2 | 20 | 19.3 | 18.9 | 19 | 19 | 18.7 | 18.5 | 19.1 | 18.5 | 18.8792
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 20.2 | 20.1 | 21 | 21.7 | 22.6 | 23.5 | 24.3 | 24.7 | 25 | 25.6 | 26.1 | 25.8 | 26.7 | 26.8 | 26.2 | 26.2 | 25.4 | 24.8 | 24.6 | 24.6 | 24.1 | 23.6 | 24 | 23.2 | 24.2
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2222.955 | 2168.9 | 2156.846 | 2244.776 | 2407.8 | 2546.323 | 2544.859 | 2681.12 | 2781.535 | 2906.901 | 2857.5 | 2906.838 | 2917.198 | 2924.279 | 2875.941 | 2871.351 | 2736.406 | 2828.295 | 2709.823 | 2651.108 | 2616.402 | 2410.532 | 2525.452 | 2516.42 | 63009.56
15 | Power Consumption of Chiller | KWH |  | 1190 | 1190 | 1180 | 1250 | 1250 | 1300 | 1370 | 1370 | 1400 | 1500 | 1380 | 1380 | 1400 | 1370 | 1370 | 1500 | 1300 | 1350 | 1350 | 1350 | 1250 | 1300 | 1300 | 1300 | 31900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53532 | 0.54867 | 0.5471 | 0.55685 | 0.51915 | 0.51054 | 0.53834 | 0.51098 | 0.50332 | 0.51601 | 0.48294 | 0.47474 | 0.47991 | 0.46849 | 0.47637 | 0.5224 | 0.47508 | 0.47732 | 0.49819 | 0.50922 | 0.47776 | 0.5393 | 0.51476 | 0.51661 | 0.50831
17 | Average iKW/TR |  |  | Hours 7: 0.50831 | 0.50831
18 | COP of chiller |  |  | 6.568 | 6.4083 | 6.4267 | 6.3141 | 6.7727 | 6.8868 | 6.5312 | 6.8809 | 6.9856 | 6.8138 | 7.2804 | 7.4061 | 7.3263 | 7.5049 | 7.3809 | 6.7304 | 7.4009 | 7.3661 | 7.0576 | 6.9047 | 7.3594 | 6.5196 | 6.8304 | 6.8059 | 6.9359
19 | EER of Chiller |  |  | 22.4166 | 21.8715 | 21.9342 | 21.55 | 23.1151 | 23.5047 | 22.2909 | 23.4845 | 23.8419 | 23.2554 | 24.848 | 25.2771 | 25.0048 | 25.6144 | 25.191 | 22.971 | 25.2594 | 25.1406 | 24.0875 | 23.5656 | 25.1177 | 22.2513 | 23.3121 | 23.2287 | 23.6722
20 | LMTD of Condenser | ºC |  | 3.8943 | 3.8587 | 3.6707 | 3.7054 | 3.6358 | 3.9568 | 4.2172 | 4.2079 | 4.3776 | 4.4245 | 4.7206 | 4.755 | 4.8237 | 4.5266 | 4.5604 | 4.6276 | 4.5941 | 4.5266 | 4.4245 | 4.4245 | 4.3559 | 4.2521 | 4.1822 | 4.1118 | 4.2848
21 | LMTD of Evaporator | ºC |  | 2.3526 | 2.1491 | 2.1711 | 2.3526 | 2.1711 | 2.4222 | 2.3236 | 2.6727 | 2.6951 | 2.9641 | 3.0566 | 3.2222 | 3.2461 | 3.0335 | 3.0796 | 3.2699 | 3.0796 | 2.7844 | 2.7399 | 2.6951 | 2.8472 | 2.8236 | 2.5597 | 2.5141 | 2.7177

## 11-02-2019 (hidden)
Performance Sheet Chiller
Date :- 11/2/2019
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 16: 0.3; Hours 17: 0.4; Hours 18: 0.4; Hours 19: 0.4; Hours 20: 0.4; Hours 21: 0.4; Hours 22: 0.4; Hours 23: 0.3 | 0.375
2 | Small temperature difference of evaporator | ºC |  | Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 16: 15.6667; Hours 17: 15.3889; Hours 18: 14.5; Hours 19: 14.0556; Hours 20: 13.7222; Hours 21: 13.6111; Hours 22: 13.3889; Hours 23: 13.1667 | 14.1875
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 16: 8.5; Hours 17: 8.1667; Hours 18: 7.8333; Hours 19: 7.8333; Hours 20: 7.9444; Hours 21: 7.9444; Hours 22: 8.0556; Hours 23: 7.1667 | 7.9306
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 16: 23.6667; Hours 17: 24.5556; Hours 18: 25.7222; Hours 19: 25.0556; Hours 20: 24.5; Hours 21: 23.9444; Hours 22: 23.5; Hours 23: 24.2778 | 24.4028
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 16: 28.9444; Hours 17: 29.5556; Hours 18: 30.5556; Hours 19: 29.4444; Hours 20: 28.6667; Hours 21: 28; Hours 22: 27.2222; Hours 23: 28.5556 | 28.8681
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 16: 2301.2026; Hours 17: 2319.0405; Hours 18: 2140.6527; Hours 19: 1997.9439; Hours 20: 1855.2316; Hours 21: 1819.5545; Hours 22: 1712.5226; Hours 23: 1926.5879 | 16072.7363
15 | Power Consumption of Chiller | KWH |  | Hours 16: 1225; Hours 17: 1225; Hours 18: 1225; Hours 19: 1225; Hours 20: 1225; Hours 21: 1225; Hours 22: 1225; Hours 23: 1225 | 9800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 16: 0.53233; Hours 17: 0.52824; Hours 18: 0.57226; Hours 19: 0.61313; Hours 20: 0.66029; Hours 21: 0.67324; Hours 22: 0.71532; Hours 23: 0.63584 | 0.61633
17 | Average iKW/TR |  |  | Hours 7: 0.61633 | 0.61633
18 | COP of chiller |  |  | Hours 16: 6.6049; Hours 17: 6.6561; Hours 18: 6.1441; Hours 19: 5.7345; Hours 20: 5.3249; Hours 21: 5.2225; Hours 22: 4.9153; Hours 23: 5.5297 | 5.7665
19 | EER of Chiller |  |  | Hours 16: 22.5426; Hours 17: 22.7173; Hours 18: 20.9698; Hours 19: 19.5719; Hours 20: 18.1739; Hours 21: 17.8244; Hours 22: 16.7759; Hours 23: 18.8729 | 19.6811
20 | LMTD of Condenser | ºC |  | Hours 16: 1.8057; Hours 17: 1.9211; Hours 18: 1.8797; Hours 19: 1.7679; Hours 20: 1.7111; Hours 21: 1.6825; Hours 22: 1.5957; Hours 23: 1.5697 | 1.7417
21 | LMTD of Evaporator | ºC |  | Hours 16: 2.6251; Hours 17: 2.6385; Hours 18: 2.5038; Hours 19: 2.3945; Hours 20: 2.2836; Hours 21: 2.2556; Hours 22: 2.1709; Hours 23: 2.3392 | 2.4014
Performance Sheet Chiller
Date :- 11/2/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 2.3 | 2.1 | 2.4 | 2.2 | 2.5 | 2.6 | 2.4 | 2.2 | 2.1 | 1.8 | 1.5 | 1.5 | 1.7 | 1.9 | 2.1 | 2 | 2.1 | 2.1 | 2.1 | 2 | 2.1 | 2.1 | 2.0818
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.35455
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 13.4 | 13 | 12.3 | 13.3 | 14.1 | 14.5 | 14.9 | 15.6 | 15.6 | 14.7 | 14.2 | 14 | 13.8 | 13.6 | 13.3 | 12.5 | 12.5 | 13.1 | 13.5 | 13.7 | 13.7 | 13.7 | 13.7727
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 6.5 | 5.4 | 5.5 | 5.4 | 5.8 | 6.2 | 6.6 | 7.3 | 8.1 | 7.8 | 8 | 7.8 | 8 | 8.1 | 7 | 5.8 | 5.5 | 5.6 | 5.6 | 5.7 | 5.8 | 5.7 | 6.5091
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 18.1 | 20.2 | 19.1 | 19.7 | 21 | 21.2 | 22.2 | 22.9 | 24.5 | 25.8 | 25.1 | 24.6 | 24 | 23.6 | 24.3 | 24.5 | 21.3 | 21.4 | 21.2 | 21.2 | 21.1 | 21 | 22.1818
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 21.1 | 24.8 | 23.3 | 24.6 | 26.1 | 26.5 | 27.3 | 28 | 29.2 | 30.1 | 29.1 | 28.5 | 27.7 | 27 | 28.4 | 28.6 | 25.6 | 26.1 | 26.1 | 26.1 | 26.1 | 26 | 26.65
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2215.5754 | 2440.3439 | 2183.4656 | 2536.6733 | 2665.1124 | 2665.1124 | 2665.1124 | 2665.1124 | 2408.2341 | 2215.5754 | 1990.8069 | 1990.8069 | 1862.3677 | 1766.0384 | 2022.9167 | 2151.3558 | 2247.6852 | 2408.2341 | 2536.6733 | 2568.7831 | 2536.6733 | 2568.7831 | 51311.4418
15 | Power Consumption of Chiller | KWH |  |  |  | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 1450 | 31900
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.65446 | 0.59418 | 0.66408 | 0.57161 | 0.54407 | 0.54407 | 0.54407 | 0.54407 | 0.6021 | 0.65446 | 0.72835 | 0.72835 | 0.77858 | 0.82105 | 0.71679 | 0.67399 | 0.64511 | 0.6021 | 0.57161 | 0.56447 | 0.57161 | 0.56447 | 0.63107
17 | Average iKW/TR |  |  | Hours 7: 0.63107 | 0.63107
18 | COP of chiller |  |  |  |  | 5.3724 | 5.9174 | 5.2945 | 6.151 | 6.4624 | 6.4624 | 6.4624 | 6.4624 | 5.8396 | 5.3724 | 4.8274 | 4.8274 | 4.5159 | 4.2823 | 4.9052 | 5.2167 | 5.4502 | 5.8396 | 6.151 | 6.2289 | 6.151 | 6.2289 | 5.6555
19 | EER of Chiller |  |  |  |  | 18.336 | 20.1961 | 18.0702 | 20.9933 | 22.0563 | 22.0563 | 22.0563 | 22.0563 | 19.9304 | 18.336 | 16.4758 | 16.4758 | 15.4128 | 14.6156 | 16.7415 | 17.8045 | 18.6017 | 19.9304 | 20.9933 | 21.2591 | 20.9933 | 21.2591 | 19.3023
20 | LMTD of Condenser | ºC |  |  |  | 3.5937 | 3.9649 | 4.1518 | 4.1822 | 4.5869 | 4.769 | 4.4759 | 4.2521 | 4.0001 | 3.5231 | 3.0786 | 3.0447 | 3.2013 | 3.3143 | 3.7871 | 3.6767 | 3.8587 | 4.0001 | 4.0699 | 3.9568 | 4.1046 | 4.1046 | 3.8953
21 | LMTD of Evaporator | ºC |  |  |  | 2.1711 | 2.3236 | 2.1491 | 2.3881 | 2.6951 | 2.6951 | 2.6951 | 2.4734 | 2.5141 | 2.3759 | 2.2116 | 1.7889 | 1.9255 | 2.0437 | 2.2353 | 2.1271 | 2.3991 | 2.5141 | 2.6051 | 2.6277 | 2.3881 | 2.6277 | 2.3625
Performance Sheet Chiller
Date :- 11/2/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 2.3; Hours 8: 2.2 | 2.25
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.3; Hours 8: 0.3 | 0.3
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 13; Hours 8: 13 | 13
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 5.6; Hours 8: 5.5 | 5.55
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 18.2; Hours 8: 18.1 | 18.15
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 23.1; Hours 8: 22.9 | 23
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 8: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2376.1243; Hours 8: 2408.2341 | 4784.3585
15 | Power Consumption of Chiller | KWH |  | Hours 7: 750; Hours 8: 750 | 1500
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.31564; Hours 8: 0.31143 | 0.31354
17 | Average iKW/TR |  |  | Hours 7: 0.31354 | 0.31354
18 | COP of chiller |  |  | Hours 7: 11.1393; Hours 8: 11.2898 | 11.2145
19 | EER of Chiller |  |  | Hours 7: 38.0183; Hours 8: 38.5321 | 38.2752
20 | LMTD of Condenser | ºC |  | Hours 7: 4.2938; Hours 8: 4.147 | 4.2204
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.2803; Hours 8: 2.302 | 2.2911

## 12-02-2019 (hidden)
Performance Sheet Chiller
Date :- 12/2/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 20: 2; Hours 21: 1.7; Hours 22: 1.7; Hours 23: 1.7; Hours 0: 1.6; Hours 1: 1.9; Hours 2: 2; Hours 3: 2; Hours 4: 2.1; Hours 5: 2; Hours 6: 2.1 | 1.8909
2 | Small temperature difference of evaporator | ºC |  | Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.7; Hours 23: 0.4; Hours 0: 0.8; Hours 1: 1.1; Hours 2: 1.1; Hours 3: 1.2; Hours 4: 1.3; Hours 5: 1.2; Hours 6: 1.4 | 0.98182
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 20: 16.2; Hours 21: 15.4; Hours 22: 14.1; Hours 23: 13.5; Hours 0: 12.7; Hours 1: 11.8; Hours 2: 12.9; Hours 3: 13.3; Hours 4: 13.5; Hours 5: 13.7; Hours 6: 13.8 | 13.7182
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 20: 8.5; Hours 21: 8.1; Hours 22: 7.8; Hours 23: 6.9; Hours 0: 6; Hours 1: 5.6; Hours 2: 5.6; Hours 3: 5.8; Hours 4: 5.8; Hours 5: 6.2; Hours 6: 6.3 | 6.6
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 20: 22; Hours 21: 24.8; Hours 22: 24.3; Hours 23: 24.5; Hours 0: 24.7; Hours 1: 22; Hours 2: 21.5; Hours 3: 21.6; Hours 4: 21.6; Hours 5: 22.1; Hours 6: 22.3 | 22.8545
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 20: 22.5; Hours 21: 30.3; Hours 22: 29.1; Hours 23: 29.4; Hours 0: 29.8; Hours 1: 26.8; Hours 2: 27; Hours 3: 27.4; Hours 4: 27.5; Hours 5: 27.9; Hours 6: 28.1 | 27.8
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3; Hours 0: 4.3; Hours 1: 4.3; Hours 2: 4.3; Hours 3: 4.3; Hours 4: 4.3; Hours 5: 4.3; Hours 6: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8; Hours 5: 3.8; Hours 6: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8; Hours 5: 3.8; Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3; Hours 3: 3; Hours 4: 3; Hours 5: 3; Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5; Hours 3: 0.5; Hours 4: 0.5; Hours 5: 0.5; Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8; Hours 3: 0.8; Hours 4: 0.8; Hours 5: 0.8; Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971; Hours 3: 971; Hours 4: 971; Hours 5: 971; Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 20: 2472.4537; Hours 21: 2344.0146; Hours 22: 2022.9167; Hours 23: 2119.246; Hours 0: 2151.3558; Hours 1: 1990.8069; Hours 2: 2344.0146; Hours 3: 2408.2341; Hours 4: 2472.4537; Hours 5: 2408.2341; Hours 6: 2408.2341 | 25141.9643
15 | Power Consumption of Chiller | KWH |  | Hours 20: 1680; Hours 21: 1600; Hours 22: 1600; Hours 23: 1650; Hours 0: 1630; Hours 1: 1650; Hours 2: 1640; Hours 3: 1640; Hours 4: 1630; Hours 5: 1650; Hours 6: 1630 | 18000
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 20: 0.67949; Hours 21: 0.68259; Hours 22: 0.79094; Hours 23: 0.77858; Hours 0: 0.75766; Hours 1: 0.82881; Hours 2: 0.69965; Hours 3: 0.681; Hours 4: 0.65926; Hours 5: 0.68515; Hours 6: 0.67684 | 0.72
17 | Average iKW/TR |  |  | Hours 7: 0.72 | 0.72
18 | COP of chiller |  |  | Hours 20: 5.1745; Hours 21: 5.151; Hours 22: 4.4454; Hours 23: 4.5159; Hours 0: 4.6406; Hours 1: 4.2422; Hours 2: 5.0253; Hours 3: 5.163; Hours 4: 5.3332; Hours 5: 5.1317; Hours 6: 5.1947 | 4.9107
19 | EER of Chiller |  |  | Hours 20: 17.6605; Hours 21: 17.5803; Hours 22: 15.172; Hours 23: 15.4128; Hours 0: 15.8383; Hours 1: 14.4787; Hours 2: 17.1515; Hours 3: 17.6214; Hours 4: 18.2023; Hours 5: 17.5146; Hours 6: 17.7295 | 16.7602
20 | LMTD of Condenser | ºC |  | Hours 20: 2.2407; Hours 21: 3.8103; Hours 22: 3.579; Hours 23: 3.6124; Hours 0: 3.5612; Hours 1: 3.8088; Hours 2: 4.1611; Hours 3: 4.2616; Hours 4: 4.4112; Hours 5: 4.2616; Hours 6: 4.3776 | 3.826
21 | LMTD of Evaporator | ºC |  | Hours 20: 3.2583; Hours 21: 3.1533; Hours 22: 2.7361; Hours 23: 2.3059; Hours 0: 2.9937; Hours 1: 3.276; Hours 2: 3.5909; Hours 3: 3.786; Hours 4: 3.9796; Hours 5: 3.786; Hours 6: 4.055 | 3.3564
Performance Sheet Chiller
Date :- 12/2/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 2.6; Hours 8: 2.6; Hours 9: 2.6; Hours 10: 2.5; Hours 11: 2.5; Hours 12: 2.5; Hours 13: 1.9; Hours 14: 1; Hours 19: 2.7; Hours 20: 2.3; Hours 21: 1.9; Hours 22: 2.1; Hours 23: 2.3 | 2.2692
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.4; Hours 8: 0.4; Hours 9: 0.3; Hours 10: 0.3; Hours 11: 0.3; Hours 12: 0.4; Hours 13: 0.3; Hours 14: 1.2; Hours 19: 0.4; Hours 20: 0.3; Hours 21: 0.3; Hours 22: 0.3; Hours 23: 0.4 | 0.40769
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 13.7; Hours 8: 13.6; Hours 9: 13.8; Hours 10: 14.2; Hours 11: 14.2; Hours 12: 14.3; Hours 13: 13.8; Hours 14: 13.7; Hours 19: 14.3; Hours 20: 16.2; Hours 21: 15.6; Hours 22: 14.1; Hours 23: 13.6 | 14.2385
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 5.7; Hours 8: 5.7; Hours 9: 5.8; Hours 10: 6.1; Hours 11: 6.2; Hours 12: 6.4; Hours 13: 6; Hours 14: 7.8; Hours 19: 7.9; Hours 20: 7.7; Hours 21: 8.1; Hours 22: 7.8; Hours 23: 7 | 6.7846
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 20.8; Hours 8: 20.3; Hours 9: 20.5; Hours 10: 20.6; Hours 11: 20.6; Hours 12: 21.2; Hours 13: 21.5; Hours 14: 23.6; Hours 19: 21.8; Hours 20: 21.6; Hours 21: 25; Hours 22: 24.6; Hours 23: 24.7 | 22.0615
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 25.9; Hours 8: 25.4; Hours 9: 25.5; Hours 10: 25.6; Hours 11: 25.5; Hours 12: 26.2; Hours 13: 26.5; Hours 14: 27.1; Hours 19: 22.3; Hours 20: 27.1; Hours 21: 29.8; Hours 22: 28.7; Hours 23: 29 | 26.5077
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 8: 4.3; Hours 9: 4.3; Hours 10: 4.3; Hours 11: 4.3; Hours 12: 4.3; Hours 13: 4.3; Hours 14: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2568.7831; Hours 8: 2536.6733; Hours 9: 2568.7831; Hours 10: 2600.8929; Hours 11: 2568.7831; Hours 12: 2536.6733; Hours 13: 2504.5635; Hours 14: 1894.4775; Hours 19: 2055.0265; Hours 20: 2729.332; Hours 21: 2408.2341; Hours 22: 2022.9167; Hours 23: 2119.246 | 31114.3849
15 | Power Consumption of Chiller | KWH |  | Hours 7: 1400; Hours 8: 1360; Hours 9: 1410; Hours 10: 1360; Hours 11: 1400; Hours 12: 1400; Hours 13: 1060; Hours 14: 1030; Hours 19: 1250; Hours 20: 1350; Hours 21: 1200; Hours 22: 1150; Hours 23: 1330 | 16700
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.54501; Hours 8: 0.53614; Hours 9: 0.5489; Hours 10: 0.5229; Hours 11: 0.54501; Hours 12: 0.5519; Hours 13: 0.42323; Hours 14: 0.54369; Hours 19: 0.60826; Hours 20: 0.49463; Hours 21: 0.49829; Hours 22: 0.56849; Hours 23: 0.62758 | 0.53954
17 | Average iKW/TR |  |  | Hours 7: 0.53954 | 0.53954
18 | COP of chiller |  |  | Hours 7: 6.4513; Hours 8: 6.558; Hours 9: 6.4056; Hours 10: 6.7241; Hours 11: 6.4513; Hours 12: 6.3707; Hours 13: 8.3076; Hours 14: 6.467; Hours 19: 5.7804; Hours 20: 7.1084; Hours 21: 7.0561; Hours 22: 6.1848; Hours 23: 5.6025 | 6.5744
19 | EER of Chiller |  |  | Hours 7: 22.0183; Hours 8: 22.3826; Hours 9: 21.8622; Hours 10: 22.9493; Hours 11: 22.0183; Hours 12: 21.7431; Hours 13: 28.3538; Hours 14: 22.0718; Hours 19: 19.7284; Hours 20: 24.2609; Hours 21: 24.0826; Hours 22: 21.1089; Hours 23: 19.1212 | 22.4386
20 | LMTD of Condenser | ºC |  | Hours 7: 4.6974; Hours 8: 4.6974; Hours 9: 4.6614; Hours 10: 4.5512; Hours 11: 4.5153; Hours 12: 4.5512; Hours 13: 3.877; Hours 14: 2.327; Hours 19: 2.9429; Hours 20: 4.5037; Hours 21: 3.8088; Hours 22: 3.7871; Hours 23: 4.0791 | 4.0769
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.6277; Hours 8: 2.6051; Hours 9: 2.4095; Hours 10: 2.4308; Hours 11: 2.4095; Hours 12: 2.6051; Hours 13: 2.3666; Hours 14: 3.3188; Hours 19: 2.2589; Hours 20: 2.5157; Hours 21: 2.302; Hours 22: 2.0381; Hours 23: 2.3059 | 2.4764
Performance Sheet Chiller
Date :- 12/2/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 13: 0.8; Hours 14: 0.7; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8 | 0.78
2 | Small temperature difference of evaporator | ºC |  | Hours 13: 0.9; Hours 14: 0.3; Hours 15: 0.3; Hours 16: 0.3; Hours 17: 0.4 | 0.44
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 13: 23.5; Hours 14: 12.8; Hours 15: 11.8; Hours 16: 12.2; Hours 17: 13 | 14.66
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 13: 16; Hours 14: 5.4; Hours 15: 5.3; Hours 16: 5.8; Hours 17: 5.6 | 7.62
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 13: 25.2; Hours 14: 27.7; Hours 15: 28.6; Hours 16: 23.8; Hours 17: 22.5 | 25.56
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 13: 25.5; Hours 14: 32.8; Hours 15: 32.8; Hours 16: 28.3; Hours 17: 27.4 | 29.36
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 13: 4.3; Hours 14: 4.3; Hours 15: 4.3; Hours 16: 4.3; Hours 17: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 13: 2408.2341; Hours 14: 2376.1243; Hours 15: 2087.1362; Hours 16: 2055.0265; Hours 17: 2376.1243 | 11302.6455
15 | Power Consumption of Chiller | KWH |  | Hours 13: 1420; Hours 14: 1420; Hours 15: 1420; Hours 16: 1420; Hours 17: 1420 | 7100
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 13: 0.58964; Hours 14: 0.59761; Hours 15: 0.68036; Hours 16: 0.69099; Hours 17: 0.59761 | 0.63124
17 | Average iKW/TR |  |  | Hours 7: 0.63124 | 0.63124
18 | COP of chiller |  |  | Hours 13: 5.9629; Hours 14: 5.8834; Hours 15: 5.1679; Hours 16: 5.0884; Hours 17: 5.8834 | 5.5972
19 | EER of Chiller |  |  | Hours 13: 20.3515; Hours 14: 20.0801; Hours 15: 17.6379; Hours 16: 17.3666; Hours 17: 20.0801 | 19.1032
20 | LMTD of Condenser | ºC |  | Hours 13: 0.94205; Hours 14: 2.4119; Hours 15: 2.2918; Hours 16: 2.3799; Hours 17: 2.4954 | 2.1042
21 | LMTD of Evaporator | ºC |  | Hours 13: 3.3578; Hours 14: 2.2803; Hours 15: 2.0827; Hours 16: 2.0605; Hours 17: 2.4912 | 2.4545

## 13-02-2019 (hidden)
Performance Sheet Chiller
Date :- 13/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.1 | 2.2 | 2.3 | 2.1 | 2.2 | 1.8 | 1.7 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.4 | 1.7 | 1.7 | [9 empty] | 1.8133
2 | Small temperature difference of evaporator | ºC |  | 1.4 | 1.6 | 1.6 | 1.6 | 1.5 | 1.1 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | [9 empty] | 0.9
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.9 | 14 | 14.3 | 14.4 | 14.6 | 14.8 | 14.6 | 13.8 | 14.6 | 14.3 | 14.3 | 14.3 | 14.2 | 14 | 13.7 | [9 empty] | 14.2533
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.1 | 6.6 | 6.6 | 6.6 | 7.1 | 8 | 7.9 | 8.2 | 8.1 | 8 | 8 | 7.8 | 8 | 6.7 | [9 empty] | 7.3333
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.2 | 20.8 | 20.3 | 20.6 | 21.1 | 21.4 | 24.2 | 25.1 | 27.3 | 26.8 | 26.1 | 26 | 26 | 25.2 | 25.3 | [9 empty] | 23.8267
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.1 | 26.8 | 26.4 | 26.8 | 27.2 | 27.5 | 29.3 | 29.7 | 32.1 | 31.5 | 31 | 30.7 | 30.8 | 29.8 | 30.6 | [9 empty] | 29.1533
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [9 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [9 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [9 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [9 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [9 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2536.6733 | 2472.4537 | 2504.5635 | 2568.7831 | 2472.4537 | 2119.246 | 1894.4775 | 2055.0265 | 1990.8069 | 2022.9167 | 2022.9167 | 2055.0265 | 1926.5873 | 2247.6852 | [9 empty] | 33329.9603
15 | Power Consumption of Chiller | KWH |  | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | 1380 | [9 empty] | 20700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.56549 | 0.54402 | 0.55815 | 0.55099 | 0.53722 | 0.55815 | 0.65117 | 0.72843 | 0.67152 | 0.69319 | 0.68218 | 0.68218 | 0.67152 | 0.71629 | 0.61396 | [9 empty] | 0.6283
17 | Average iKW/TR |  |  | Hours 7: 0.6283 | 0.6283
18 | COP of chiller |  |  | 6.2176 | 6.463 | 6.2994 | 6.3812 | 6.5448 | 6.2994 | 5.3995 | 4.8268 | 5.2359 | 5.0722 | 5.154 | 5.154 | 5.2359 | 4.9086 | 5.7267 | [9 empty] | 5.6613
19 | EER of Chiller |  |  | 21.2206 | 22.0582 | 21.4998 | 21.779 | 22.3374 | 21.4998 | 18.4284 | 16.4739 | 17.87 | 17.3115 | 17.5907 | 17.5907 | 17.87 | 16.7531 | 19.5453 | [9 empty] | 19.3219
20 | LMTD of Condenser | ºC |  | 4.4112 | 4.5604 | 4.7093 | 4.5113 | 4.5941 | 4.1242 | 3.6789 | 3.396 | 3.4625 | 3.4293 | 3.4955 | 3.4293 | 3.2256 | 3.5117 | 3.7448 | [9 empty] | 3.8856
21 | LMTD of Evaporator | ºC |  | 4.0844 | 4.435 | 4.375 | 4.405 | 4.3341 | 3.7029 | 2.3059 | 2.1401 | 2.4384 | 2.5538 | 2.5795 | 2.5795 | 2.6051 | 2.5022 | 2.3991 | [9 empty] | 3.1627
Performance Sheet Chiller
Date :- 13/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [6 empty] | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.6 | 0.8 | 0.9 | 0.8 | 0.9 | 0.8 | 0.9 | 0.9 | 0.8 | 0.76842
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.8 | 0.7 | 0.7 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.4 | 0.4 | 0.4 | 0.2 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.42105
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 17.6 | 14.8 | 14.7 | 14.8 | 14.6 | 14.5 | 14.5 | 14.4 | 14.2 | 13.9 | 13.3 | 12.8 | 13.6 | 13.8 | 14.2 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3632
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 14.8 | 8.1 | 8.1 | 8 | 8 | 8 | 7.8 | 8 | 7.6 | 6.5 | 6 | 5.5 | 5.7 | 5.7 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 7.2
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 21.6 | 24.5 | 27.3 | 27.5 | 27 | 26.5 | 26.2 | 26.3 | 25.5 | 25.6 | 25.9 | 24.8 | 23.1 | 22.2 | 22 | 22.7 | 21.8 | 21.8 | 22.3 | 24.4526
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 21.2 | 28.9 | 31.6 | 32.1 | 31.4 | 30.8 | 30.6 | 30.6 | 29.7 | 30.7 | 31 | 29.8 | 28.2 | 27.7 | 27.7 | 28.3 | 27.6 | 27.5 | 28 | 29.1263
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 899.0741 | 2151.3558 | 2119.246 | 2183.4656 | 2119.246 | 2087.1362 | 2151.3558 | 2055.0265 | 2119.246 | 2376.1243 | 2344.0146 | 2344.0146 | 2536.6733 | 2600.8929 | 2697.2222 | 2729.332 | 2729.332 | 2729.332 | 2729.332 | 43701.422
15 | Power Consumption of Chiller | KWH | [6 empty] | 1208.7 | 669.7 | 1424.3 | 1378.1 | 1393.5 | 1393.5 | 1316.5 | 1316.5 | 1439.7 | 1485.9 | 1439.7 | 1578.3 | 1562.9 | 1470.5 | 1655.3 | 1609.1 | 1455.1 | 1470.5 | 1532.2 | 26800
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 1.3444 | 0.31129 | 0.67208 | 0.63115 | 0.65755 | 0.66766 | 0.61194 | 0.64062 | 0.67935 | 0.62535 | 0.6142 | 0.67333 | 0.61612 | 0.56538 | 0.61371 | 0.58956 | 0.53313 | 0.53878 | 0.56138 | 0.63931
17 | Average iKW/TR |  |  | Hours 7: 0.63931 | 0.63931
18 | COP of chiller | [7 empty] | 2.6153 | 11.2949 | 5.2315 | 5.5708 | 5.3472 | 5.2661 | 5.7457 | 5.4884 | 5.1756 | 5.6225 | 5.7245 | 5.2218 | 5.7067 | 6.2188 | 5.7291 | 5.9638 | 6.595 | 6.5259 | 6.2631 | 5.8582
19 | EER of Chiller | [7 empty] | 8.9261 | 38.5494 | 17.8552 | 19.013 | 18.2499 | 17.9733 | 19.61 | 18.7319 | 17.6642 | 19.1895 | 19.5377 | 17.822 | 19.4768 | 21.2248 | 19.5535 | 20.3544 | 22.5086 | 22.2729 | 21.376 | 19.9942
20 | LMTD of Condenser | ºC | [6 empty] | 0.57708 | 2.2156 | 2.1871 | 2.2723 | 2.2156 | 2.1871 | 2.2156 | 2.1871 | 2.2918 | 2.4119 | 2.2654 | 2.524 | 2.6883 | 2.6651 | 2.8608 | 2.693 | 2.8892 | 2.8608 | 2.7208 | 2.3647
21 | LMTD of Evaporator | ºC | [6 empty] | 1.8616 | 2.8412 | 2.815 | 2.5363 | 2.1049 | 2.0827 | 2.1271 | 1.8304 | 2.1049 | 2.4912 | 2.4683 | 2.4683 | 2.1344 | 2.6502 | 2.7175 | 2.9408 | 2.7399 | 2.7399 | 2.7399 | 2.4418

## 14-02-2019 (hidden)
Chiller Operation
Performance Sheet Chiller
Date :- 14/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [11 empty] | 2.4 | 2.1 | 2.1 | 2.1 | 2.2 | 2.1 | 2 | 2.1 | 2.1 | 2.2 | 2.1 | 2.2 | 2.1 | 2.2 | 2.1429
2 | Small temperature difference of evaporator | ºC | [11 empty] | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.33571
3 | Entering Chilled Water Temp. (tchwe) | ºC | [11 empty] | 15.5 | 15.6 | 14.8 | 14.6 | 14.3 | 13.7 | 13.1 | 12.2 | 12.5 | 13.3 | 13.8 | 14.2 | 14.5 | 14.6 | 14.05
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [11 empty] | 10 | 8.2 | 8 | 7.5 | 7 | 6.6 | 6 | 5.6 | 5.4 | 5.7 | 6.1 | 6.3 | 6.5 | 6.5 | 6.8143
5 | Entering Condenser Water Temp. (tcwe) | ºC | [11 empty] | 20.6 | 24.8 | 25.8 | 25.9 | 26.1 | 26 | 25.5 | 25.1 | 22.2 | 22.1 | 22.5 | 22.7 | 22.8 | 22.8 | 23.9214
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [11 empty] | 25.2 | 29.6 | 30.3 | 30.4 | 30.7 | 30.6 | 30.1 | 29.3 | 26.5 | 27 | 27.3 | 27.8 | 27.7 | 27.9 | 28.6
7 | Chilled water inlet pressure | (Kg/Cm2) | [11 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [11 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [11 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [11 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [11 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [11 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [11 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [11 empty] | 1766.0384 | 2376.1243 | 2183.4656 | 2279.795 | 2344.0146 | 2279.795 | 2279.795 | 2119.246 | 2279.795 | 2440.3439 | 2472.4537 | 2536.6733 | 2568.7831 | 2600.8929 | 32527.2156
15 | Power Consumption of Chiller | KWH | [11 empty] | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1350 | 1450 | 19000
16 | Specific power consumption of Chiller | (iKW/TR) | [11 empty] | 0.76442 | 0.56815 | 0.61828 | 0.59216 | 0.57593 | 0.59216 | 0.59216 | 0.63702 | 0.59216 | 0.5532 | 0.54602 | 0.53219 | 0.52554 | 0.5575 | 0.58906
17 | Average iKW/TR |  |  | 0.58906 | [23 empty] | 0.58906
18 | COP of chiller | [12 empty] | 4.5995 | 6.1885 | 5.6867 | 5.9376 | 6.1049 | 5.9376 | 5.9376 | 5.5195 | 5.9376 | 6.3557 | 6.4394 | 6.6066 | 6.6903 | 6.3067 | 6.0177
19 | EER of Chiller | [12 empty] | 15.6983 | 21.1213 | 19.4088 | 20.265 | 20.8359 | 20.265 | 20.265 | 18.8379 | 20.265 | 21.6921 | 21.9776 | 22.5484 | 22.8338 | 21.5248 | 20.5385
20 | LMTD of Condenser | ºC | [11 empty] | 4.2973 | 4.035 | 3.9297 | 3.9297 | 4.0763 | 3.9649 | 3.8528 | 3.823 | 3.8587 | 4.1822 | 4.035 | 4.2521 | 4.0699 | 4.2521 | 4.0399
21 | LMTD of Evaporator | ºC | [11 empty] | 2.0437 | 2.4912 | 2.1491 | 2.215 | 2.2586 | 2.215 | 2.215 | 2.1049 | 2.215 | 2.5369 | 2.5597 | 2.3881 | 2.4095 | 2.6502 | 2.318
Chiller Operation
Performance Sheet Chiller
Date :- 14/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C | [27 empty] | Average
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.8 | 0.9 | 0.7 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.81176
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.4 | 0.1 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [7 empty] | 0.35294
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.2 | 14.1 | 14.6 | 14.8 | 14.8 | 14.6 | 14.3 | 14.3 | 14.3 | 14.3 | 14.4 | 15.7 | 15 | 14.6 | 14.3 | 13.8 | 13.2 | [7 empty] | 14.4294
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.7 | 5.7 | 6.1 | 6.4 | 6.5 | 6.5 | 6.3 | 6.4 | 6.3 | 6.2 | 6.4 | 8.2 | 7.8 | 7.5 | 6.7 | 6 | 5.8 | [7 empty] | 6.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.7 | 21.7 | 21.8 | 22.7 | 22.8 | 23.6 | 24.1 | 24.5 | 23.9 | 23.8 | 23.8 | 24.9 | 25.9 | 25.9 | 26.1 | 26 | 25.6 | [7 empty] | 24.0471
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.4 | 27.4 | 27.5 | 28.3 | 28.3 | 29 | 29.4 | 29.7 | 29.2 | 29.3 | 29.1 | 30 | 30.7 | 30.8 | 31.5 | 31.4 | 30.6 | [7 empty] | 29.3882
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2729.332 | 2697.2222 | 2729.332 | 2697.2222 | 2665.1124 | 2600.8929 | 2568.7831 | 2536.6733 | 2568.7831 | 2600.8929 | 2568.7831 | 2408.2341 | 2311.9048 | 2279.795 | 2440.3439 | 2504.5635 | 2376.1243 | [7 empty] | 43283.9947
15 | Power Consumption of Chiller | KWH |  | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.94 | 1252.96 | [7 empty] | 21300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.45906 | 0.46453 | 0.45906 | 0.46453 | 0.47013 | 0.48173 | 0.48776 | 0.49393 | 0.48776 | 0.48173 | 0.48776 | 0.52027 | 0.54195 | 0.54958 | 0.51343 | 0.50026 | 0.52731 | [7 empty] | 0.49358
17 | Average iKW/TR |  |  | 0.49358 | [23 empty] | 0.49358
18 | COP of chiller |  |  | 7.6591 | 7.5689 | 7.6591 | 7.5689 | 7.4788 | 7.2986 | 7.2085 | 7.1184 | 7.2085 | 7.2986 | 7.2085 | 6.758 | 6.4877 | 6.3976 | 6.8481 | 7.0283 | 6.6678 | [7 empty] | 7.1449
19 | EER of Chiller |  |  | 26.1403 | 25.8328 | 26.1403 | 25.8328 | 25.5253 | 24.9102 | 24.6027 | 24.2951 | 24.6027 | 24.9102 | 24.6027 | 23.065 | 22.1424 | 21.8349 | 23.3725 | 23.9876 | 22.7571 | [7 empty] | 24.3856
20 | LMTD of Condenser | ºC |  | 2.7208 | 2.7208 | 2.7208 | 2.693 | 2.6651 | 2.6371 | 2.7462 | 2.5808 | 2.7462 | 2.5215 | 2.7462 | 2.5524 | 2.4667 | 2.4954 | 2.6371 | 2.6371 | 2.524 | [7 empty] | 2.636
21 | LMTD of Evaporator | ºC |  | 2.7399 | 2.7175 | 2.7399 | 2.4946 | 2.4734 | 2.8472 | 2.8236 | 2.8 | 2.6277 | 1.8381 | 2.6277 | 2.302 | 2.2368 | 2.215 | 2.3236 | 2.3666 | 2.2803 | [7 empty] | 2.4973

## 15-02-2019 (hidden)
Performance Sheet Chiller
Date :- 15/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  |  |  | 1.8 | 1.6 | 1.4 | 1.4 | 1.4 | 1.4 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.6 | 1.4 | 1.6 | 1.8 | 1.8 | 1.6 | 1.8 | 1.6 | 1.6 | 1.8 | 1.8 | 1.5818
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.8 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.5 | 0.4 | 0.4 | 6 | 0.6 | 0.5 | 0.7 | 0.9 | 1.5 | 1.4 | 1.1 | 1.2 | 1.4 | 1.4 | 1.4 | 1.4 | 1.1136
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 14.3 | 14.6 | 13.6 | 13 | 12.8 | 12.9 | 13 | 13.1 | 13.4 | 13.5 | 13.5 | 13.3 | 13 | 12.4 | 13.2 | 13.6 | 13.7 | 13.6 | 13.5 | 13.4 | 13.3 | 13.2 | 13.3591
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 9 | 7.3 | 6.8 | 6.9 | 7 | 7 | 7 | 6.8 | 7 | 7.1 | 7 | 7 | 5.9 | 5.5 | 5.7 | 5.8 | 5.8 | 5.8 | 5.8 | 5.5 | 5.6 | 5.7 | 6.5
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 21.1 | 24.3 | 25.1 | 24.3 | 24.5 | 24.5 | 25.1 | 25.3 | 26.1 | 26 | 25.6 | 25 | 25.1 | 23.3 | 22.1 | 21.5 | 21 | 20.8 | 20.1 | 20.2 | 21.1 | 21.5 | 23.3455
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 26.7 | 29.9 | 30.1 | 29 | 29 | 29 | 29.7 | 30.1 | 31.1 | 31 | 30.5 | 29.8 | 30.5 | 28.6 | 27.9 | 27.5 | 27.1 | 26.8 | 26.2 | 26.3 | 27 | 27.3 | 28.6864
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 1701.8188 | 2344.0146 | 2183.4656 | 1958.6971 | 1862.3677 | 1894.4775 | 1926.5873 | 2022.9167 | 2055.0265 | 2055.0265 | 2087.1362 | 2022.9167 | 2279.795 | 2215.5754 | 2408.2341 | 2504.5635 | 2536.6733 | 2504.5635 | 2472.4537 | 2536.6733 | 2472.4537 | 2408.2341 | 48453.6706
15 | Power Consumption of Chiller | KWH |  |  |  | 1530 | 1530 | 1484 | 1484 | 1484 | 1530 | 1530 | 1530 | 1530 | 1484 | 1484 | 1550 | 1550 | 1550 | 1550 | 1580 | 1580 | 1580 | 1580 | 1550 | 1550 | 1580 | 33800
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.89904 | 0.65273 | 0.67965 | 0.75765 | 0.79684 | 0.80761 | 0.79415 | 0.75633 | 0.74452 | 0.72213 | 0.71102 | 0.76622 | 0.67989 | 0.69959 | 0.64363 | 0.63085 | 0.62286 | 0.63085 | 0.63904 | 0.61104 | 0.62691 | 0.65608 | 0.70585
17 | Average iKW/TR |  |  | 0.70585 | [23 empty] | 0.70585
18 | COP of chiller |  |  |  |  | 3.9108 | 5.3866 | 5.1732 | 4.6407 | 4.4125 | 4.3536 | 4.4274 | 4.6487 | 4.7225 | 4.8689 | 4.945 | 4.5888 | 5.1715 | 5.0258 | 5.4628 | 5.5734 | 5.6449 | 5.5734 | 5.502 | 5.7542 | 5.6085 | 5.3591 | 5.0343
19 | EER of Chiller |  |  |  |  | 13.3477 | 18.3846 | 17.6562 | 15.8387 | 15.0597 | 14.8588 | 15.1106 | 15.8662 | 16.118 | 16.6176 | 16.8773 | 15.6614 | 17.6502 | 17.153 | 18.6446 | 19.0222 | 19.266 | 19.0222 | 18.7783 | 19.6389 | 19.1417 | 18.2906 | 17.182
20 | LMTD of Condenser | ºC |  |  |  | 3.9613 | 3.7232 | 3.2899 | 3.1933 | 3.1283 | 3.1283 | 3.2791 | 3.3448 | 3.4099 | 3.4099 | 3.2578 | 3.4625 | 3.4167 | 3.6264 | 4.0268 | 4.0918 | 3.8823 | 4.0918 | 3.8823 | 3.8823 | 4.0594 | 4.0268 | 3.617
21 | LMTD of Evaporator | ºC |  |  |  | 2.609 | 2.832 | 2.7067 | 2.528 | 2.2891 | 2.4763 | 2.3392 | 2.2353 | 2.2589 | 8.8162 | 2.6306 | 2.4137 | 2.9451 | 3.1952 | 4.1858 | 4.1429 | 3.7585 | 3.8712 | 4.1137 | 4.1721 | 4.1137 | 4.055 | 3.3949
Performance Sheet Chiller
Date :- 15/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | [24 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 2.3 | 2.4 | 2.1 | 1.9 | 1.8 | 1.7 | 1.7 | 1.7 | 1.7 | 1.9 | 1.8 | 1.7 | 1.8 | 1.9 | [10 empty] | 1.8857
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.4 | [10 empty] | 0.32857
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.7 | 14.7 | 15.3 | 14.2 | 13.7 | 13.1 | 13 | 13 | 13.2 | 13.3 | 13.6 | 13.7 | 13.6 | 13.5 | [10 empty] | 13.7571
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.8 | 6.6 | 7 | 7.1 | 7 | 6.9 | 7 | 7.1 | 7.1 | 7.1 | 7 | 7 | 6.8 | 7 | [10 empty] | 6.9643
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.8 | 22.8 | 22.1 | 25.2 | 25.2 | 24.6 | 24.7 | 24.8 | 25.3 | 25.5 | 26.2 | 26.3 | 25.8 | 25.2 | [10 empty] | 24.75
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28 | 27.8 | 27.3 | 29.8 | 29.5 | 28.5 | 28.6 | 28.7 | 29.3 | 29.5 | 30.5 | 30.5 | 30.2 | 29.4 | [10 empty] | 29.1143
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [10 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [10 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [10 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [10 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [10 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [10 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [10 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2600.8929 | 2665.1124 | 2279.795 | 2151.3558 | 1990.8069 | 1926.5873 | 1894.4775 | 1958.6971 | 1990.8069 | 2119.246 | 2151.3558 | 2183.4656 | 2087.1362 | [10 empty] | 30536.4087
15 | Power Consumption of Chiller | KWH |  | 1340 | 1260 | 1300 | 1240 | 1260 | 1240 | 1240 | 1240 | 1240 | 1300 | 1260 | 1260 | 1260 | 1260 | [10 empty] | 17700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.52825 | 0.48445 | 0.48778 | 0.54391 | 0.58568 | 0.62286 | 0.64363 | 0.65453 | 0.63307 | 0.653 | 0.59455 | 0.58568 | 0.57706 | 0.6037 | [10 empty] | 0.58558
17 | Average iKW/TR |  |  | 0.58558 | [23 empty] | 0.58558
18 | COP of chiller |  |  | 6.6559 | 7.2577 | 7.2081 | 6.4643 | 6.0033 | 5.6449 | 5.4628 | 5.3718 | 5.5539 | 5.3844 | 5.9137 | 6.0033 | 6.0929 | 5.8241 | [10 empty] | 6.0601
19 | EER of Chiller |  |  | 22.7167 | 24.7706 | 24.6013 | 22.0627 | 20.4893 | 19.266 | 18.6446 | 18.3338 | 18.9553 | 18.3768 | 20.1835 | 20.4893 | 20.7951 | 19.8777 | [10 empty] | 20.683
20 | LMTD of Condenser | ºC |  | 4.3993 | 4.4405 | 4.1736 | 3.74 | 3.5231 | 3.2714 | 3.2714 | 3.2714 | 3.3062 | 3.5301 | 3.5231 | 3.3753 | 3.5577 | 3.6007 | [10 empty] | 3.6417
21 | LMTD of Evaporator | ºC |  | 2.6051 | 2.6502 | 2.6951 | 2.215 | 2.1271 | 1.7889 | 1.9708 | 1.9481 | 1.9933 | 2.0158 | 2.1049 | 2.3293 | 2.1491 | 2.2825 | [10 empty] | 2.2054

## 16-02-2019 (hidden)
Performance Sheet Chiller
Date :- 16/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.6 | 1.4 | 1.6 | 1.6 | 1.6 | 1.7 | 0.9 | 0.9 | 1.4 | 1.4 | [8 empty] | 1.5562
2 | Small temperature difference of evaporator | ºC |  | 1.5 | 1.7 | 1.6 | 1.7 | 1.6 | 1.6 | 1.2 | 0.9 | 0.8 | 0.9 | 1.1 | 1.4 | 0.3 | 0.3 | 0.7 | 0.6 | [8 empty] | 1.1188
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.1 | 13.5 | 13.6 | 13.6 | 13.1 | 12.6 | 12 | 12 | 12.1 | 12.3 | 14 | 14.6 | 15.1 | 13.5 | 13.3 | [8 empty] | 13.2188
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.5 | 5.8 | 5.8 | 5.8 | 5.6 | 5.5 | 5.3 | 5.5 | 5.6 | 5.5 | 6.4 | 6.8 | 7.9 | 7.1 | 7 | [8 empty] | 6.0375
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.5 | 20.4 | 20.7 | 20 | 20 | 20 | 20 | 20.7 | 22 | 22.1 | 22.1 | 22.6 | 21.9 | 23.7 | 24 | 24 | [8 empty] | 21.5437
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.3 | 26.3 | 26.7 | 26.1 | 26 | 26 | 25.5 | 25.8 | 27 | 27.1 | 27.3 | 28.3 | 28 | 29.2 | 29 | 28.9 | [8 empty] | 27.0938
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2440.3439 | 2440.3439 | 2472.4537 | 2504.5635 | 2504.5635 | 2408.2341 | 2279.795 | 2151.3558 | 2087.1362 | 2087.1362 | 2183.4656 | 2440.3439 | 2504.5635 | 2311.9048 | 2055.0265 | 2022.9167 | [8 empty] | 36894.1468
15 | Power Consumption of Chiller | KWH |  | 1345 | 1400 | 1375 | 1345 | 1345 | 1345 | 1320 | 1320 | 1295 | 1340 | 1390 | 1345 | 1345 | 1300 | 1345 | 1345 | [8 empty] | 21500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.55115 | 0.57369 | 0.55613 | 0.53702 | 0.53702 | 0.5585 | 0.579 | 0.61357 | 0.62047 | 0.64203 | 0.6366 | 0.55115 | 0.53702 | 0.56231 | 0.65449 | 0.66488 | [8 empty] | 0.58594
17 | Average iKW/TR |  |  | 0.58594 | [23 empty] | 0.58594
18 | COP of chiller |  |  | 6.3794 | 6.1287 | 6.3223 | 6.5472 | 6.5472 | 6.2954 | 6.0725 | 5.7304 | 5.6667 | 5.4764 | 5.5231 | 6.3794 | 6.5472 | 6.2528 | 5.3721 | 5.2882 | [8 empty] | 6.0331
19 | EER of Chiller |  |  | 21.7728 | 20.9174 | 21.578 | 22.3457 | 22.3457 | 21.4863 | 20.7256 | 19.558 | 19.3404 | 18.6909 | 18.8502 | 21.7728 | 22.3457 | 21.3409 | 18.335 | 18.0485 | [8 empty] | 20.5909
20 | LMTD of Condenser | ºC |  | 4.0268 | 4.0594 | 4.0918 | 4.1242 | 4.0918 | 4.0918 | 3.691 | 3.3218 | 3.5284 | 3.5284 | 3.5938 | 3.8753 | 2.9738 | 2.8037 | 3.2899 | 3.2578 | [8 empty] | 3.6469
21 | LMTD of Evaporator | ºC |  | 4.2156 | 4.4722 | 4.375 | 4.5331 | 4.405 | 4.3146 | 3.6713 | 3.1404 | 2.9398 | 3.0852 | 3.4491 | 4.0844 | 2.3666 | 2.2368 | 2.7625 | 2.5795 | [8 empty] | 3.5394
Performance Sheet Chiller
Date :- 16/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [13 empty] | 0.9 | 0.9 | 0.8 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 0.86667
2 | Small temperature difference of evaporator | ºC | [13 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.34167
3 | Entering Chilled Water Temp. (tchwe) | ºC | [13 empty] | 15.2 | 15.3 | 14 | 13.6 | 12.8 | 12.5 | 13.1 | 13.2 | 13.3 | 13.3 | 13.2 | 13.2 | 13.5583
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [13 empty] | 8 | 7.8 | 7.8 | 7 | 5.8 | 5.4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.4 | 5.5 | 6.225
5 | Entering Condenser Water Temp. (tcwe) | ºC | [13 empty] | 22 | 23.8 | 24.3 | 24.2 | 24.3 | 20.8 | 19.2 | 20 | 19.8 | 19.6 | 19.2 | 19.3 | 21.375
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [13 empty] | 21.3 | 29 | 28.5 | 28.7 | 29.1 | 25.6 | 24.2 | 25.1 | 25.1 | 24.8 | 24.4 | 24.5 | 25.8583
7 | Chilled water inlet pressure | (Kg/Cm2) | [13 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [13 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [13 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [13 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [13 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [13 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [13 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [13 empty] | 2311.9048 | 2408.2341 | 1990.8069 | 2119.246 | 2247.6852 | 2279.795 | 2440.3439 | 2472.4537 | 2504.5635 | 2504.5635 | 2504.5635 | 2472.4537 | 28256.6138
15 | Power Consumption of Chiller | KWH | [13 empty] | 1315 | 1315 | 1325 | 1320 | 1315 | 1315 | 1315 | 1320 | 1315 | 1315 | 1315 | 1315 | 15800
16 | Specific power consumption of Chiller | (iKW/TR) | [13 empty] | 0.5688 | 0.54604 | 0.66556 | 0.62286 | 0.58505 | 0.57681 | 0.53886 | 0.53388 | 0.52504 | 0.52504 | 0.52504 | 0.53186 | 0.56207
17 | Average iKW/TR |  |  | 0.56207 | [23 empty] | 0.56207
18 | COP of chiller | [14 empty] | 6.1815 | 6.4391 | 5.2828 | 5.6449 | 6.0098 | 6.0956 | 6.5249 | 6.5857 | 6.6966 | 6.6966 | 6.6966 | 6.6108 | 6.2887
19 | EER of Chiller | [14 empty] | 21.0974 | 21.9765 | 18.0301 | 19.266 | 20.5114 | 20.8044 | 22.2695 | 22.4771 | 22.8555 | 22.8555 | 22.8555 | 22.5625 | 21.4635
20 | LMTD of Condenser | ºC | [13 empty] | 0.4654 | 2.7173 | 2.2918 | 2.244 | 2.3285 | 2.6005 | 2.6591 | 2.6883 | 2.7462 | 2.7173 | 2.7173 | 2.85 | 2.4188
21 | LMTD of Evaporator | ºC | [13 empty] | 2.2368 | 2.302 | 2.0158 | 2.1049 | 2.1931 | 2.215 | 2.5369 | 2.5597 | 2.5824 | 2.3666 | 2.5824 | 2.5597 | 2.3546

## 17-02-2019 (hidden)
Performance Sheet Chiller
Date :- 17/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [11 empty] | 1.4 | 1.4 | 1.1 | 1.1 | 1.1 | 1.5 | 1.6 | 1.6 | 1.5 | 1.5 | 1.6 | 1.5 | 1.6 | 1.6 | 1.4357
2 | Small temperature difference of evaporator | ºC | [11 empty] | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 1.1 | 1.2 | 1.2 | 1.3 | 1.3 | 1.4 | 1.3 | 1.4 | 1.0857
3 | Entering Chilled Water Temp. (tchwe) | ºC | [11 empty] | 15 | 15 | 13.8 | 13.3 | 13.3 | 12.2 | 12.7 | 13.3 | 13.6 | 13.8 | 13.8 | 13.7 | 13.7 | 13.8 | 13.6429
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [11 empty] | 8 | 7.9 | 7.8 | 7.1 | 6.1 | 5.4 | 5.7 | 5.7 | 6.2 | 6.2 | 6.1 | 6.1 | 6 | 6.1 | 6.4571
5 | Entering Condenser Water Temp. (tcwe) | ºC | [11 empty] | 19.9 | 24.2 | 24.2 | 24 | 25.2 | 23.7 | 22.6 | 22.4 | 21.9 | 21.4 | 21.7 | 21.7 | 21.8 | 21.3 | 22.5714
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [11 empty] | 25 | 29.6 | 28.8 | 28.8 | 30.6 | 29 | 28 | 28.3 | 27.7 | 27.3 | 27.7 | 27.7 | 27.8 | 27.3 | 28.1143
7 | Chilled water inlet pressure | (Kg/Cm2) | [11 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [11 empty] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) | [11 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [11 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [11 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [11 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [11 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [11 empty] | 2247.6852 | 2279.795 | 1926.5873 | 1990.8069 | 2311.9048 | 2183.4656 | 2247.6852 | 2215.5754 | 2215.5754 | 2215.5754 | 2215.5754 | 2215.5754 | 2215.5754 | 2215.5754 | 30696.9577
15 | Power Consumption of Chiller | KWH | [11 empty] | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.9 | 1592.3 | 22300
16 | Specific power consumption of Chiller | (iKW/TR) | [11 empty] | 0.70868 | 0.6987 | 0.8268 | 0.80013 | 0.689 | 0.72953 | 0.70868 | 0.40622 | 0.40622 | 0.40622 | 0.40622 | 0.40622 | 0.40622 | 0.40622 | 0.57179
17 | Average iKW/TR |  |  | 0.57179 | [23 empty] | 0.57179
18 | COP of chiller | [12 empty] | 4.9613 | 5.0322 | 4.2525 | 4.3943 | 5.1031 | 4.8196 | 4.9613 | 8.6555 | 8.6555 | 8.6555 | 8.6555 | 8.6555 | 8.6555 | 8.6555 | 6.7223
19 | EER of Chiller | [12 empty] | 16.9329 | 17.1748 | 14.5139 | 14.9977 | 17.4167 | 16.4491 | 16.9329 | 29.5413 | 29.5413 | 29.5413 | 29.5413 | 29.5413 | 29.5413 | 29.5413 | 22.9434
20 | LMTD of Condenser | ºC | [11 empty] | 3.3218 | 3.4167 | 2.7961 | 2.8578 | 3.0397 | 3.5065 | 3.6588 | 4.0408 | 4.0408 | 4.0408 | 4.0408 | 4.0408 | 4.0408 | 4.0408 | 3.6345
21 | LMTD of Evaporator | ºC | [11 empty] | 3.2225 | 3.1004 | 2.8037 | 2.8584 | 3.1269 | 3.1678 | 3.506 | 2.3759 | 2.3759 | 2.3759 | 2.3759 | 2.3759 | 2.3759 | 2.3759 | 2.7441
Performance Sheet Chiller
Date :- 17/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1 | 1 | 0.9 | 0.9 | 1 | 1.1 | 0.9 | 0.9 | 1 | 1 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | [9 empty] | 0.90667
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | [9 empty] | 0.34667
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 13.1 | 13.4 | 13.5 | 13.6 | 13.9 | 14.1 | 14.3 | 14.7 | 15 | 15.4 | 15.3 | 14.1 | 13.7 | 13.6 | [9 empty] | 14.0533
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.7 | 5.6 | 5.6 | 5.6 | 5.7 | 5.7 | 5.7 | 6 | 6.1 | 7.7 | 7.8 | 7.8 | 8 | 6.2 | [9 empty] | 6.32
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 19.2 | 19.2 | 19.8 | 19.4 | 19.6 | 20.5 | 21.3 | 22.1 | 22.1 | 22.2 | 23.1 | 24.3 | 24.5 | 24.1 | 25.3 | [9 empty] | 21.78
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 24.2 | 24.2 | 24.9 | 24.7 | 24.9 | 26 | 26.8 | 27.9 | 28.1 | 28.2 | 28.2 | 29.3 | 28.6 | 28 | 30.4 | [9 empty] | 26.96
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [9 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | [9 empty] | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [9 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [9 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [9 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [9 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [9 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2376.1243 | 2504.5635 | 2536.6733 | 2568.7831 | 2633.0026 | 2697.2222 | 2761.4418 | 2793.5516 | 2857.7712 | 2472.4537 | 2408.2341 | 2022.9167 | 1830.2579 | 2376.1243 | [9 empty] | 37247.3545
15 | Power Consumption of Chiller | KWH |  | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1270 | 1270 | 1300 | 1320 | 1210 | 1210 | 1200 | 1260 | 1240 | [9 empty] | 18600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.5066 | 0.51344 | 0.48711 | 0.48094 | 0.47493 | 0.46335 | 0.47085 | 0.4599 | 0.46536 | 0.4619 | 0.48939 | 0.50244 | 0.5932 | 0.68843 | 0.52186 | [9 empty] | 0.50531
17 | Average iKW/TR |  |  | 0.50531 | [23 empty] | 0.50531
18 | COP of chiller |  |  | 6.9405 | 6.8479 | 7.2181 | 7.3106 | 7.4031 | 7.5882 | 7.4673 | 7.6451 | 7.5555 | 7.6121 | 7.1844 | 6.9978 | 5.9271 | 5.1073 | 6.7375 | [9 empty] | 7.0362
19 | EER of Chiller |  |  | 23.6878 | 23.3719 | 24.6353 | 24.9511 | 25.2669 | 25.8986 | 25.4858 | 26.0926 | 25.7869 | 25.98 | 24.5204 | 23.8835 | 20.2293 | 17.4312 | 22.995 | [9 empty] | 24.0144
20 | LMTD of Condenser | ºC |  | 2.7906 | 2.7906 | 2.6883 | 2.7462 | 2.8796 | 3.0696 | 2.8037 | 2.8892 | 3.0834 | 3.0834 | 2.6883 | 2.6591 | 2.1295 | 2.0715 | 2.4119 | [9 empty] | 2.719
21 | LMTD of Evaporator | ºC |  | 2.5141 | 2.4912 | 2.5824 | 2.6051 | 2.6277 | 2.6727 | 2.7175 | 2.7622 | 2.7844 | 2.8287 | 2.3451 | 2.302 | 1.8097 | 1.6842 | 2.0343 | [9 empty] | 2.4508

## 18-02-2019 (hidden)
Performance Sheet Chiller
Date :- 18/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.7 | 1.7 | 1.6 | 1.7 | 1.7 | 1.7 | 1.6 | 1.6 | 1.5 | 1.4 | 1.4 | 1.2 | 1.2 | 1.6 | 1.8 | 1.6 | 1.6 | 1.6 | 1.7 | 1.6 | 1.6 | 1.4 | 1.5 | 1 | 1.5417
2 | Small temperature difference of evaporator | ºC |  | 1.5 | 1.6 | 1.7 | 1.7 | 1.7 | 1.6 | 1.5 | 1.5 | 1.5 | 0.8 | 1.1 | 1.1 | 1.2 | 1 | 0.7 | 1.2 | 1.4 | 1.6 | 1.4 | 1.3 | 1.4 | 1.3 | 1.4 | 1.3 | 1.3542
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.7 | 13.5 | 13.7 | 13.7 | 13.7 | 14 | 14.2 | 14.5 | 14.9 | 15.3 | 14.7 | 13.8 | 13.6 | 13.5 | 13 | 12.2 | 13.2 | 13.7 | 13.7 | 13.8 | 13.8 | 13.8 | 13.7 | 13.7 | 13.8083
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6 | 5.7 | 5.9 | 5.9 | 5.9 | 6.3 | 6.5 | 6.7 | 7.2 | 7.6 | 8 | 8 | 8.1 | 7.2 | 5.8 | 5.5 | 5.8 | 6.2 | 6.1 | 6.1 | 6.2 | 6.2 | 6.1 | 6.1 | 6.4625
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.8 | 20.5 | 20.8 | 20.3 | 20.1 | 20.4 | 20.6 | 22.2 | 22.6 | 22.9 | 24.6 | 22.6 | 22.5 | 22.1 | 22.4 | 22.4 | 21.6 | 21.4 | 20.7 | 21.3 | 21 | 20.8 | 21.2 | 21 | 21.5333
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.8 | 26.6 | 26.8 | 26.4 | 26.2 | 26.5 | 26.7 | 28.2 | 28.5 | 28.9 | 29.8 | 27.3 | 26.8 | 27 | 28 | 27.7 | 27.4 | 27.3 | 26.7 | 27.2 | 27 | 26.8 | 27.2 | 27 | 27.2833
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2472.4537 | 2504.5635 | 2504.5635 | 2504.5635 | 2504.5635 | 2472.4537 | 2472.4537 | 2504.5635 | 2472.4537 | 2472.4537 | 2151.3558 | 1862.3677 | 1766.0384 | 2022.9167 | 2311.9048 | 2151.3558 | 2376.1243 | 2408.2341 | 2440.3439 | 2472.4537 | 2440.3439 | 2440.3439 | 2440.3439 | 2440.3439 | 56609.5569
15 | Power Consumption of Chiller | KWH |  | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1400 | 1400 | 1200 | 1300 | 1400 | 1600 | 1400 | 1300 | 1600 | 1500 | 1400 | 1500 | 1600 | 1500 | 1500 | 25000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.68758 | 0.67876 | 0.67876 | 0.67876 | 0.67876 | 0.68758 | 0.68758 | 0.67876 | 0.68758 | 0.56624 | 0.65075 | 0.64434 | 0.73611 | 0.69207 | 0.69207 | 0.65075 | 0.54711 | 0.66439 | 0.61467 | 0.56624 | 0.61467 | 0.65565 | 0.61467 | 0.61467 | 0.65285
17 | Average iKW/TR |  |  | 0.65285 | [23 empty] | 0.65285
18 | COP of chiller |  |  | 5.1136 | 5.18 | 5.18 | 5.18 | 5.18 | 5.1136 | 5.1136 | 5.18 | 5.1136 | 6.2094 | 5.403 | 5.4567 | 4.7765 | 5.0804 | 5.0804 | 5.403 | 6.4265 | 5.2921 | 5.7202 | 6.2094 | 5.7202 | 5.3627 | 5.7202 | 5.7202 | 5.414
19 | EER of Chiller |  |  | 17.4528 | 17.6794 | 17.6794 | 17.6794 | 17.6794 | 17.4528 | 17.4528 | 17.6794 | 17.4528 | 21.1927 | 18.4404 | 18.6238 | 16.302 | 17.3394 | 17.3394 | 18.4404 | 21.9337 | 18.0619 | 19.5229 | 21.1927 | 19.5229 | 18.3027 | 19.5229 | 19.5229 | 18.4779
20 | LMTD of Condenser | ºC |  | 3.972 | 4.004 | 3.8507 | 4.004 | 4.004 | 4.004 | 3.8823 | 3.8507 | 3.6967 | 3.6036 | 3.3535 | 2.9511 | 2.8244 | 3.4955 | 3.9613 | 3.6264 | 3.7872 | 3.819 | 3.972 | 3.819 | 3.8507 | 3.6036 | 3.728 | 3.0834 | 3.6978
21 | LMTD of Evaporator | ºC |  | 4.2454 | 4.405 | 4.5331 | 4.5331 | 4.5331 | 4.375 | 4.2454 | 4.275 | 4.2454 | 3.2583 | 3.4204 | 3.1587 | 3.1981 | 3.1692 | 2.9709 | 3.5552 | 4.0255 | 4.3146 | 4.0844 | 3.9796 | 4.0844 | 3.9507 | 4.0844 | 3.9507 | 3.9415
Performance Sheet Chiller
Date :- 18/02/2019
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [10 empty] | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | [10 empty] | 0.72
2 | Small temperature difference of evaporator | ºC | [10 empty] | 0.2 | 0.1 | 0.1 | 0.2 | 0.3 | [10 empty] | 0.18
3 | Entering Chilled Water Temp. (tchwe) | ºC | [10 empty] | 15.3 | 14.7 | 13.7 | 13.6 | 13.5 | [10 empty] | 14.16
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [10 empty] | 12.6 | 7.2 | 8 | 8 | 6.9 | [10 empty] | 8.54
5 | Entering Condenser Water Temp. (tcwe) | ºC | [10 empty] | 23 | 24.8 | 22.7 | 22.5 | 22.2 | [10 empty] | 23.04
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [10 empty] | 24.6 | 29.6 | 26.6 | 26.1 | 26.1 | [10 empty] | 26.6
7 | Chilled water inlet pressure | (Kg/Cm2) | [10 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [10 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [10 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [10 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [10 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [10 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [10 empty] | 3 | 3 | 3 | 3 | 3 | [10 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [10 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [10 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [10 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [10 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [10 empty] | 971 | 971 | 971 | 971 | 971 | [10 empty] | 971
14 | TR Genrated by Chiller | TR | [10 empty] | 866.9643 | 2408.2341 | 1830.2579 | 1798.1481 | 2119.246 | [10 empty] | 9022.8505
15 | Power Consumption of Chiller | KWH | [10 empty] | 1400 | 1200 | 1200 | 1400 | 1600 | [10 empty] | 6800
16 | Specific power consumption of Chiller | (iKW/TR) | [10 empty] | 1.6148 | 0.49829 | 0.65565 | 0.77858 | 0.75499 | [10 empty] | 0.86047
17 | Average iKW/TR |  |  | 0.86047 | [23 empty] | 0.86047
18 | COP of chiller | [11 empty] | 2.1773 | 7.0561 | 5.3627 | 4.5159 | 7.0561 | [10 empty] | 5.2336
19 | EER of Chiller | [11 empty] | 7.4312 | 24.0826 | 18.3027 | 15.4128 | 24.0826 | [10 empty] | 17.8624
20 | LMTD of Condenser | ºC | [10 empty] | 1.2314 | 2.1846 | 2.2025 | 2.1117 | 2.2025 | [10 empty] | 1.9866
21 | LMTD of Evaporator | ºC | [10 empty] | 1.0097 | 1.7318 | 1.4038 | 1.6631 | 2.1049 | [10 empty] | 1.5827

## 19-02-2019 (hidden)
Performance Sheet Chiller
Date :- 19/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.8 | 1.7 | 1.7 | 1.8 | 1.7 | 1.7 | 1.6 | 1.4 | 1.5 | 1.5 | 1.5 | 1.7 | 1.6 | 1.5 | 1.4 | 1.3 | 1.4 | 1.6 | 1.6 | 1.5 | 1.6 | 1.6 | 1.7 | 1.7 | 1.5875
2 | Small temperature difference of evaporator | ºC |  | 1.8 | 1.8 | 1.7 | 1.8 | 1.7 | 1.4 | 1 | 0.8 | 0.8 | 0.8 | 1.1 | 1.4 | 1.1 | 0.8 | 0.4 | 0.3 | 0.9 | 1.2 | 1.2 | 1 | 1.1 | 1.2 | 1 | 1.1 | 1.1417
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.6 | 13.5 | 13.7 | 13.8 | 13.7 | 13.7 | 12.9 | 12.3 | 12.1 | 12.2 | 12.9 | 14.4 | 15 | 14.9 | 13.7 | 13.1 | 12.4 | 12.2 | 13.1 | 13.3 | 13.6 | 13.7 | 13.8 | 13.8 | 13.3917
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.9 | 5.8 | 6 | 6 | 6.1 | 6.2 | 5.5 | 5.4 | 5.4 | 5.5 | 5.8 | 6.7 | 7.2 | 7.8 | 6.4 | 6.1 | 5.8 | 5.6 | 5.6 | 5.9 | 6.1 | 6.1 | 6.3 | 6.3 | 6.0625
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.6 | 20.2 | 20.2 | 20 | 19.9 | 19.8 | 20.4 | 20.9 | 22.8 | 23.6 | 23.4 | 22.6 | 21.7 | 24.2 | 25 | 25.1 | 24.8 | 22.2 | 21.6 | 22.1 | 22 | 21.9 | 21.9 | 22.1 | 22.0417
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.6 | 26.1 | 26.3 | 26 | 25.8 | 25.8 | 26.1 | 26.3 | 27.9 | 28.7 | 29 | 28.6 | 27.9 | 29.6 | 30.5 | 30.3 | 29.7 | 27.3 | 27.5 | 27.9 | 27.8 | 27.8 | 27.9 | 27.9 | 27.7208
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2472.4537 | 2472.4537 | 2472.4537 | 2504.5635 | 2440.3439 | 2408.2341 | 2376.1243 | 2215.5754 | 2151.3558 | 2151.3558 | 2279.795 | 2472.4537 | 2504.5635 | 2279.795 | 2344.0146 | 2247.6852 | 2119.246 | 2119.246 | 2408.2341 | 2376.1243 | 2408.2341 | 2440.3439 | 2408.2341 | 2408.2341 | 56481.1177
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1450 | 1500 | 1500 | 1450 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 35900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.60668 | 0.60668 | 0.60668 | 0.59891 | 0.61467 | 0.62286 | 0.63128 | 0.67703 | 0.69723 | 0.69723 | 0.65795 | 0.60668 | 0.59891 | 0.63602 | 0.63993 | 0.66735 | 0.68421 | 0.7078 | 0.62286 | 0.63128 | 0.62286 | 0.61467 | 0.62286 | 0.62286 | 0.63731
17 | Average iKW/TR |  |  | 0.63731 | [23 empty] | 0.63731
18 | COP of chiller |  |  | 5.7954 | 5.7954 | 5.7954 | 5.8707 | 5.7202 | 5.6449 | 5.5696 | 5.1933 | 5.0428 | 5.0428 | 5.3438 | 5.7954 | 5.8707 | 5.5281 | 5.4944 | 5.2686 | 5.1388 | 4.9675 | 5.6449 | 5.5696 | 5.6449 | 5.7202 | 5.6449 | 5.6449 | 5.5311
19 | EER of Chiller |  |  | 19.7798 | 19.7798 | 19.7798 | 20.0367 | 19.5229 | 19.266 | 19.0092 | 17.7248 | 17.211 | 17.211 | 18.2385 | 19.7798 | 20.0367 | 18.8674 | 18.7523 | 17.9816 | 17.5387 | 16.9541 | 19.266 | 19.0092 | 19.266 | 19.5229 | 19.266 | 19.266 | 18.8778
20 | LMTD of Condenser | ºC |  | 4.0918 | 3.9398 | 4.004 | 4.0918 | 3.9398 | 3.972 | 3.7553 | 3.4167 | 3.4422 | 3.4422 | 3.6021 | 3.972 | 3.9138 | 3.5385 | 3.4482 | 3.2309 | 3.2578 | 3.5612 | 3.819 | 3.6653 | 3.7872 | 3.819 | 3.972 | 3.9076 | 3.7329
21 | LMTD of Evaporator | ºC |  | 4.6288 | 4.6288 | 4.5027 | 4.6596 | 4.4722 | 4.055 | 3.4771 | 3.0472 | 2.9937 | 2.9937 | 3.5344 | 4.1137 | 3.7307 | 3.1004 | 2.4683 | 2.1931 | 3.1128 | 3.526 | 3.786 | 3.4771 | 3.6471 | 3.8144 | 3.5046 | 3.6471 | 3.6298
Performance Sheet Chiller
Date :- 19/02/2019
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [13 empty] | 0.8 | 0.7 | 0.7 | 0.7 | [8 empty] | 0.725
2 | Small temperature difference of evaporator | ºC | [13 empty] | 0.1 | 0.1 | 0.2 | 0.1 | [8 empty] | 0.125
3 | Entering Chilled Water Temp. (tchwe) | ºC | [13 empty] | 14.9 | 14.9 | 13.7 | 13.1 | [8 empty] | 14.15
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [13 empty] | 9 | 7.8 | 6.1 | 6 | [8 empty] | 7.225
5 | Entering Condenser Water Temp. (tcwe) | ºC | [13 empty] | 24.2 | 24.8 | 25.2 | 24.8 | [8 empty] | 24.75
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [13 empty] | 28.7 | 29.3 | 30 | 29 | [8 empty] | 29.25
7 | Chilled water inlet pressure | (Kg/Cm2) | [13 empty] | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [13 empty] | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [13 empty] | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [13 empty] | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [13 empty] | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [13 empty] | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [13 empty] | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR | [13 empty] | 1894.4775 | 2279.795 | 2440.3439 | 2279.795 | [8 empty] | 8894.4114
15 | Power Consumption of Chiller | KWH | [13 empty] | 1375 | 1375 | 1375 | 1375 | [8 empty] | 5500
16 | Specific power consumption of Chiller | (iKW/TR) | [13 empty] | 0.72579 | 0.60312 | 0.56345 | 0.60312 | [8 empty] | 0.62387
17 | Average iKW/TR |  |  | 0.62387 | [23 empty] | 0.62387
18 | COP of chiller | [14 empty] | 4.8444 | 5.8296 | 6.2402 | 5.8296 | [8 empty] | 5.686
19 | EER of Chiller | [14 empty] | 16.5338 | 19.8966 | 21.2977 | 19.8966 | [8 empty] | 19.4062
20 | LMTD of Condenser | ºC | [13 empty] | 2.3799 | 2.244 | 2.3285 | 2.1584 | [8 empty] | 2.2777
21 | LMTD of Evaporator | ºC | [13 empty] | 1.441 | 1.6602 | 2.0745 | 1.6602 | [8 empty] | 1.709

## 20-02-2019 (hidden)
Performance Sheet Chiller
Date :- 20/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.7 | 1.8 | 1.8 | 1.8 | 1.9 | 1.7 | 1.6 | 1.6 | 1.6 | 1.5 | 1.6 | 1.6 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | [7 empty] | 1.6235
2 | Small temperature difference of evaporator | ºC |  | 1.3 | 1.4 | 1.3 | 1.4 | 1.1 | 0.5 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | [7 empty] | 0.65294
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.8 | 14 | 14.3 | 14.5 | 14.7 | 15.1 | 15 | 14.1 | 13.8 | 13.8 | 13.8 | 13.9 | 14 | 13.8 | 13.8 | 13.7 | 13.5 | [7 empty] | 14.0941
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.3 | 6.6 | 6.8 | 7.1 | 7.5 | 7.8 | 7.2 | 7 | 7.1 | 7 | 7.1 | 7 | 7 | 7 | 6.7 | 6.5 | [7 empty] | 6.9412
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 22.1 | 21.7 | 21.6 | 22.4 | 22.9 | 24.1 | 27.1 | 26.6 | 26.7 | 26.5 | 26.6 | 26.5 | 26.5 | 26.5 | 26.6 | 26.5 | 26.6 | [7 empty] | 25.1471
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.9 | 27.7 | 27.6 | 28.4 | 28.8 | 29.9 | 32.5 | 31.7 | 31.8 | 31.5 | 31.8 | 31.6 | 31.7 | 31.7 | 31.7 | 31.7 | 31.8 | [7 empty] | 30.5765
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2472.4537 | 2472.4537 | 2472.4537 | 2440.3439 | 2440.3439 | 2311.9048 | 2215.5754 | 2183.4656 | 2151.3558 | 2183.4656 | 2183.4656 | 2247.6852 | 2183.4656 | 2183.4656 | 2247.6852 | 2247.6852 | [7 empty] | 39045.5026
15 | Power Consumption of Chiller | KWH |  | 1400 | 1380 | 1380 | 1400 | 1390 | 1400 | 1390 | 1390 | 1380 | 1380 | 1380 | 1380 | 1400 | 1380 | 1380 | 1390 | 1400 | [7 empty] | 23600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58134 | 0.55815 | 0.55815 | 0.56624 | 0.56959 | 0.57369 | 0.60124 | 0.62738 | 0.63202 | 0.64146 | 0.63202 | 0.63202 | 0.62286 | 0.63202 | 0.63202 | 0.61841 | 0.62286 | [7 empty] | 0.60597
17 | Average iKW/TR |  |  | 0.60597 | [23 empty] | 0.60597
18 | COP of chiller |  |  | 6.0481 | 6.2994 | 6.2994 | 6.2094 | 6.1728 | 6.1287 | 5.848 | 5.6043 | 5.5631 | 5.4813 | 5.5631 | 5.5631 | 5.6449 | 5.5631 | 5.5631 | 5.6855 | 5.6449 | [7 empty] | 5.8166
19 | EER of Chiller |  |  | 20.6422 | 21.4998 | 21.4998 | 21.1927 | 21.0679 | 20.9174 | 19.9591 | 19.1274 | 18.9868 | 18.7076 | 18.9868 | 18.9868 | 19.266 | 18.9868 | 18.9868 | 19.4047 | 19.266 | [7 empty] | 19.852
20 | LMTD of Condenser | ºC |  | 3.9076 | 4.0918 | 4.0918 | 4.0918 | 4.1777 | 3.9076 | 3.6588 | 3.5612 | 3.5612 | 3.4099 | 3.5938 | 3.5612 | 3.4744 | 3.4744 | 3.4422 | 3.4744 | 3.3535 | [7 empty] | 3.6961
21 | LMTD of Evaporator | ºC |  | 3.9218 | 4.1137 | 3.9796 | 4.1137 | 3.675 | 2.7289 | 2.2368 | 2.3759 | 2.3526 | 2.3293 | 2.3526 | 2.1491 | 2.1931 | 2.3526 | 2.3526 | 2.3991 | 2.3991 | [7 empty] | 2.825
Performance Sheet Chiller
Date :- 20/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC | [6 empty] | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 1 | 1 | 1 | 0.9 | 0.8 | 0.9 | 0.8 | 0.9 | 0.87368
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.3 | 0.3 | 0.4 | 0.3 | 0.2 | 0.3 | 0.2 | 0.2 | 0.3 | 0.27895
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 17.7 | 15.3 | 14.3 | 14.1 | 14 | 14.1 | 14.1 | 14.1 | 14 | 14 | 13.8 | 13.7 | 12.8 | 13.1 | 14 | 14.6 | 14.7 | 14.8 | 15 | 14.3263
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 8.5 | 7.2 | 6.9 | 7 | 7 | 7 | 7 | 7.1 | 7 | 7.1 | 6.5 | 6 | 5.3 | 5.6 | 5.7 | 5.9 | 6.1 | 6.1 | 6.2 | 6.5895
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 23.7 | 27.5 | 26.9 | 27 | 26.7 | 27 | 26.8 | 26.7 | 26.8 | 26.9 | 26.7 | 26.9 | 26.8 | 26 | 25.2 | 25.2 | 24.9 | 24.9 | 24.8 | 26.1789
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 23.2 | 33.1 | 31.9 | 31.8 | 31.5 | 31.7 | 31.6 | 31.6 | 31.6 | 31.6 | 31.7 | 32.2 | 32 | 31.2 | 30.9 | 31.1 | 30.8 | 30.8 | 30.8 | 31.1105
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 2954.1005 | 2600.8929 | 2376.1243 | 2279.795 | 2247.6852 | 2279.795 | 2279.795 | 2247.6852 | 2247.6852 | 2215.5754 | 2344.0146 | 2472.4537 | 2408.2341 | 2408.2341 | 2665.1124 | 2793.5516 | 2761.4418 | 2793.5516 | 2825.6614 | 47201.3889
15 | Power Consumption of Chiller | KWH | [6 empty] | 1620 | 1550 | 1540 | 1550 | 1540 | 1520 | 1520 | 1520 | 1520 | 1510 | 1530 | 1530 | 1520 | 1550 | 1580 | 1640 | 1600 | 1560 | 1600 | 29500
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.54839 | 0.59595 | 0.64811 | 0.67989 | 0.68515 | 0.66673 | 0.66673 | 0.67625 | 0.67625 | 0.68154 | 0.65273 | 0.61882 | 0.63117 | 0.64363 | 0.59285 | 0.58707 | 0.57941 | 0.55843 | 0.56624 | 0.62923
17 | Average iKW/TR |  |  | 0.62923 | [23 empty] | 0.62923
18 | COP of chiller | [7 empty] | 6.4115 | 5.8998 | 5.425 | 5.1715 | 5.1317 | 5.2735 | 5.2735 | 5.1993 | 5.1993 | 5.1589 | 5.3866 | 5.6818 | 5.5706 | 5.4628 | 5.9307 | 5.9891 | 6.0683 | 6.2962 | 6.2094 | 5.6179
19 | EER of Chiller | [7 empty] | 21.8824 | 20.1361 | 18.5154 | 17.6502 | 17.5146 | 17.9985 | 17.9985 | 17.745 | 17.745 | 17.6074 | 18.3846 | 19.392 | 19.0125 | 18.6446 | 20.2415 | 20.4408 | 20.711 | 21.4891 | 21.1927 | 19.1738
20 | LMTD of Condenser | ºC | [6 empty] | 0.61658 | 2.693 | 2.524 | 2.4667 | 2.6005 | 2.5709 | 2.4667 | 2.4954 | 2.4667 | 2.5709 | 2.6591 | 2.8796 | 2.85 | 2.85 | 2.8608 | 2.7761 | 2.9175 | 2.7761 | 2.9457 | 2.5782
21 | LMTD of Evaporator | ºC | [6 empty] | 2.6626 | 2.4308 | 2.2803 | 2.215 | 2.1931 | 2.215 | 2.215 | 2.1931 | 1.9534 | 1.933 | 2.2586 | 2.3451 | 2.5141 | 2.302 | 2.2136 | 2.5579 | 2.2726 | 2.2922 | 2.5789 | 2.2961

## 21-02-2019 (hidden)
Date :- 21/02/2019
CHILLER NO. 2
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 1.6 | 1.6 | 1.2 | 1.2 | 1.2 | 1.5 | 1.6 | 1.7 | 1.7 | 1.6 | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | [7 empty] | 1.4733
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.7 | 0.7 | 0.3 | 0.3 | 0.3 | 0.6 | 0.7 | 0.8 | 0.9 | 0.9 | 0.9 | 0.5 | 0.7 | 0.6 | 0.4 | [7 empty] | 0.62
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 15.3 | 14.9 | 12.7 | 12.6 | 12.5 | 13.6 | 14.2 | 14.6 | 15.2 | 16.1 | 15.2 | 14.6 | 14.2 | 13.7 | 13.3 | [7 empty] | 14.18
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 8.5 | 8 | 7 | 7 | 7.1 | 7.2 | 7.1 | 7.1 | 7.7 | 8.6 | 7.7 | 7.3 | 7 | 6.3 | 6.1 | [7 empty] | 7.3133
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 21.2 | 25 | 24.7 | 25.2 | 25.2 | 25.2 | 25.4 | 25.4 | 25.3 | 26 | 26 | 26.1 | 26.2 | 24.9 | 26 | [7 empty] | 25.1867
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 26.6 | 30.3 | 29 | 29.3 | 29.3 | 30 | 30.8 | 31.2 | 31.1 | 31.8 | 31.6 | 31.7 | 31.6 | 30.5 | 31.4 | [7 empty] | 30.4133
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2183.4656 | 2215.5754 | 1830.2579 | 1798.1481 | 1733.9286 | 2055.0265 | 2279.795 | 2408.2341 | 2408.2341 | 2408.2341 | 2408.2341 | 2344.0146 | 2311.9048 | 2376.1243 | 2311.9048 | [7 empty] | 33073.082
15 | Power Consumption of Chiller | KWH |  |  |  | 1450 | 1410 | 1410 | 1410 | 1450 | 1470 | 1510 | 1500 | 1480 | 1530 | 1480 | 1470 | 1470 | 1490 | 1470 | [7 empty] | 22000
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.66408 | 0.6364 | 0.77038 | 0.78414 | 0.83625 | 0.71532 | 0.66234 | 0.62286 | 0.61456 | 0.63532 | 0.61456 | 0.62713 | 0.63584 | 0.62707 | 0.63584 | [7 empty] | 0.67214
17 | Average iKW/TR |  |  | Hours 7: 0.67214 | 0.67214
18 | COP of chiller |  |  |  |  | 5.2945 | 5.5248 | 4.564 | 4.4839 | 4.2045 | 4.9153 | 5.3084 | 5.6449 | 5.7212 | 5.5342 | 5.7212 | 5.6065 | 5.5297 | 5.607 | 5.5297 | [7 empty] | 5.2793
19 | EER of Chiller |  |  |  |  | 18.0702 | 18.8561 | 15.5768 | 15.3035 | 14.3499 | 16.7759 | 18.1177 | 19.266 | 19.5264 | 18.8883 | 19.5264 | 19.135 | 18.8729 | 19.1367 | 18.8729 | [7 empty] | 18.0183
20 | LMTD of Condenser | ºC |  |  |  | 3.6588 | 3.6264 | 2.8244 | 2.7602 | 2.7602 | 3.3448 | 3.6588 | 3.9076 | 3.9076 | 3.7872 | 3.6021 | 3.6021 | 3.4167 | 3.4795 | 3.4167 | [7 empty] | 3.4502
21 | LMTD of Evaporator | ºC |  |  |  | 2.8673 | 2.8933 | 1.9027 | 1.8799 | 1.834 | 2.6051 | 2.9451 | 3.206 | 3.3578 | 3.3578 | 3.3578 | 2.6572 | 2.9709 | 2.8568 | 2.4453 | [7 empty] | 2.7425
Date :- 21/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | [5 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1.1 | 1 | 1.1 | 1.2 | 1.2 | 1 | 0.96842
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.3 | 0.3 | 0.2 | [5 empty] | 0.5 | 0.5 | 0.5 | 0.4 | 0.5 | 0.5 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.5 | 0.5 | 0.42632
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15 | 15.2 | 15.5 | 15.1 | 12.9 | [5 empty] | 15.3 | 16.3 | 15.5 | 14.8 | 14.5 | 14 | 13.5 | 13 | 12.8 | 13.7 | 14.3 | 14.7 | 14.9 | 15.1 | 14.5316
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.3 | 6.3 | 6.6 | 7.8 | 7 | [5 empty] | 8.6 | 7.8 | 7.2 | 6.9 | 7 | 6.3 | 6 | 5.8 | 5.6 | 5.7 | 5.9 | 6.1 | 6.4 | 6.5 | 6.6211
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.6 | 24 | 24 | 25.3 | 24.9 | [5 empty] | 25.7 | 26.3 | 26.2 | 26.4 | 26.5 | 25.2 | 26.2 | 26.1 | 24.8 | 24.3 | 24.5 | 24.5 | 24.5 | 24.3 | 25.1737
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.7 | 30.1 | 30.2 | 30.1 | 28.8 | [5 empty] | 24.9 | 32.1 | 32 | 31.8 | 31.6 | 30.4 | 31.5 | 31.1 | 29.7 | 30 | 30.4 | 30.3 | 30.5 | 30.3 | 30.3421
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [5 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [5 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | [5 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | [5 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2793.5516 | 2857.7712 | 2857.7712 | 2344.0146 | 1894.4775 | [5 empty] | 2151.3558 | 2729.332 | 2665.1124 | 2536.6733 | 2408.2341 | 2472.4537 | 2408.2341 | 2311.9048 | 2311.9048 | 2568.7831 | 2697.2222 | 2761.4418 | 2729.332 | 2761.4418 | 48261.0119
15 | Power Consumption of Chiller | KWH |  | 1480 | 1530 | 1340 | 1310 | 1310 | [5 empty] | 1480 | 1500 | 1400 | 1420 | 1360 | 1400 | 1400 | 1400 | 1430 | 1430 | 1450 | 1500 | 1530 | 1530 | 27200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.52979 | 0.53538 | 0.4689 | 0.55887 | 0.69148 | [5 empty] | 0.68794 | 0.54959 | 0.52531 | 0.55979 | 0.56473 | 0.56624 | 0.58134 | 0.60556 | 0.61854 | 0.55668 | 0.53759 | 0.54319 | 0.56058 | 0.55406 | 0.56819
17 | Average iKW/TR |  |  | Hours 7: 0.56819 | 0.56819
18 | COP of chiller |  |  | 6.6366 | 6.5673 | 7.4985 | 6.2913 | 5.0847 | [5 empty] | 5.1109 | 6.3976 | 6.6932 | 6.2809 | 6.226 | 6.2094 | 6.0481 | 5.8062 | 5.6844 | 6.316 | 6.5403 | 6.4728 | 6.2721 | 6.3459 | 6.2359
19 | EER of Chiller |  |  | 22.6506 | 22.4141 | 25.5922 | 21.4721 | 17.3541 | [5 empty] | 17.4436 | 21.8349 | 22.844 | 21.4369 | 21.2493 | 21.1927 | 20.6422 | 19.8165 | 19.4008 | 21.5564 | 22.322 | 22.0917 | 21.4067 | 21.6586 | 21.2831
20 | LMTD of Condenser | ºC |  | 2.9738 | 2.9738 | 3.0018 | 2.6005 | 2.3298 | [5 empty] | 0.3641 | 2.8892 | 2.8892 | 2.7751 | 2.6883 | 2.7173 | 2.7462 | 2.7906 | 2.8884 | 2.9967 | 3.1882 | 3.2887 | 3.3487 | 3.0834 | 2.7649
21 | LMTD of Evaporator | ºC |  | 2.7844 | 2.8287 | 2.5999 | 2.2586 | 1.7263 | [5 empty] | 2.512 | 2.9408 | 2.8941 | 2.6051 | 2.7051 | 2.7527 | 2.302 | 2.4453 | 2.6332 | 2.8236 | 2.7175 | 2.9641 | 2.9408 | 2.9641 | 2.6525

## 22-02-2019 (hidden)
Date :- 22/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  |  | 1.9 | 1.8 | 1.8 | 1.8 | 1.8 | 1.7 | 1.6 | 1 | 1 | 1.7 | 1.6 | 1.7 | 1.8 | 1.7 | 1.7 | 1.7 | 1.8 | 2 | 1.9 | 1.8 | 2.1 | 2 | 1.9 | 2.2
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.5 | 0.3 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.38636
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 15.1 | 15.2 | 14 | 13.6 | 13.4 | 13.6 | 14 | 14.1 | 14.4 | 14.4 | 14.2 | 14.1 | 14 | 13.9 | 13.5 | 12.5 | 12.7 | 14 | 14.5 | 14.7 | 15.1 | 15.2 | 14.1
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 10.6 | 7.6 | 7 | 6.9 | 7 | 7.1 | 7.1 | 7.2 | 7.3 | 7.3 | 7.2 | 7.1 | 7.1 | 6.8 | 6.2 | 5.6 | 5.6 | 6.2 | 6.5 | 6.7 | 6.8 | 7.1 | 7
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 20.2 | 25.6 | 25.5 | 25.7 | 26 | 27.1 | 27.5 | 27.1 | 26.8 | 26.3 | 26 | 25.5 | 25.7 | 26.2 | 25.7 | 25.3 | 24.2 | 23.6 | 23.7 | 23.6 | 23.5 | 23.3 | 25.1864
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 25.3 | 30.4 | 30 | 30 | 30.1 | 31.3 | 31.8 | 31.6 | 31.4 | 31 | 30.5 | 30 | 30.1 | 30.7 | 30.3 | 29.7 | 28.8 | 28.5 | 28.8 | 28.7 | 28.7 | 28.7 | 29.8364
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 1444.9405 | 2440.3439 | 2247.6852 | 2151.3558 | 2055.0265 | 2087.1362 | 2215.5754 | 2215.5754 | 2279.795 | 2279.795 | 2247.6852 | 2247.6852 | 2215.5754 | 2279.795 | 2344.0146 | 2215.5754 | 2279.795 | 2504.5635 | 2568.7831 | 2568.7831 | 2665.1124 | 2600.8929 | 50155.4894
15 | Power Consumption of Chiller | KWH |  |  |  | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1500 | 1500 | 1500 | 1500 | 33600
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 1.0381 | 0.61467 | 0.66735 | 0.69723 | 0.72992 | 0.71869 | 0.67703 | 0.67703 | 0.65795 | 0.65795 | 0.66735 | 0.66735 | 0.72216 | 0.70182 | 0.68259 | 0.72216 | 0.70182 | 0.63883 | 0.58393 | 0.58393 | 0.56283 | 0.57673 | 0.67943
17 | Average iKW/TR |  |  | Hours 7: 0.67943 | 0.67943
18 | COP of chiller |  |  |  |  | 3.3869 | 5.7202 | 5.2686 | 5.0428 | 4.817 | 4.8922 | 5.1933 | 5.1933 | 5.3438 | 5.3438 | 5.2686 | 5.2686 | 4.8687 | 5.0098 | 5.151 | 4.8687 | 5.0098 | 5.5038 | 6.0212 | 6.0212 | 6.247 | 6.0965 | 5.2517
19 | EER of Chiller |  |  |  |  | 11.5596 | 19.5229 | 17.9816 | 17.211 | 16.4404 | 16.6972 | 17.7248 | 17.7248 | 18.2385 | 18.2385 | 17.9816 | 17.9816 | 16.617 | 17.0986 | 17.5803 | 16.617 | 17.0986 | 18.7844 | 20.5504 | 20.5504 | 21.3211 | 20.8073 | 17.924
20 | LMTD of Condenser | ºC |  |  |  | 3.9109 | 3.6943 | 3.5921 | 3.5231 | 3.4536 | 3.3753 | 3.2951 | 2.6397 | 2.6701 | 3.5454 | 3.3625 | 3.4778 | 3.5577 | 3.4778 | 3.5117 | 3.4438 | 3.6263 | 3.9568 | 3.9109 | 3.7954 | 4.1736 | 4.1274 | 3.551
21 | LMTD of Evaporator | ºC |  |  |  | 1.796 | 2.5369 | 2.3991 | 2.1271 | 2.0605 | 2.0827 | 2.3759 | 2.5607 | 2.6091 | 2.6091 | 2.1931 | 2.3991 | 2.1711 | 2.4222 | 2.4683 | 2.3759 | 2.4222 | 2.5824 | 2.4095 | 2.6277 | 2.6951 | 2.6502 | 2.3897
Date :- 22/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.1 | 1 | 0.9 | 0.9 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 0.9 | 0.8 | 1 | 0.9 | [7 empty] | 0.93529
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | [7 empty] | 0.40588
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.2 | 15.2 | 15.6 | 15.2 | 14 | 13.6 | 13.5 | 13.6 | 14 | 14.1 | 14.4 | 14.4 | 14.3 | 14.2 | 14 | 14 | 13.5 | [7 empty] | 14.2824
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.5 | 6.7 | 6.9 | 7.1 | 6.8 | 7 | 6.8 | 7 | 7 | 7.1 | 7 | 7.1 | 7 | 7 | 7 | 6.1 | 5.7 | [7 empty] | 6.8118
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.2 | 24.3 | 24.2 | 25.7 | 25.6 | 25.8 | 26 | 27.1 | 27.5 | 27.2 | 26.8 | 26.5 | 26 | 25.5 | 25.7 | 26.2 | 25.7 | [7 empty] | 25.8824
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.2 | 30.3 | 30.2 | 31.5 | 30.6 | 30.3 | 30.5 | 31.7 | 32.3 | 32 | 32 | 31.6 | 31.2 | 30.5 | 30.6 | 31.8 | 31.2 | [7 empty] | 31.0882
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2793.5516 | 2729.332 | 2793.5516 | 2600.8929 | 2311.9048 | 2119.246 | 2151.3558 | 2119.246 | 2247.6852 | 2247.6852 | 2376.1243 | 2344.0146 | 2344.0146 | 2311.9048 | 2247.6852 | 2536.6733 | 2504.5635 | [7 empty] | 40779.4312
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1300 | 1300 | 1200 | 1200 | 1200 | 1200 | 1200 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | [7 empty] | 21600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.46536 | 0.47631 | 0.46536 | 0.49983 | 0.51905 | 0.56624 | 0.55779 | 0.56624 | 0.53388 | 0.57837 | 0.54711 | 0.5546 | 0.5546 | 0.56231 | 0.57837 | 0.51248 | 0.51905 | [7 empty] | 0.53276
17 | Average iKW/TR |  |  | Hours 7: 0.53276 | 0.53276
18 | COP of chiller |  |  | 7.5555 | 7.3818 | 7.5555 | 7.0344 | 6.7739 | 6.2094 | 6.3035 | 6.2094 | 6.5857 | 6.0791 | 6.4265 | 6.3397 | 6.3397 | 6.2528 | 6.0791 | 6.8607 | 6.7739 | [7 empty] | 6.633
19 | EER of Chiller |  |  | 25.7869 | 25.1941 | 25.7869 | 24.0085 | 23.1193 | 21.1927 | 21.5138 | 21.1927 | 22.4771 | 20.748 | 21.9337 | 21.6373 | 21.6373 | 21.3409 | 20.748 | 23.4157 | 23.1193 | [7 empty] | 22.6383
20 | LMTD of Condenser | ºC |  | 3.2175 | 3.0834 | 2.9457 | 2.8892 | 2.7906 | 2.5115 | 2.5115 | 2.5413 | 2.6005 | 2.6005 | 2.7173 | 2.8203 | 2.85 | 2.6591 | 2.4954 | 2.9676 | 2.8037 | [7 empty] | 2.765
21 | LMTD of Evaporator | ºC |  | 3.1742 | 3.126 | 2.9873 | 2.6502 | 2.2368 | 2.1049 | 2.1271 | 2.3059 | 2.3991 | 2.3991 | 2.2803 | 2.4683 | 2.4683 | 2.4453 | 2.3991 | 2.6051 | 2.5824 | [7 empty] | 2.5153

## 23-02-2019 (hidden)
Date :- 23/01/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.1; Hours 8: 1.1; Hours 9: 1.9; Hours 10: 1.7; Hours 16: 1.9; Hours 17: 1.9; Hours 18: 1.8; Hours 19: 1.7; Hours 20: 1.9; Hours 21: 1.9; Hours 22: 1.7; Hours 23: 1.8 | 1.7
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.4; Hours 10: 0.3; Hours 16: 0.4; Hours 17: 0.4; Hours 18: 0.4; Hours 19: 0.5; Hours 20: 0.3; Hours 21: 0.4; Hours 22: 0.4; Hours 23: 0.4 | 0.40833
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 15.3; Hours 8: 15.5; Hours 9: 16; Hours 10: 15.6; Hours 16: 15.7222; Hours 17: 15.7222; Hours 18: 15.7222; Hours 19: 15.4444; Hours 20: 15; Hours 21: 14.5; Hours 22: 14.1667; Hours 23: 13.7222 | 15.2
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 7; Hours 8: 7.1; Hours 9: 7.6; Hours 10: 8; Hours 16: 7.8889; Hours 17: 7.8889; Hours 18: 7.8889; Hours 19: 7.7222; Hours 20: 7.5; Hours 21: 7; Hours 22: 6.6667; Hours 23: 6.4444 | 7.3917
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 23.6; Hours 8: 23.1; Hours 9: 23.3; Hours 10: 26.2; Hours 16: 25.6667; Hours 17: 25.6667; Hours 18: 25.6667; Hours 19: 26.1111; Hours 20: 26; Hours 21: 24.9444; Hours 22: 24.8333; Hours 23: 24.7778 | 24.9889
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 28.8; Hours 8: 28.4; Hours 9: 28.7; Hours 10: 31.1; Hours 16: 30.6111; Hours 17: 30.6111; Hours 18: 30.6111; Hours 19: 31; Hours 20: 30.7778; Hours 21: 29.8889; Hours 22: 29.5; Hours 23: 29.4444 | 29.9537
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4.3; Hours 8: 4.3; Hours 9: 4.3; Hours 10: 4.3; Hours 16: 4.3; Hours 17: 4.3; Hours 18: 4.3; Hours 19: 4.3; Hours 20: 4.3; Hours 21: 4.3; Hours 22: 4.3; Hours 23: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 10: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 10: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2665.1124; Hours 8: 2697.2222; Hours 9: 2697.2222; Hours 10: 2440.3439; Hours 16: 2515.266; Hours 17: 2515.266; Hours 18: 2515.266; Hours 19: 2479.5875; Hours 20: 2408.2341; Hours 21: 2408.2341; Hours 22: 2408.2351; Hours 23: 2336.8785 | 30086.8682
15 | Power Consumption of Chiller | KWH |  | 1600 | 1500 | 1400 | 1200 |  | 0 | 0 | 0 | 0 | 1100 | 1400 | 1600 | 1500 | 1500 | 1400 | 1500 | 800 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16500
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.60035; Hours 8: 0.55613; Hours 9: 0.51905; Hours 10: 0.49173; Hours 16: 0.43733; Hours 17: 0.5566; Hours 18: 0.63612; Hours 19: 0.60494; Hours 20: 0.62286; Hours 21: 0.58134; Hours 22: 0.62286; Hours 23: 0.34234 | 0.54764
17 | Average iKW/TR |  |  | Hours 7: 0.54764 | 0.54764
18 | COP of chiller |  |  | Hours 7: 5.8566; Hours 8: 6.3223; Hours 9: 6.7739; Hours 10: 7.1502; Hours 16: 8.0397; Hours 17: 6.3169; Hours 18: 5.5273; Hours 19: 5.8122; Hours 20: 5.6449; Hours 21: 6.0481; Hours 22: 5.6449; Hours 23: 10.2706 | 6.6173
19 | EER of Chiller |  |  | Hours 7: 19.9885; Hours 8: 21.578; Hours 9: 23.1193; Hours 10: 24.4037; Hours 16: 27.4395; Hours 17: 21.5596; Hours 18: 18.8647; Hours 19: 19.8369; Hours 20: 19.266; Hours 21: 20.6422; Hours 22: 19.2661; Hours 23: 35.0535 | 22.5848
20 | LMTD of Condenser | ºC |  | Hours 7: 2.9795; Hours 8: 3.0097; Hours 9: 4.0118; Hours 10: 3.6124; Hours 16: 3.8581; Hours 17: 3.8581; Hours 18: 3.7431; Hours 19: 3.6087; Hours 20: 3.8011; Hours 21: 3.8581; Hours 22: 3.5342; Hours 23: 3.649 | 3.627
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.8941; Hours 8: 2.9175; Hours 9: 2.7175; Hours 10: 2.3236; Hours 16: 2.59; Hours 17: 2.59; Hours 18: 2.59; Hours 19: 2.7579; Hours 20: 2.302; Hours 21: 2.5141; Hours 22: 2.5141; Hours 23: 2.4632 | 2.5978
Date :- 23/01/2019
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  |  | 1.9 | 1.9 | 1.8 | 1.4 | 1.8 | 1.8 | 1.7 | 1.7 | 1.9 | 1.8 | 1.7 | 1.7 | 1.8 | 1.7 | 1.8 | 1.7 | 1.9 | 1.9 | 1.8 | 1.7 | 1.8 | 2 | 2.1 | 1.7957
2 | Small temperature difference of evaporator | ºC |  |  | 0.4 | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.3 | 0.4 | 0.4 | 0.5 | 0.3 | 0.4 | 0.5 | 0.3 | 0.4 | 0.4 | 0.39565
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  | 15.6 | 15.6 | 15.6 | 14.5 | 13 | 12.3 | 12.8 | 13.5 | 14 | 14.3 | 15.5 | 15.5 | 14.9 | 14.4 | 14.1 | 13.7 | 12.5 | 12.2 | 12.3 | 13.6 | 13.8 | 14.1 | 14.1 | 13.9957
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  | 7.6 | 7.6 | 7.6 | 7 | 7 | 5.5 | 5.6 | 5.8 | 6.2 | 6.3 | 7.9 | 7.7 | 7.3 | 7.1 | 6.6 | 6.5 | 5.4 | 5.3 | 5.3 | 5.6 | 5.5 | 5.5 | 5.6 | 6.413
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  | 26 | 26 | 26 | 25.1 | 24.7 | 23.3 | 23.7 | 25 | 24.9 | 24.5 | 25.2 | 25.9 | 26 | 24.8 | 24.6 | 24.5 | 23.5 | 23.5 | 21.9 | 21 | 20.6 | 20.2 | 20 | 23.9522
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  | 31.6 | 31.6 | 31.6 | 30.2 | 29 | 28.2 | 28.6 | 30.3 | 30.4 | 30 | 30.8 | 31.5 | 31.1 | 30.1 | 30 | 29.8 | 28.5 | 28.3 | 26.7 | 26.2 | 26 | 26 | 25.6 | 29.2217
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  | 2568.7831 | 2568.7831 | 2568.7831 | 2408.2341 | 1926.5873 | 2183.4656 | 2311.9048 | 2472.4537 | 2504.5635 | 2568.7831 | 2440.3439 | 2504.5635 | 2440.3439 | 2344.0146 | 2408.2341 | 2311.9048 | 2279.795 | 2215.5754 | 2247.6852 | 2568.7831 | 2665.1124 | 2761.4418 | 2729.332 | 55999.4709
15 | Power Consumption of Chiller | KWH |  |  | 1500 | 1500 | 1300 | 1200 | 1500 | 1400 | 1500 | 1600 | 1500 | 1300 | 1600 | 1400 | 1400 | 1400 | 1400 | 1300 | 1200 | 1400 | 1500 | 1500 | 1300 | 1500 | 1500 | 32700
16 | Specific power consumption of Chiller | (iKW/TR) |  |  | 0.58393 | 0.58393 | 0.50608 | 0.49829 | 0.77858 | 0.64118 | 0.64882 | 0.64713 | 0.59891 | 0.50608 | 0.65565 | 0.55898 | 0.57369 | 0.59727 | 0.58134 | 0.56231 | 0.52636 | 0.63189 | 0.66735 | 0.58393 | 0.48778 | 0.54319 | 0.54959 | 0.58749
17 | Average iKW/TR |  |  | Hours 7: 0.58749 | 0.58749
18 | COP of chiller |  |  |  | 6.0212 | 6.0212 | 6.9476 | 7.0561 | 4.5159 | 5.4836 | 5.4191 | 5.4332 | 5.8707 | 6.9476 | 5.3627 | 6.29 | 6.1287 | 5.8868 | 6.0481 | 6.2528 | 6.6798 | 5.5643 | 5.2686 | 6.0212 | 7.2081 | 6.4728 | 6.3976 | 6.0564
19 | EER of Chiller |  |  |  | 20.5504 | 20.5504 | 23.7121 | 24.0826 | 15.4128 | 18.7156 | 18.4954 | 18.5436 | 20.0367 | 23.7121 | 18.3027 | 21.4679 | 20.9174 | 20.0917 | 20.6422 | 21.3409 | 22.7982 | 18.9908 | 17.9816 | 20.5504 | 24.6013 | 22.0917 | 21.8349 | 20.6706
20 | LMTD of Condenser | ºC |  |  | 4.0785 | 4.0785 | 3.9613 | 3.3218 | 3.5231 | 3.7282 | 3.6124 | 3.7448 | 4.0452 | 3.9283 | 3.8429 | 3.8429 | 3.7954 | 3.7448 | 3.8953 | 3.7448 | 3.877 | 3.8088 | 3.6943 | 3.7119 | 3.8953 | 4.2616 | 4.3101 | 3.8455
21 | LMTD of Evaporator | ºC |  |  | 2.6277 | 2.6277 | 2.6277 | 2.302 | 2.164 | 2.3526 | 2.4453 | 2.5597 | 2.5824 | 2.6277 | 2.5369 | 2.5824 | 2.7289 | 2.2586 | 2.5141 | 2.4453 | 2.6091 | 2.1711 | 2.3991 | 2.8236 | 2.4734 | 2.7622 | 2.7399 | 2.5201

## 24-02-2019 (hidden)
Date :- 24/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [6 empty] | 1.1 | 0.9 | 0.9 | 1 | 1 | 0.9 | 0.9 | 0.9 | 1.1 | 1.8 | 0.9 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1 | 1.1 | 1.1 | 1.0526
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.7 | 0.6 | 0.6 | 0.6 | 0.4 | 0.5 | 0.6 | 0.4 | 0.7 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.7 | 0.8 | 0.8 | 0.64737
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 15.8 | 15.7778 | 14.6667 | 14.4444 | 14.3889 | 14.2778 | 14.2778 | 14.1667 | 14.2778 | 13.9444 | 13.5556 | 12.5556 | 12.4444 | 13.3333 | 13.6111 | 13.8889 | 14 | 14.1111 | 14.1111 | 14.086
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 9 | 8.2778 | 8 | 8 | 8.1111 | 8.1111 | 8 | 8.1111 | 8.1111 | 6.1111 | 5.8889 | 5.7222 | 5.6111 | 5.6111 | 5.6111 | 5.6111 | 5.6111 | 5.6111 | 5.6111 | 6.8801
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 22.9444 | 24.3889 | 23.9444 | 24.5556 | 23.4444 | 23.1111 | 22.8889 | 22.8333 | 23.6111 | 22.9444 | 22.6111 | 22.1667 | 20.9444 | 19.9444 | 19.9444 | 20.5 | 21.4444 | 22.4444 | 21.3333 | 22.4211
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 25.8889 | 29.4444 | 28.5 | 28.9444 | 27.6111 | 27.2778 | 27.0556 | 27 | 27.7778 | 28.2778 | 28 | 27 | 25.6111 | 25.2778 | 25.5 | 26.2778 | 27.2778 | 28.3333 | 27.2222 | 27.2778
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 2183.4656 | 2408.2344 | 2140.6533 | 2069.2957 | 2015.7816 | 1980.1044 | 2015.7816 | 1944.4272 | 1980.1044 | 2515.2654 | 2461.7522 | 2194.1704 | 2194.171 | 2479.5885 | 2568.7831 | 2657.9776 | 2693.6548 | 2729.332 | 2729.332 | 43961.875
15 | Power Consumption of Chiller | KWH | [6 empty] | 1310 | 1310 | 1300 | 1300 | 1280 | 1280 | 1280 | 1290 | 1320 | 1370 | 1310 | 1310 | 1320 | 1320 | 1370 | 1360 | 1390 | 1390 | 1390 | 25200
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.59996 | 0.54397 | 0.60729 | 0.62823 | 0.63499 | 0.64643 | 0.63499 | 0.66343 | 0.66663 | 0.54467 | 0.53214 | 0.59704 | 0.60159 | 0.53235 | 0.53333 | 0.51167 | 0.51603 | 0.50928 | 0.50928 | 0.57965
17 | Average iKW/TR |  |  | Hours 7: 0.57965 | 0.57965
18 | COP of chiller | [7 empty] | 5.8604 | 6.4636 | 5.7896 | 5.5966 | 5.5371 | 5.4391 | 5.5371 | 5.2997 | 5.2743 | 6.4552 | 6.6073 | 5.8891 | 5.8445 | 6.6047 | 6.5926 | 6.8717 | 6.8136 | 6.9038 | 6.9038 | 6.1202
19 | EER of Chiller | [7 empty] | 20.0014 | 22.0604 | 19.7601 | 19.1014 | 18.8981 | 18.5636 | 18.8981 | 18.0879 | 18.0011 | 22.0317 | 22.5506 | 20.0995 | 19.9472 | 22.5419 | 22.5005 | 23.453 | 23.2548 | 23.5628 | 23.5628 | 20.8882
20 | LMTD of Condenser | ºC | [6 empty] | 2.2614 | 2.6753 | 2.5281 | 2.6057 | 2.5372 | 2.4112 | 2.4112 | 2.4112 | 2.6606 | 3.8732 | 2.7719 | 2.868 | 2.8167 | 3.0197 | 3.0862 | 3.0192 | 3.0353 | 3.1849 | 3.1849 | 2.8085
21 | LMTD of Evaporator | ºC | [6 empty] | 2.8673 | 2.8816 | 2.673 | 2.6164 | 2.2301 | 2.3807 | 2.5738 | 2.1773 | 2.7007 | 2.9638 | 2.9228 | 2.876 | 2.876 | 3.1043 | 3.3363 | 3.4079 | 3.2721 | 3.4649 | 3.4649 | 2.8837
Date :- 25/12/2018
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 2.3 | 2.2 | 2.2 | 2.1 | 2 | 1.9 | 1.8 | 1.4 | 1.8 | 1.8 | 1.4 | 1.5 | 1.6 | 1.8 | 1.8 | 1.7 | [8 empty] | 1.8313
2 | Small temperature difference of evaporator | ºC |  | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.1 | 0.2 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.2 | [8 empty] | 0.33125
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.1 | 14.1 | 14.2 | 14.6 | 14.7 | 15.2 | 15.6 | 14.6 | 14.1 | 14.2 | 14.1 | 14.2 | 14.2 | 14.1 | 14.2 | 13.3 | [8 empty] | 14.3437
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.6 | 5.6 | 5.8 | 6.1 | 6.3 | 8 | 8 | 8 | 7.8 | 8 | 8 | 8 | 8.2 | 7.1 | 6 | [8 empty] | 7.0062
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.6 | 21.5 | 20.9 | 20.8 | 21.2 | 21.6 | 23.8 | 23.7 | 24.2 | 23.3 | 22.9 | 22.7 | 22.7 | 23.4 | 23.1 | 22.2 | [8 empty] | 22.4125
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.7 | 27.1 | 26.7 | 26.7 | 27.2 | 27.5 | 29.2 | 28.3 | 28.7 | 27.6 | 27.1 | 26.9 | 26.8 | 27.3 | 28.1 | 27.6 | [8 empty] | 27.4688
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2729.332 | 2729.332 | 2761.4418 | 2825.6614 | 2761.4418 | 2857.7712 | 2440.3439 | 2119.246 | 1958.6971 | 2055.0265 | 1958.6971 | 1990.8069 | 1990.8069 | 1894.4775 | 2279.795 | 2344.0146 | [8 empty] | 37696.8915
15 | Power Consumption of Chiller | KWH |  | 1250 | 1290 | 1300 | 1270 | 1300 | 1210 | 1200 | 1180 | 1140 | 1140 | 1140 | 1140 | 1140 | 1200 | 1230 | 1170 | [8 empty] | 19300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.45799 | 0.47264 | 0.47077 | 0.44945 | 0.47077 | 0.42341 | 0.49173 | 0.5568 | 0.58202 | 0.55474 | 0.58202 | 0.57263 | 0.57263 | 0.63342 | 0.53952 | 0.49914 | [8 empty] | 0.52061
17 | Average iKW/TR |  |  | Hours 7: 0.52061 | 0.52061
18 | COP of chiller |  |  | 7.6771 | 7.439 | 7.4686 | 7.8229 | 7.4686 | 8.3041 | 7.1502 | 6.3146 | 6.041 | 6.3381 | 6.041 | 6.1401 | 6.1401 | 5.5508 | 6.5169 | 7.0441 | [8 empty] | 6.8411
19 | EER of Chiller |  |  | 26.2018 | 25.3894 | 25.4905 | 26.6994 | 25.4905 | 28.3418 | 24.4037 | 21.5518 | 20.618 | 21.6321 | 20.618 | 20.9561 | 20.9561 | 18.9449 | 22.2421 | 24.0414 | [8 empty] | 23.3486
20 | LMTD of Condenser | ºC |  | 4.7093 | 4.4245 | 4.4927 | 4.4112 | 4.3281 | 4.1777 | 3.8953 | 3.1609 | 3.5921 | 3.5231 | 3.0297 | 3.1461 | 3.2272 | 3.3834 | 3.7618 | 3.7776 | [8 empty] | 3.815
21 | LMTD of Evaporator | ºC |  | 2.7399 | 2.7399 | 2.9641 | 3.0104 | 2.7622 | 2.8287 | 2.3236 | 1.5697 | 1.7681 | 2.0605 | 1.9933 | 2.0158 | 2.2116 | 1.9481 | 2.215 | 2.0142 | [8 empty] | 2.3228

## 25-02-2019 (hidden)
Date :- 25/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [9 empty] | 1.7 | 1.6 | 1.4 | 1.4 | 1.6 | 1.7 | 1.5 | 1.5 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.8 | 1.9 | 1.8 | 1.7125
2 | Small temperature difference of evaporator | ºC | [9 empty] | 0.4 | 0.4 | 0.3 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.41875
3 | Entering Chilled Water Temp. (tchwe) | ºC | [9 empty] | 13.2222 | 15.7222 | 15 | 14.7222 | 14.3889 | 14.1667 | 13.7778 | 13.2222 | 12.5556 | 11.9444 | 13.0556 | 13.5556 | 14 | 14.2778 | 14.5556 | 14.7222 | 13.9306
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [9 empty] | 9 | 8.5556 | 7.9444 | 7.9444 | 8.1667 | 7.3889 | 7 | 6.1111 | 5.7222 | 5.5 | 5.5 | 5.7222 | 5.9444 | 6.1667 | 6.3333 | 6.5 | 6.8438
5 | Entering Condenser Water Temp. (tcwe) | ºC | [9 empty] | 19.7778 | 23.9444 | 25.3889 | 24.2222 | 24.1111 | 22.9444 | 23.1111 | 24.5556 | 25.2222 | 23.2778 | 21.8889 | 23.0556 | 23.4444 | 23.8333 | 24.5 | 24.1667 | 23.5903
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [9 empty] | 25.5556 | 28.5556 | 29.7778 | 28.4444 | 28.0556 | 27.1667 | 27.3889 | 29.0556 | 29.5556 | 27.4444 | 26.6667 | 28.1667 | 28.6667 | 29.0556 | 29.7222 | 29.5 | 28.2986
7 | Chilled water inlet pressure | (Kg/Cm2) | [9 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [9 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [9 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [9 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [9 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [9 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [9 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [9 empty] | 1355.7459 | 2301.2006 | 2265.5241 | 2176.3295 | 1997.9426 | 2176.3311 | 2176.3308 | 2283.362 | 2194.1704 | 2069.2957 | 2426.074 | 2515.2683 | 2586.6217 | 2604.4615 | 2640.1394 | 2640.1374 | 36408.9352
15 | Power Consumption of Chiller | KWH | [9 empty] | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 1475 | 23600
16 | Specific power consumption of Chiller | (iKW/TR) | [9 empty] | 1.088 | 0.64097 | 0.65106 | 0.67775 | 0.73826 | 0.67775 | 0.67775 | 0.64598 | 0.67224 | 0.7128 | 0.60798 | 0.58642 | 0.57024 | 0.56634 | 0.55868 | 0.55868 | 0.66443
17 | Average iKW/TR |  |  | Hours 7: 0.66443 | 0.66443
18 | COP of chiller |  |  | Hours 15: 3.2317; Hours 16: 5.4854; Hours 17: 5.4004; Hours 18: 5.1878; Hours 19: 4.7626; Hours 20: 5.1878 | 4.8759
19 | EER of Chiller |  |  | Hours 15: 11.0299; Hours 16: 18.7218; Hours 17: 18.4315; Hours 18: 17.7059; Hours 19: 16.2546; Hours 20: 17.7059 | 16.6416
20 | LMTD of Condenser | ºC |  | Hours 15: 3.9005; Hours 16: 3.3997; Hours 17: 3.0919; Hours 18: 3.037; Hours 19: 3.1739; Hours 20: 3.383 | 3.331
21 | LMTD of Evaporator | ºC |  | Hours 15: 1.7254; Hours 16: 2.4376; Hours 17: 2.2053; Hours 18: 2.3475; Hours 19: 2.2169; Hours 20: 2.5309 | 2.2439
Date :- 25/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.2 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0.9 | 0.9 | 0.9 | 0.9 | 1.1 | 1.1 | 0.9 | [8 empty] | 1.0875
2 | Small temperature difference of evaporator | ºC |  | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.4 | 0.4 | 0.6 | 0.4 | 0.3 | [8 empty] | 0.64375
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14 | 13.8889 | 14.1111 | 14.2222 | 14.2222 | 14.5556 | 14.7778 | 15.1111 | 15.4444 | 15.7778 | 15 | 14.8333 | 14.3889 | 14.2778 | 13.8333 | 13.2778 | [8 empty] | 14.4826
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.5 | 5.5 | 5.6111 | 5.5556 | 5.5556 | 5.6667 | 5.7778 | 6.2222 | 6.5556 | 7.7222 | 8.0556 | 7.8889 | 7.8889 | 8.2222 | 7.0556 | 5.9444 | [8 empty] | 6.5451
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 20.7778 | 19.7778 | 19.4444 | 20.7222 | 20.8333 | 20.3889 | 20.5 | 22.4444 | 23.2778 | 24.1111 | 25.3889 | 24.2222 | 24.2222 | 23.3333 | 23.2222 | 24.8333 | [8 empty] | 22.3438
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.7778 | 25.5556 | 25.4444 | 26.6667 | 26.7778 | 26.5556 | 26.7778 | 28.6667 | 29.5 | 29.7222 | 30.3333 | 29 | 28.6667 | 27.4444 | 27.8333 | 30 | [8 empty] | 27.8576
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [8 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [8 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2729.3317 | 2693.6545 | 2729.332 | 2782.8475 | 2782.8475 | 2854.2047 | 2889.8813 | 2854.2028 | 2854.2022 | 2586.6223 | 2229.8466 | 2229.8453 | 2087.1366 | 1944.4269 | 2176.3289 | 2354.7183 | [8 empty] | 40779.429
15 | Power Consumption of Chiller | KWH |  | 1240 | 1280 | 1240 | 1240 | 1240 | 1320 | 1250 | 1330 | 1240 | 1150 | 1150 | 1050 | 1050 | 1100 | 1210 | 1210 | [8 empty] | 19300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.45432 | 0.47519 | 0.45432 | 0.44559 | 0.44559 | 0.46248 | 0.43254 | 0.46598 | 0.43445 | 0.4446 | 0.51573 | 0.47088 | 0.50308 | 0.56572 | 0.55598 | 0.51386 | [8 empty] | 0.47752
17 | Average iKW/TR |  |  | Hours 7: 0.47752 | 0.47752
18 | COP of chiller |  |  | 7.739 | 7.3991 | 7.739 | 7.8907 | 7.8907 | 7.6026 | 8.1287 | 7.5454 | 8.093 | 7.9083 | 6.8175 | 7.4668 | 6.9889 | 6.2151 | 6.3239 | 6.8423 | [8 empty] | 7.4119
19 | EER of Chiller |  |  | 26.4131 | 25.2532 | 26.4131 | 26.931 | 26.931 | 25.9475 | 27.7431 | 25.7524 | 27.6216 | 26.9911 | 23.2682 | 25.4842 | 23.8532 | 21.2121 | 21.5836 | 23.3528 | [8 empty] | 25.297
20 | LMTD of Condenser | ºC |  | 3.3487 | 3.2821 | 3.2175 | 3.3321 | 3.3321 | 3.3983 | 3.4312 | 3.4148 | 3.4148 | 2.8355 | 2.6429 | 2.5939 | 2.4949 | 2.643 | 2.7995 | 2.7077 | [8 empty] | 3.0555
21 | LMTD of Evaporator | ºC |  | 3.6231 | 3.5939 | 3.4649 | 3.5075 | 3.5075 | 3.3962 | 3.4236 | 3.3962 | 3.3962 | 3.0182 | 2.7431 | 2.3862 | 2.2825 | 2.5166 | 2.3475 | 2.2658 | [8 empty] | 3.0543

## 26-02-2019 (hidden)
Performance Sheet Chiller
Date :- 26/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  | 1.8 | 2 | 1.6 | 1.7 | [8 empty] | 1.7 | 1.7 | 1.6 | 1.6 | 1.4 | [7 empty] | 1.6778
2 | Small temperature difference of evaporator | ºC |  | 0.5 | 0.6 | 0.4 | 0.4 | [8 empty] | 0.4 | 0.3 | 0.6 | 0.6 | 0.6 | [7 empty] | 0.48889
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.8889 | 14.8889 | 15.5 | 15.0556 | [8 empty] | 13.6111 | 15.5556 | 14.4444 | 13.9444 | 13.2222 | [7 empty] | 14.5679
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.4444 | 6.5556 | 7 | 7.8889 | [8 empty] | 8.5 | 8 | 6.3889 | 6.2778 | 5.7778 | [7 empty] | 6.9815
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.0556 | 24 | 24.1111 | 25.3333 | [8 empty] | 18.0556 | 24.6667 | 25.1667 | 25.2222 | 25.2778 | [7 empty] | 23.9877
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.3889 | 29.5556 | 29.6111 | 29.7778 | [8 empty] | 24.5 | 29.2778 | 30.0556 | 29.9444 | 30.0556 | [7 empty] | 29.1296
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | [8 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | [8 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | [8 empty] | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | [8 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | [8 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | [8 empty] | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2711.4937 | 2675.8162 | 2729.332 | 2301.2029 | [8 empty] | 1641.1666 | 2426.074 | 2586.6204 | 2461.7489 | 2390.3942 | [7 empty] | 21923.849
15 | Power Consumption of Chiller | KWH |  | 1460 | 1360 | 1270 | 1450 | [8 empty] | 1270 | 1270 | 1300 | 1360 | 1360 | [7 empty] | 12100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.53845 | 0.50826 | 0.46532 | 0.63011 | [8 empty] | 0.77384 | 0.52348 | 0.50259 | 0.55245 | 0.56894 | [7 empty] | 0.5626
17 | Average iKW/TR |  |  | 0.5626 | [23 empty] | 0.5626
18 | COP of chiller |  |  | 6.5299 | 6.9178 | 7.5562 | 5.58 | [8 empty] | 4.5436 | 6.7166 | 6.9958 | 6.3643 | 6.1799 | [7 empty] | 6.376
19 | EER of Chiller |  |  | 22.2865 | 23.6104 | 25.7892 | 19.0446 | [8 empty] | 15.5072 | 22.9237 | 23.8767 | 21.7215 | 21.0919 | [7 empty] | 21.7613
20 | LMTD of Condenser | ºC |  | 3.8732 | 4.1798 | 3.691 | 3.4589 | [8 empty] | 4.1134 | 3.5154 | 3.4918 | 3.4367 | 3.2185 | [7 empty] | 3.6643
21 | LMTD of Evaporator | ºC |  | 2.9278 | 3.0857 | 2.7399 | 2.4376 | [8 empty] | 1.9485 | 2.314 | 3.0182 | 2.9228 | 2.8679 | [7 empty] | 2.6958
Performance Sheet Chiller
Date :- 26/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | 25:00 | 26:00 | 27:00 | 28:00 | 29:00 | 30:00
1 | Small temperature difference of condenser | ºC |  |  |  | 1 | 1.1 | 1 | 1.1 | 1 | 1.1 | 1.2 | 1.1 | 1 | 1.3 | 1 | 1 | 1.1 | 1.1 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0818
2 | Small temperature difference of evaporator | ºC |  |  |  | 0.6 | 0.5 | 0.4 | 0.5 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.3 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.5 | 0.6 | 0.6 | 0.5
3 | Entering Chilled Water Temp. (tchwe) | ºC |  |  |  | 15.6111 | 15.1111 | 13.8889 | 12.2222 | 12.4444 | 12.5556 | 12.8889 | 12.9444 | 13.0556 | 14.6111 | 15.5 | 15.5 | 14.5 | 14.0556 | 13.3333 | 12.6667 | 12.9444 | 14.1111 | 14.5556 | 14.7778 | 14.8889 | 14.7778 | 13.952
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  |  |  | 8.9 | 7.8333 | 5.8889 | 5.3333 | 5.5556 | 5.4444 | 5.5556 | 5.5 | 5.6111 | 5.8333 | 6.5 | 7.8889 | 6.2222 | 6 | 5.5556 | 5.3333 | 5.7778 | 5.7778 | 5.7778 | 5.7778 | 5.8889 | 5.7778 | 6.0788
5 | Entering Condenser Water Temp. (tcwe) | ºC |  |  |  | 24.1111 | 25.3333 | 25.2222 | 23.3333 | 22.0556 | 21.3889 | 20.6667 | 21.4444 | 22.1111 | 24 | 24.2222 | 24.7222 | 25.1667 | 25.1667 | 25.3889 | 25 | 23.7778 | 24 | 24.3889 | 23.9444 | 23.6111 | 23.6111 | 23.7576
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  |  |  | 23.4444 | 30.5 | 30.8889 | 28 | 26.7222 | 26.1667 | 25.6667 | 26.5556 | 27.2222 | 30.1667 | 30.4444 | 29.9444 | 30.7778 | 30.7778 | 30.7778 | 30.1111 | 28.6667 | 29.6667 | 30.4444 | 30.1111 | 29.7778 | 29.7778 | 28.9369
7 | Chilled water inlet pressure | (Kg/Cm2) |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  |  |  | 2154.9232 | 2336.8788 | 2568.7837 | 2212.007 | 2212.0093 | 2283.3643 | 2354.718 | 2390.3936 | 2390.3971 | 2818.5256 | 2889.881 | 2443.9116 | 2657.9767 | 2586.6233 | 2497.4268 | 2354.719 | 2301.1997 | 2675.8149 | 2818.5269 | 2889.8813 | 2889.8816 | 2889.8813 | 55617.7247
15 | Power Consumption of Chiller | KWH |  |  |  | 1510 | 1570 | 1430 | 1410 | 1430 | 1440 | 1450 | 1460 | 1570 | 1600 | 1500 | 1550 | 1540 | 1530 | 1500 | 1450 | 1570 | 1590 | 1600 | 1600 | 1600 | 1600 | 33500
16 | Specific power consumption of Chiller | (iKW/TR) |  |  |  | 0.70072 | 0.67184 | 0.55668 | 0.63743 | 0.64647 | 0.63065 | 0.61578 | 0.61078 | 0.65679 | 0.56767 | 0.51905 | 0.63423 | 0.57939 | 0.5915 | 0.60062 | 0.61578 | 0.68225 | 0.59421 | 0.56767 | 0.55366 | 0.55366 | 0.55366 | 0.60639
17 | Average iKW/TR |  |  | 0.60639 | [23 empty] | 0.60639
18 | COP of chiller |  |  |  |  | 5.0177 | 5.2334 | 6.316 | 5.5159 | 5.4388 | 5.5752 | 5.7098 | 5.7566 | 5.3533 | 6.1937 | 6.7739 | 5.5437 | 6.0685 | 5.9442 | 5.854 | 5.7098 | 5.1535 | 5.9171 | 6.1937 | 6.3505 | 6.3505 | 6.3505 | 5.8327
19 | EER of Chiller |  |  |  |  | 17.1254 | 17.8617 | 21.5564 | 18.8258 | 18.5625 | 19.0282 | 19.4875 | 19.6472 | 18.2707 | 21.1391 | 23.1193 | 18.9208 | 20.7117 | 20.2874 | 19.9796 | 19.4875 | 17.5889 | 20.195 | 21.1391 | 21.6743 | 21.6743 | 21.6743 | 19.9071
20 | LMTD of Condenser | ºC |  |  |  | 0.60682 | 2.9695 | 2.987 | 2.8167 | 2.6903 | 2.8509 | 3.0446 | 2.9526 | 2.8236 | 3.5277 | 3.147 | 2.8566 | 3.1027 | 3.1027 | 2.9058 | 2.9526 | 2.885 | 3.1192 | 3.2338 | 3.2663 | 3.2663 | 3.2663 | 2.9261
21 | LMTD of Evaporator | ºC |  |  |  | 2.6842 | 2.6518 | 2.6277 | 2.558 | 2.8904 | 2.7849 | 2.8403 | 2.8679 | 2.8679 | 2.5743 | 3.2461 | 2.5395 | 2.6902 | 2.6402 | 2.5774 | 2.4759 | 2.4376 | 2.7026 | 3.0053 | 3.0566 | 3.2461 | 3.2461 | 2.7823

## 27-02-19 (hidden)
Performance Sheet Chiller
Date :- 27/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [6 empty] | 1.7 | 1.5 | 1.3 | 1.4 | 1.3 | 1.4 | 1.4 | 1.5 | 1.4 | 1.6 | 1.4 | 1.4 | 1.5 | 1.6 | 1.6 | 1.7 | 1.8 | 1.7 | 1.8 | 1.5263
2 | Small temperature difference of evaporator | ºC | [6 empty] | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.5 | 0.4 | 0.5 | 0.39474
3 | Entering Chilled Water Temp. (tchwe) | ºC | [6 empty] | 13.7222 | 14.3333 | 13.8889 | 13.7222 | 13.7222 | 13.8333 | 13.8889 | 13.8889 | 13.7778 | 13.7778 | 13.6667 | 13.1111 | 12.5556 | 12.7778 | 13.8889 | 14.4444 | 14.6667 | 14.8333 | 15.0556 | 13.8713
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [6 empty] | 8 | 6.9444 | 6.9444 | 7 | 7.1111 | 7.1111 | 7 | 7.1111 | 7 | 7 | 6.1667 | 5.6111 | 5.6111 | 5.6111 | 5.8333 | 6.0556 | 6.5 | 6.4444 | 6.5556 | 6.6111
5 | Entering Condenser Water Temp. (tcwe) | ºC | [6 empty] | 20 | 24.3889 | 24.2222 | 24.3889 | 24.6667 | 24.3333 | 24.5 | 24.9444 | 24.9444 | 24.9444 | 25.2778 | 25.4444 | 25.2222 | 23.5556 | 23.4444 | 23.4444 | 23.7222 | 23.4444 | 23 | 24.0994
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [6 empty] | 24.5 | 29.0556 | 28.4444 | 28.5556 | 28.7778 | 28.5556 | 28.8889 | 29.3333 | 29.3333 | 29.1111 | 30 | 30.2222 | 29.5 | 28.2222 | 28.6111 | 28.8333 | 29 | 28.7778 | 28.2778 | 28.7368
7 | Chilled water inlet pressure | (Kg/Cm2) | [6 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [6 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [6 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [6 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [6 empty] | 1837.3927 | 2372.5553 | 2229.8466 | 2158.4906 | 2122.8131 | 2158.4903 | 2212.008 | 2176.3305 | 2176.3308 | 2176.3308 | 2408.2354 | 2408.2341 | 2229.8482 | 2301.2026 | 2586.6223 | 2693.6526 | 2622.3005 | 2693.6535 | 2729.3336 | 44293.6716
15 | Power Consumption of Chiller | KWH | [6 empty] | 1520 | 1520 | 1520 | 1490 | 1510 | 1470 | 1490 | 1500 | 1500 | 1500 | 1580 | 1500 | 1500 | 1530 | 1530 | 1600 | 1510 | 1500 | 1530 | 28800
16 | Specific power consumption of Chiller | (iKW/TR) | [6 empty] | 0.82726 | 0.64066 | 0.68166 | 0.6903 | 0.71132 | 0.68103 | 0.6736 | 0.68923 | 0.68923 | 0.68923 | 0.65608 | 0.62286 | 0.67269 | 0.66487 | 0.5915 | 0.59399 | 0.57583 | 0.55686 | 0.56058 | 0.65625
17 | Average iKW/TR |  |  | Hours 7: 0.65625 | 0.65625
18 | COP of chiller | [7 empty] | 4.2502 | 5.4881 | 5.158 | 5.0935 | 4.9429 | 5.1628 | 5.2197 | 5.1013 | 5.1013 | 5.1013 | 5.3591 | 5.6449 | 5.2268 | 5.2883 | 5.9442 | 5.9193 | 6.106 | 6.3139 | 6.2721 | 5.4049
19 | EER of Chiller | [7 empty] | 14.5059 | 18.7309 | 17.6042 | 17.384 | 16.8702 | 17.6205 | 17.815 | 17.4108 | 17.4108 | 17.4108 | 18.2906 | 19.266 | 17.8389 | 18.0488 | 20.2874 | 20.2026 | 20.8397 | 21.5494 | 21.4067 | 18.447
20 | LMTD of Condenser | ºC | [6 empty] | 3.4778 | 3.301 | 2.9191 | 3.0186 | 2.8828 | 3.037 | 3.0919 | 3.2092 | 3.0919 | 3.2499 | 3.2005 | 3.2185 | 3.1721 | 3.4182 | 3.583 | 3.774 | 3.8547 | 3.7558 | 3.8547 | 3.3216
21 | LMTD of Evaporator | ºC | [6 empty] | 2.0974 | 2.4887 | 2.1809 | 2.132 | 2.1074 | 2.132 | 2.3733 | 2.3475 | 2.3475 | 2.3475 | 2.5141 | 2.5141 | 2.3862 | 2.4376 | 2.8367 | 2.715 | 2.8629 | 2.715 | 2.9408 | 2.4461
Performance Sheet Chiller
Date :- 27/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.1 | 1.2 | 1.1 | 1.1 | 0.9 | 1.1 | 1 | 1 | 0.9 | 1 | 0.9 | 0.9 | 0.9 | 1.1 | 1 | 1 | 0.9 | [7 empty] | 1.0059
2 | Small temperature difference of evaporator | ºC |  | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.4 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | [7 empty] | 0.48824
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.7778 | 14.6667 | 15.1111 | 15.1111 | 15.6111 | 15.5 | 14.8889 | 14 | 13.7778 | 13.7778 | 13.8889 | 14 | 13.8889 | 13.7778 | 13.8889 | 13.6667 | 13.2222 | [7 empty] | 14.3268
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.7778 | 5.6667 | 6 | 6.1111 | 6.3333 | 7.1667 | 7 | 7 | 7.1111 | 7.1111 | 7.1111 | 7 | 7 | 6.8889 | 7.1111 | 6 | 5.4444 | [7 empty] | 6.5784
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.6111 | 22.8333 | 22.8333 | 23.6111 | 23.6111 | 24.7222 | 24.5 | 24.2778 | 24.4444 | 24.6667 | 24.3333 | 24.5556 | 25.0556 | 24.9444 | 25.0556 | 25.3333 | 25.4444 | [7 empty] | 24.3431
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.7222 | 29.0556 | 29.2222 | 29.8889 | 29.8333 | 30.3889 | 29.9444 | 29 | 28.8889 | 29.2778 | 29.0556 | 29.2778 | 29.7778 | 29.6667 | 29.6667 | 30.6111 | 30.8333 | [7 empty] | 29.6536
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [7 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [7 empty] | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [7 empty] | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [7 empty] | 971
14 | TR Genrated by Chiller | TR |  | 2889.8813 | 2889.8819 | 2925.5581 | 2889.8806 | 2979.0742 | 2675.8153 | 2533.1059 | 2247.6852 | 2140.6533 | 2140.6533 | 2176.3305 | 2247.6852 | 2212.008 | 2212.008 | 2176.3305 | 2461.7515 | 2497.4274 | [7 empty] | 42295.7302
15 | Power Consumption of Chiller | KWH |  | 1300 | 1340 | 1340 | 1340 | 1250 | 1220 | 1200 | 1190 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1220 | 1200 | [7 empty] | 21000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.44985 | 0.46369 | 0.45803 | 0.46369 | 0.41959 | 0.45594 | 0.47373 | 0.52943 | 0.56058 | 0.56058 | 0.55139 | 0.53388 | 0.54249 | 0.54249 | 0.55139 | 0.49558 | 0.48049 | [7 empty] | 0.50193
17 | Average iKW/TR |  |  | Hours 7: 0.50193 | 0.50193
18 | COP of chiller |  |  | 7.816 | 7.5827 | 7.6763 | 7.5827 | 8.3795 | 7.7116 | 7.422 | 6.6411 | 6.2721 | 6.2721 | 6.3766 | 6.5857 | 6.4812 | 6.4812 | 6.3766 | 7.0947 | 7.3175 | [7 empty] | 7.0629
19 | EER of Chiller |  |  | 26.6761 | 25.8798 | 26.1993 | 25.8798 | 28.5994 | 26.3197 | 25.3313 | 22.6659 | 21.4067 | 21.4067 | 21.7635 | 22.4771 | 22.1203 | 22.1203 | 21.7635 | 24.2142 | 24.9745 | [7 empty] | 24.1058
20 | LMTD of Condenser | ºC |  | 3.25 | 3.4148 | 3.3308 | 3.2986 | 3.008 | 3.1192 | 2.9221 | 2.7071 | 2.4949 | 2.6735 | 2.5775 | 2.5775 | 2.5775 | 2.8338 | 2.6735 | 2.873 | 2.7719 | [7 empty] | 2.8885
21 | LMTD of Evaporator | ºC |  | 3.2461 | 3.2461 | 3.2726 | 3.2461 | 3.1204 | 2.9019 | 2.7974 | 2.3991 | 2.3215 | 2.5038 | 2.7011 | 2.3991 | 2.3733 | 2.558 | 2.3475 | 2.5521 | 2.5774 | [7 empty] | 2.739
Performance Sheet Chiller
Date :- 27/02/2019
CHILLER NO. 1
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 11: 1.2 | 1.2
2 | Small temperature difference of evaporator | ºC |  | Hours 11: 0.5 | 0.5
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 11: 15.2778 | 15.2778
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 11: 8 | 8
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 11: 23.7222 | 23.7222
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 11: 22.7778 | 22.7778
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 11: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 11: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 11: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 11: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 11: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 11: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 11: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 11: 2336.8798 | 2336.8798
15 | Power Consumption of Chiller | KWH |  | Hours 11: 1200 | 1200
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 11: 0.51351 | 0.51351
17 | Average iKW/TR |  |  | Hours 7: 0.51351 | 0.51351
18 | COP of chiller |  |  | Hours 11: 6.8471 | 6.8471
19 | EER of Chiller |  |  | Hours 11: 23.369 | 23.369
20 | LMTD of Condenser | ºC |  | Hours 11: 0.61065 | 0.61065
21 | LMTD of Evaporator | ºC |  | Hours 11: 2.6518 | 2.6518

## 28-02-2019 (hidden)
Performance Sheet Chiller
Date :- 28/02/2019
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 7: 1.6; Hours 8: 1.7; Hours 9: 1.6; Hours 10: 1.8; Hours 11: 1.8; Hours 12: 1.7; Hours 13: 1.6; Hours 14: 1.6; Hours 15: 1.6; Hours 16: 1.6; Hours 17: 1.6; Hours 18: 1.6; Hours 19: 1.5; Hours 20: 1.4 | 1.6214
2 | Small temperature difference of evaporator | ºC |  | Hours 7: 0.4; Hours 8: 0.4; Hours 9: 0.6; Hours 10: 0.7; Hours 11: 0.7; Hours 12: 0.6; Hours 13: 0.5; Hours 14: 0.4; Hours 15: 0.4; Hours 16: 0.5; Hours 17: 0.4; Hours 18: 0.4; Hours 19: 0.5; Hours 20: 0.4 | 0.49286
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 7: 15.0556; Hours 8: 15.1111; Hours 9: 15.2222; Hours 10: 15.6667; Hours 11: 15.8333; Hours 12: 15.3333; Hours 13: 14.8333; Hours 14: 14.2222; Hours 15: 13.7778; Hours 16: 13.6111; Hours 17: 13.5556; Hours 18: 14.5556; Hours 19: 15.2778; Hours 20: 15.6667 | 14.8373
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 7: 6.5556; Hours 8: 6.6667; Hours 9: 6.7222; Hours 10: 7.0556; Hours 11: 7.2778; Hours 12: 6.8333; Hours 13: 6.3889; Hours 14: 5.9444; Hours 15: 5.6111; Hours 16: 5.6111; Hours 17: 5.5; Hours 18: 6.0556; Hours 19: 6.3889; Hours 20: 7.3333 | 6.4246
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 7: 23; Hours 8: 23.3333; Hours 9: 23.4444; Hours 10: 23.2222; Hours 11: 22.7778; Hours 12: 22.6667; Hours 13: 22.2222; Hours 14: 21.9444; Hours 15: 21.6667; Hours 16: 22.6111; Hours 17: 22.2222; Hours 18: 21.7778; Hours 19: 20.6111; Hours 20: 23.6111 | 22.5079
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 7: 28.2778; Hours 8: 28.6111; Hours 9: 28.7778; Hours 10: 28.7778; Hours 11: 28.2778; Hours 12: 28.0556; Hours 13: 27.5556; Hours 14: 27.2778; Hours 15: 26.8889; Hours 16: 27.7222; Hours 17: 27.5; Hours 18: 27.2778; Hours 19: 26.3333; Hours 20: 28.6111 | 27.8532
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 7: 4; Hours 8: 4; Hours 9: 4; Hours 10: 4; Hours 11: 4; Hours 12: 4; Hours 13: 4; Hours 14: 4; Hours 15: 4; Hours 16: 4; Hours 17: 4; Hours 18: 4; Hours 19: 4; Hours 20: 4 | 4
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 7: 3.5; Hours 8: 3.5; Hours 9: 3.5; Hours 10: 3.5; Hours 11: 3.5; Hours 12: 3.5; Hours 13: 3.5; Hours 14: 3.5; Hours 15: 3.5; Hours 16: 3.5; Hours 17: 3.5; Hours 18: 3.5; Hours 19: 3.5; Hours 20: 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 7: 3.8; Hours 8: 3.8; Hours 9: 3.8; Hours 10: 3.8; Hours 11: 3.8; Hours 12: 3.8; Hours 13: 3.8; Hours 14: 3.8; Hours 15: 3.8; Hours 16: 3.8; Hours 17: 3.8; Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 7: 3; Hours 8: 3; Hours 9: 3; Hours 10: 3; Hours 11: 3; Hours 12: 3; Hours 13: 3; Hours 14: 3; Hours 15: 3; Hours 16: 3; Hours 17: 3; Hours 18: 3; Hours 19: 3; Hours 20: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 7: 0.5; Hours 8: 0.5; Hours 9: 0.5; Hours 10: 0.5; Hours 11: 0.5; Hours 12: 0.5; Hours 13: 0.5; Hours 14: 0.5; Hours 15: 0.5; Hours 16: 0.5; Hours 17: 0.5; Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 7: 0.8; Hours 8: 0.8; Hours 9: 0.8; Hours 10: 0.8; Hours 11: 0.8; Hours 12: 0.8; Hours 13: 0.8; Hours 14: 0.8; Hours 15: 0.8; Hours 16: 0.8; Hours 17: 0.8; Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 7: 971; Hours 8: 971; Hours 9: 971; Hours 10: 971; Hours 11: 971; Hours 12: 971; Hours 13: 971; Hours 14: 971; Hours 15: 971; Hours 16: 971; Hours 17: 971; Hours 18: 971; Hours 19: 971; Hours 20: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 7: 2729.3336; Hours 8: 2711.4928; Hours 9: 2729.3317; Hours 10: 2765.0105; Hours 11: 2747.17; Hours 12: 2729.331; Hours 13: 2711.4921; Hours 14: 2657.976; Hours 15: 2622.3005; Hours 16: 2568.7831; Hours 17: 2586.6229; Hours 18: 2729.333; Hours 19: 2854.2041; Hours 20: 2675.8166 | 37818.1978
15 | Power Consumption of Chiller | KWH |  | 1500 | 1600 | 1600 | 1500 | 1500 | 1600 | 1400 | 1600 | 1500 | 1400 | 1600 | 1600 | 1300 | 1500 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21800
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 7: 0.54958; Hours 8: 0.59008; Hours 9: 0.58622; Hours 10: 0.54249; Hours 11: 0.54602; Hours 12: 0.58622; Hours 13: 0.51632; Hours 14: 0.60196; Hours 15: 0.57202; Hours 16: 0.54501; Hours 17: 0.61857; Hours 18: 0.58622; Hours 19: 0.45547; Hours 20: 0.56058 | 0.5612
17 | Average iKW/TR |  |  | Hours 7: 0.5612 | 0.5612
18 | COP of chiller |  |  | Hours 7: 6.3976; Hours 8: 5.9585; Hours 9: 5.9977; Hours 10: 6.4812; Hours 11: 6.4394; Hours 12: 5.9977; Hours 13: 6.8097; Hours 14: 5.8409; Hours 15: 6.1467; Hours 16: 6.4513; Hours 17: 5.6841; Hours 18: 5.9977; Hours 19: 7.7195; Hours 20: 6.2721 | 6.2996
19 | EER of Chiller |  |  | Hours 7: 21.8349; Hours 8: 20.3364; Hours 9: 20.4702; Hours 10: 22.1203; Hours 11: 21.9776; Hours 12: 20.4702; Hours 13: 23.2416; Hours 14: 19.935; Hours 15: 20.9786; Hours 16: 22.0183; Hours 17: 19.3998; Hours 18: 20.4702; Hours 19: 26.3467; Hours 20: 21.4067 | 21.5005
20 | LMTD of Condenser | ºC |  | Hours 7: 3.6192; Hours 8: 3.7375; Hours 9: 3.6372; Hours 10: 3.9466; Hours 11: 3.9283; Hours 12: 3.774; Hours 13: 3.6372; Hours 14: 3.6372; Hours 15: 3.6011; Hours 16: 3.5648; Hours 17: 3.6192; Hours 18: 3.691; Hours 19: 3.6408; Hours 20: 3.2899 | 1.22
21 | LMTD of Evaporator | ºC |  | Hours 7: 2.7399; Hours 8: 2.7275; Hours 9: 3.126; Hours 10: 3.3275; Hours 11: 3.3137; Hours 12: 3.126; Hours 13: 2.9278; Hours 14: 2.6902; Hours 15: 2.6652; Hours 16: 2.8236; Hours 17: 2.6402; Hours 18: 2.7399; Hours 19: 3.031; Hours 20: 2.7026 | 2.8986
Performance Sheet Chiller
Date :- 28/02/2019
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | Hours 18: 1.2; Hours 19: 1.2; Hours 20: 0.9; Hours 21: 1.1; Hours 22: 0.9; Hours 23: 1.1; Hours 0: 1.1; Hours 1: 1.1; Hours 2: 0.9; Hours 3: 1; Hours 4: 1.1; Hours 5: 1.1; Hours 6: 1.1 | 1.0615
2 | Small temperature difference of evaporator | ºC |  | Hours 18: 0.6; Hours 19: 0.6; Hours 20: 0.6; Hours 21: 0.4; Hours 22: 0.4; Hours 23: 0.7; Hours 0: 0.6; Hours 1: 0.7; Hours 2: 0.6; Hours 3: 0.7; Hours 4: 0.7; Hours 5: 0.7; Hours 6: 0.7 | 0.61538
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 18: 15.9444; Hours 19: 15.9444; Hours 20: 15.9444; Hours 21: 14.3889; Hours 22: 13.3889; Hours 23: 12.6111; Hours 0: 13.2778; Hours 1: 13.3889; Hours 2: 13.5556; Hours 3: 13.5556; Hours 4: 13.5556; Hours 5: 13.3889; Hours 6: 13.2778 | 14.0171
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 18: 7.2778; Hours 19: 7.2778; Hours 20: 7.2778; Hours 21: 6.9444; Hours 22: 5.8333; Hours 23: 5.3333; Hours 0: 5.6667; Hours 1: 5.6667; Hours 2: 5.6667; Hours 3: 5.5556; Hours 4: 5.4444; Hours 5: 5.4444; Hours 6: 5.5 | 6.0684
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 18: 23; Hours 19: 23; Hours 20: 23; Hours 21: 24.6111; Hours 22: 24.6111; Hours 23: 23.5; Hours 0: 20.1111; Hours 1: 20.1667; Hours 2: 19.7778; Hours 3: 19.6667; Hours 4: 19.7778; Hours 5: 19.8889; Hours 6: 20.3333 | 21.6496
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 18: 29.1111; Hours 19: 29.1111; Hours 20: 29.1111; Hours 21: 29.8889; Hours 22: 29.8333; Hours 23: 28.3333; Hours 0: 25.3889; Hours 1: 25.3889; Hours 2: 25.1667; Hours 3: 25.0556; Hours 4: 25.2222; Hours 5: 25.2222; Hours 6: 25.5 | 27.1026
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 18: 4; Hours 19: 4; Hours 20: 4; Hours 21: 4; Hours 22: 4; Hours 23: 4; Hours 0: 4; Hours 1: 4; Hours 2: 4; Hours 3: 4; Hours 4: 4; Hours 5: 4; Hours 6: 4 | 4
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 18: 3.5; Hours 19: 3.5; Hours 20: 3.5; Hours 21: 3.5; Hours 22: 3.5; Hours 23: 3.5; Hours 0: 3.5; Hours 1: 3.5; Hours 2: 3.5; Hours 3: 3.5; Hours 4: 3.5; Hours 5: 3.5; Hours 6: 3.5 | 3.5
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 18: 3.8; Hours 19: 3.8; Hours 20: 3.8; Hours 21: 3.8; Hours 22: 3.8; Hours 23: 3.8; Hours 0: 3.8; Hours 1: 3.8; Hours 2: 3.8; Hours 3: 3.8; Hours 4: 3.8; Hours 5: 3.8; Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 18: 3; Hours 19: 3; Hours 20: 3; Hours 21: 3; Hours 22: 3; Hours 23: 3; Hours 0: 3; Hours 1: 3; Hours 2: 3; Hours 3: 3; Hours 4: 3; Hours 5: 3; Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 18: 0.5; Hours 19: 0.5; Hours 20: 0.5; Hours 21: 0.5; Hours 22: 0.5; Hours 23: 0.5; Hours 0: 0.5; Hours 1: 0.5; Hours 2: 0.5; Hours 3: 0.5; Hours 4: 0.5; Hours 5: 0.5; Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 18: 0.8; Hours 19: 0.8; Hours 20: 0.8; Hours 21: 0.8; Hours 22: 0.8; Hours 23: 0.8; Hours 0: 0.8; Hours 1: 0.8; Hours 2: 0.8; Hours 3: 0.8; Hours 4: 0.8; Hours 5: 0.8; Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 18: 971; Hours 19: 971; Hours 20: 971; Hours 21: 971; Hours 22: 971; Hours 23: 971; Hours 0: 971; Hours 1: 971; Hours 2: 971; Hours 3: 971; Hours 4: 971; Hours 5: 971; Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 18: 2782.8504; Hours 19: 2782.8504; Hours 20: 2782.8504; Hours 21: 2390.3955; Hours 22: 2426.0734; Hours 23: 2336.8788; Hours 0: 2443.9123; Hours 1: 2479.5895; Hours 2: 2533.1068; Hours 3: 2568.7844; Hours 4: 2604.4622; Hours 5: 2550.9448; Hours 6: 2497.4284 | 33180.1271
15 | Power Consumption of Chiller | KWH |  | Hours 18: 1200; Hours 19: 1300; Hours 20: 1400; Hours 21: 1300; Hours 22: 1300; Hours 23: 1200; Hours 0: 1400; Hours 1: 1300; Hours 2: 1300; Hours 3: 1300; Hours 4: 1300; Hours 5: 1200; Hours 6: 1200 | 16700
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 18: 0.43121; Hours 19: 0.46715; Hours 20: 0.50308; Hours 21: 0.54384; Hours 22: 0.53585; Hours 23: 0.51351; Hours 0: 0.57285; Hours 1: 0.52428; Hours 2: 0.5132; Hours 3: 0.50608; Hours 4: 0.49914; Hours 5: 0.47041; Hours 6: 0.48049 | 0.5047
17 | Average iKW/TR |  |  | Hours 7: 0.5047 | 0.5047
18 | COP of chiller |  |  | Hours 18: 8.1538; Hours 19: 7.5265; Hours 20: 6.9889; Hours 21: 6.4651; Hours 22: 6.5616; Hours 23: 6.8471; Hours 0: 6.1377; Hours 1: 6.7063; Hours 2: 6.8511; Hours 3: 6.9476; Hours 4: 7.0441; Hours 5: 7.4743; Hours 6: 7.3175 | 7.0017
19 | EER of Chiller |  |  | Hours 18: 27.8288; Hours 19: 25.6881; Hours 20: 23.8532; Hours 21: 22.0654; Hours 22: 22.3947; Hours 23: 23.369; Hours 0: 20.948; Hours 1: 22.8887; Hours 2: 23.3827; Hours 3: 23.7121; Hours 4: 24.0414; Hours 5: 25.5097; Hours 6: 24.9745 | 23.8966
20 | LMTD of Condenser | ºC |  | Hours 18: 3.3818; Hours 19: 3.3818; Hours 20: 2.9769; Hours 21: 3.003; Hours 22: 2.7238; Hours 23: 2.868; Hours 0: 3.003; Hours 1: 2.9862; Hours 2: 2.7719; Hours 3: 2.9058; Hours 4: 3.053; Hours 5: 3.0197; Hours 6: 2.9695 | 3.0034
21 | LMTD of Evaporator | ºC |  | Hours 18: 3.1662; Hours 19: 3.1662; Hours 20: 3.1662; Hours 21: 2.5014; Hours 22: 2.5268; Hours 23: 2.9909; Hours 0: 2.9091; Hours 1: 3.1044; Hours 2: 2.9774; Hours 3: 3.1746; Hours 4: 3.2026; Hours 5: 3.1606; Hours 6: 3.1184 | 3.0127

## 25-03-2023
Performance Sheet Chiller
Date :- 25/03/2023
CHILLER NO. 4
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.9 | 0.9 | 0.9 |  |  |  |  | 0.8 | 0.9 | 0.8 | 0.9 | 0.8 | 1 | 0.9 | 1 | 1 | 0.9 | 1 | 1 | 0.8 |  |  |  |  | 0.90625
2 | Small temperature difference of evaporator | ºC |  | 1 | 1.1 | 0.8 |  |  |  |  | 1.3 | 1.1 | 1.1 | 1 | 0.8 | 0.9 | 0.9 | 1 | 1 | 1.3 | 1.3 | 1 | 0.9 |  |  |  |  | 1.0313
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.2 | 14.2 | 12.9 |  |  |  |  | 16.2 | 15.4 | 14.6 | 14.1 | 13.7 | 12.7 | 13.4 | 14.4 | 15 | 15.3 | 14.8 | 13.4 | 12.3 |  |  |  |  | 14.225
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.3 | 6.3 | 5.3 |  |  |  |  | 9.2 | 7.4 | 6.9 | 7.1 | 5.7 | 5.7 | 5.8 | 6.4 | 7 | 7.3 | 6.8 | 5.7 | 5.4 |  |  |  |  | 6.5813
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.5 | 23.3 | 23.2 |  |  |  |  | 24.7 | 23.8 | 22.9 | 23.1 | 23.3 | 23.8 | 23.2 | 22.9 | 22.9 | 22.9 | 22.8 | 22.6 | 22.1 |  |  |  |  | 23.1875
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.8 | 28.6 | 28 |  |  |  |  | 29.3 | 29.1 | 27.9 | 27.6 | 28.5 | 30.2 | 28.1 | 28.2 | 28.2 | 28.4 | 27.9 | 27.6 | 26.5 |  |  |  |  | 28.3062
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 |  |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  |  | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 |  |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 |  |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  |  | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2536.6733 | 2440.3439 |  |  |  |  | 2247.6852 | 2568.7831 | 2472.4537 | 2247.6852 | 2568.7831 | 2247.6852 | 2440.3439 | 2568.7831 | 2568.7831 | 2568.7831 | 2568.7831 | 2472.4537 | 2215.5754 |  |  |  |  | 39270.2712
15 | Power Consumption of Chiller | KWH |  | 1500 | 900 | 900 |  |  |  |  | 1200 | 1700 | 1300 | 1500 | 1300 | 1100 | 1900 | 1500 | 1400 | 1400 | 1200 | 1000 | 500 |  |  |  |  | 20300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.59133 | 0.3548 | 0.3688 |  |  |  |  | 0.53388 | 0.66179 | 0.52579 | 0.66735 | 0.50608 | 0.48939 | 0.77858 | 0.58393 | 0.54501 | 0.54501 | 0.46715 | 0.40446 | 0.22568 |  |  |  |  | 0.51556
17 | Average iKW/TR |  |  | Hours 7: 0.51556 | 0.51556
18 | COP of chiller |  |  | 5.946 | 9.9099 | 9.5336 |  |  |  |  | 6.5857 | 5.3128 | 6.687 | 5.2686 | 6.9476 | 7.1844 | 4.5159 | 6.0212 | 6.4513 | 6.4513 | 7.5265 | 8.6931 | 15.5799 |  |  |  |  | 7.4134
19 | EER of Chiller |  |  | 20.2936 | 33.8226 | 32.5382 |  |  |  |  | 22.4771 | 18.1327 | 22.8229 | 17.9816 | 23.7121 | 24.5204 | 15.4128 | 20.5504 | 22.0183 | 22.0183 | 25.6881 | 29.6697 | 53.1743 |  |  |  |  | 25.3021
20 | LMTD of Condenser | ºC |  | 2.7462 | 2.7462 | 2.6005 |  |  |  |  | 2.409 | 2.7462 | 2.524 | 2.5115 | 2.5808 | 3.1976 | 2.6299 | 2.8796 | 2.8796 | 2.8037 | 2.8203 | 2.7906 | 2.3507 |  |  |  |  | 2.701
21 | LMTD of Evaporator | ºC |  | 3.6138 | 3.7585 | 3.2322 |  |  |  |  | 3.7758 | 3.7862 | 3.7029 | 3.3663 | 3.3363 | 3.2225 | 3.3847 | 3.641 | 3.641 | 4.0658 | 4.0658 | 3.5593 | 3.1952 |  |  |  |  | 3.5842
Performance Sheet Chiller
Date :- 25/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.2 | 1.1 | 1.1 | 1.3 | 1.3 | 1.3 | 0.9 | 1 | 1.1 | 1.1 | 1.4 | 1.1 |  |  |  |  | 1 | 1 | 0.8 | 1 | 1.1 | 1.2 | 1.1 | 1.115
2 | Small temperature difference of evaporator | ºC |  | 1.1 | 0.8 | 0.8 | 0.6 | 0.7 | 0.8 | 0.7 | 0.8 | 0.5 | 0.8 | 0.8 | 0.7 | 0.7 |  |  |  |  | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.71
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 15.1 | 14.2 | 12.9 | 12.9 | 13.9 | 14.7 | 15.5 | 15.7 | 15.4 | 14.6 | 14.1 | 13.6 | 12.6 |  |  |  |  | 14.7 | 13.4 | 12.2 | 11.7 | 12.9 | 13.3 | 13.7 | 13.855
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.8 | 6.5 | 5.5 | 5.8 | 6.5 | 6.7 | 7.6 | 8.4 | 7.8 | 7.1 | 7 | 5.7 | 5.7 |  |  |  |  | 6.8 | 5.7 | 5.3 | 5.6 | 5.7 | 5.6 | 5.7 | 6.375
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.3 | 23.1 | 23 | 22.5 | 22.7 | 22.6 | 23.9 | 24.6 | 23.7 | 22.9 | 23.1 | 23.3 | 23.3 |  |  |  |  | 22.6 | 22.4 | 21.9 | 21.1 | 21.3 | 21.2 | 21.6 | 22.705
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.9 | 28.9 | 28.4 | 27.8 | 28.3 | 28.7 | 29.8 | 30.3 | 29.4 | 28.3 | 28.2 | 29.1 | 25.3 |  |  |  |  | 28.7 | 28.1 | 27.1 | 25.7 | 26.6 | 27.2 | 27.5 | 28.165
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2665.1124 | 2472.4537 | 2376.1243 | 2279.795 | 2376.1243 | 2568.7831 | 2536.6733 | 2344.0146 | 2440.3439 | 2408.2341 | 2279.795 | 2536.6733 | 2215.5754 |  |  |  |  | 2536.6733 | 2472.4537 | 2215.5754 | 1958.6971 | 2311.9048 | 2472.4537 | 2568.7831 | 48036.2434
15 | Power Consumption of Chiller | KWH |  | 1500 | 1400 | 1200 | 1800 | 1400 | 1400 | 1600 | 1100 | 1700 | 1500 | 1500 | 1200 | 1600 |  |  |  |  | 1200 | 1600 | 1000 | 1300 | 1400 | 1100 | 1800 | 28300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.56283 | 0.56624 | 0.50502 | 0.78954 | 0.58919 | 0.54501 | 0.63075 | 0.46928 | 0.69662 | 0.62286 | 0.65795 | 0.47306 | 0.72216 |  |  |  |  | 0.47306 | 0.64713 | 0.45135 | 0.66371 | 0.60556 | 0.4449 | 0.70072 | 0.59085
17 | Average iKW/TR |  |  | Hours 7: 0.59085 | 0.59085
18 | COP of chiller |  |  | 6.247 | 6.2094 | 6.962 | 4.4532 | 5.9675 | 6.4513 | 5.5743 | 7.4923 | 5.0472 | 5.6449 | 5.3438 | 7.4325 | 4.8687 |  |  |  |  | 7.4325 | 5.4332 | 7.79 | 5.2975 | 5.8062 | 7.9029 | 5.0177 | 6.1187
19 | EER of Chiller |  |  | 21.3211 | 21.1927 | 23.7615 | 15.1988 | 20.367 | 22.0183 | 19.0252 | 25.5713 | 17.2261 | 19.266 | 18.2385 | 25.367 | 16.617 |  |  |  |  | 25.367 | 18.5436 | 26.5871 | 18.0804 | 19.8165 | 26.9725 | 17.1254 | 20.8831
20 | LMTD of Condenser | ºC |  | 3.526 | 3.2887 | 3.0397 | 3.0097 | 3.355 | 3.5075 | 3.4468 | 2.8608 | 2.9967 | 3.0397 | 2.9493 | 3.5417 | 1.9303 |  |  |  |  | 3.1121 | 2.9967 | 2.5808 | 2.6701 | 3.0097 | 3.3487 | 3.1882 | 3.0699
21 | LMTD of Evaporator | ºC |  | 3.8687 | 3.2583 | 3.1797 | 2.7821 | 3.0222 | 3.3363 | 3.1494 | 3.1533 | 2.7289 | 3.206 | 3.1004 | 3.1494 | 2.8933 |  |  |  |  | 2.9801 | 3.0987 | 2.7319 | 2.528 | 2.8071 | 3.0987 | 3.0046 | 3.0539

## 26-03-2023
Performance Sheet Chiller
Date :- 26/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [8 empty] | 0.5 | 0.6 | 0.5 | 0.5 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 0.1 | 0.46471
2 | Small temperature difference of evaporator | ºC | [8 empty] | 1.5 | 1.5 | 1.2 | 1.2 | 1.4 | 1.4 | 1.4 | 1.5 | 1.1 | 1.3 | 1.1 | 1.1 | 1.2 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2647
3 | Entering Chilled Water Temp. (tchwe) | ºC | [8 empty] | 15.8 | 14.5 | 13.8 | 13.8 | 13.6 | 13 | 12.6 | 13.9 | 14.4 | 13.7 | 12.8 | 12.2 | 11.9 | 12.6 | 13.7 | 14.2 | 14.6 | 13.5941
4 | Leaving Chilled Water Temp. (tchwl) | ºC | [8 empty] | 7.9 | 6.7 | 6.9 | 7.1 | 6.1 | 5.6 | 5.5 | 6.1 | 6.9 | 6.1 | 5.4 | 5.4 | 5.4 | 5.7 | 6 | 6.3 | 6.7 | 6.2235
5 | Entering Condenser Water Temp. (tcwe) | ºC | [8 empty] | 24.8 | 24.1 | 23.5 | 23.8 | 23.9 | 24.4 | 24.1 | 24 | 25.6 | 23.9 | 23.4 | 23.3 | 23.3 | 23.2 | 23.4 | 23.5 | 23.5 | 23.8647
6 | Leaving Condenser Water Temp. (tcwl) | ºC | [8 empty] | 29.6 | 29.1 | 27.8 | 27.9 | 28.6 | 29.2 | 28.8 | 29.2 | 30.4 | 28.7 | 28.2 | 27.6 | 27.4 | 27.5 | 28.4 | 28.6 | 28.5 | 28.5588
7 | Chilled water inlet pressure | (Kg/Cm2) | [8 empty] | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) | [8 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) | [8 empty] | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) | [8 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) | [8 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) | [8 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) | [8 empty] | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR | [8 empty] | 2536.6733 | 2504.5635 | 2215.5754 | 2151.3558 | 2408.2341 | 2376.1243 | 2279.795 | 2504.5635 | 2408.2341 | 2440.3439 | 2376.1243 | 2183.4656 | 2087.1362 | 2215.5754 | 2472.4537 | 2536.6733 | 2536.6733 | 40233.5648
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 400 | 1500 | 1500 | 1300 | 1200 | 1500 | 1400 | 1400 | 1600 | 1300 | 1500 | 1400 | 1200 | 1300 | 1300 | 1400 | 1500 | 1500 | 1400 | 25600
16 | Specific power consumption of Chiller | (iKW/TR) | [8 empty] | 0.59133 | 0.51905 | 0.54162 | 0.69723 | 0.58134 | 0.58919 | 0.70182 | 0.51905 | 0.62286 | 0.57369 | 0.50502 | 0.59538 | 0.62286 | 0.63189 | 0.60668 | 0.59133 | 0.5519 | 0.59072
17 | Average iKW/TR |  |  | Hours 7: 0.59072 | 0.59072
18 | COP of chiller | [9 empty] | 5.946 | 6.7739 | 6.4916 | 5.0428 | 6.0481 | 5.9675 | 5.0098 | 6.7739 | 5.6449 | 6.1287 | 6.962 | 5.9054 | 5.6449 | 5.5643 | 5.7954 | 5.946 | 6.3707 | 6.0009
19 | EER of Chiller | [9 empty] | 20.2936 | 23.1193 | 22.156 | 17.211 | 20.6422 | 20.367 | 17.0986 | 23.1193 | 19.266 | 20.9174 | 23.7615 | 20.1552 | 19.266 | 18.9908 | 19.7798 | 20.2936 | 21.7431 | 20.4812
20 | LMTD of Condenser | ºC | [8 empty] | 2.0332 | 2.2385 | 1.9012 | 1.8475 | 2.1574 | 2.1846 | 2.007 | 2.1367 | 1.8714 | 2.0332 | 2.0332 | 1.7452 | 1.8475 | 1.7452 | 1.9211 | 1.9458 | 1.2717 | 1.9365
21 | LMTD of Evaporator | ºC | [8 empty] | 4.3046 | 4.275 | 3.6134 | 3.5552 | 4.055 | 4.0255 | 3.9366 | 4.275 | 3.6471 | 3.9507 | 3.619 | 3.4491 | 3.4967 | 3.4776 | 3.7029 | 3.8994 | 3.8994 | 3.8343
Performance Sheet Chiller
Date :- 26/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.3 | 1.3 | 1.3 | 1.2 | 1.1 | 1.2 | 1.4 | 1.2 | 1.1 | 0.9 | 1 | 1.2 | 1.2 |  |  | 1.2 | 1.2 | 1.2 | 1 | 1 |  |  |  |  | 1.1667
2 | Small temperature difference of evaporator | ºC |  | 0.7 | 0.7 | 0.8 | 0.7 | 0.7 | 0.8 | 0.8 | 0.7 | 0.7 | 0.6 | 0.7 | 0.8 | 0.7 |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 |  |  |  |  | 0.72778
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.7 | 13.9 | 14.4 | 14.6 | 14.9 | 15.4 | 15.8 | 15.6 | 14.4 | 14 | 13.7 | 13.7 | 12.9 |  |  | 14.2 | 13.5 | 12.8 | 12.2 | 11.9 |  |  |  |  | 13.9778
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.8 | 5.9 | 6.2 | 6.6 | 6.9 | 7.4 | 7.9 | 8 | 6.8 | 7.1 | 7.1 | 5.8 | 5.4 |  |  | 6.6 | 5.8 | 5.4 | 5.5 | 5.5 |  |  |  |  | 6.4278
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 21.7 | 21.6 | 22.3 | 22.7 | 22.8 | 23.7 | 24.1 | 24.5 | 23.8 | 23.2 | 23.4 | 23.7 | 24.2 |  |  | 25.3 | 23.7 | 23.2 | 23.3 | 23.1 |  |  |  |  | 23.35
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.6 | 27.5 | 28.2 | 28.8 | 28.8 | 29.6 | 30.1 | 30.3 | 29.7 | 28.4 | 28.6 | 29.7 | 30 |  |  | 31.2 | 29.7 | 28.9 | 28 | 27.9 |  |  |  |  | 29.0556
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  |  | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  |  | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  | 3 | 3 | 3 | 3 | 3 |  |  |  |  | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  |  | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  | 971 | 971 | 971 | 971 | 971 |  |  |  |  | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2568.7831 | 2633.0026 | 2568.7831 | 2568.7831 | 2568.7831 | 2536.6733 | 2440.3439 | 2440.3439 | 2215.5754 | 2119.246 | 2536.6733 | 2408.2341 |  |  | 2440.3439 | 2472.4537 | 2376.1243 | 2151.3558 | 2055.0265 |  |  |  |  | 43637.2024
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1700 | 1100 | 1900 | 1500 | 1500 | 1500 | 1400 | 1200 | 1500 | 1600 |  |  |  | 1300 | 1600 | 1400 | 1300 | 700 |  |  |  | 1400 | 25600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.59133 | 0.58393 | 0.64565 | 0.42822 | 0.73965 | 0.58393 | 0.59133 | 0.61467 | 0.57369 | 0.54162 | 0.7078 | 0.63075 |  |  |  | 0.53271 | 0.64713 | 0.58919 | 0.60427 | 0.34063 |  |  |  |  | 0.58509
17 | Average iKW/TR |  |  | Hours 7: 0.58509 | 0.58509
18 | COP of chiller |  |  | 5.946 | 6.0212 | 5.4457 | 8.2108 | 4.7536 | 6.0212 | 5.946 | 5.7202 | 6.1287 | 6.4916 | 4.9675 | 5.5743 |  |  |  | 6.6002 | 5.4332 | 5.9675 | 5.8186 | 10.3221 |  |  |  |  | 6.1981
19 | EER of Chiller |  |  | 20.2936 | 20.5504 | 18.5861 | 28.0233 | 16.224 | 20.5504 | 20.2936 | 19.5229 | 20.9174 | 22.156 | 16.9541 | 19.0252 |  |  |  | 22.5265 | 18.5436 | 20.367 | 19.8588 | 35.2293 |  |  |  |  | 21.1543
20 | LMTD of Condenser | ºC |  | 3.4468 | 3.4468 | 3.4468 | 3.3785 | 3.2175 | 3.3188 | 3.6036 | 3.2887 | 3.1882 | 2.7173 | 2.85 | 3.3487 | 3.2887 |  |  | 3.3188 | 3.3487 | 3.2586 | 2.7004 | 2.7306 |  |  |  |  | 3.2165
21 | LMTD of Evaporator | ºC |  | 3.1494 | 3.1746 | 3.3879 | 3.1746 | 3.1746 | 3.3363 | 3.3103 | 3.0733 | 3.0733 | 2.7319 | 2.815 | 3.3103 | 3.0478 |  |  | 3.2322 | 3.2583 | 3.1797 | 2.9937 | 2.4384 |  |  |  |  | 3.1034

## 27-03-2023
Performance Sheet Chiller
Date :- 27/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.6 | 0.6 | 0.5 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.5 | 0.4 | 0.6 | 0.6 | 0.7 | 0.6 | 0.53333
2 | Small temperature difference of evaporator | ºC |  | 1.6 | 1.4 | 1.4 | 1.4 | 1.3 | 1.4 | 1.4 | 1.4 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.2 | 1.3 | 1.4 | 1.5 | 1.6 | 1.6 | 1.35
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.9 | 13.5 | 12.6 | 12.5 | 14.1 | 14.6 | 14 | 13.8 | 13.7 | 13.8 | 14 | 13.8 | 13.3 | 13.1 | 13.2 | 13.4 | 13.2 | 13.1 | 12.8 | 12.1 | 12.5 | 13.5 | 14.2 | 14.6 | 13.5125
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7 | 5.9 | 5.5 | 5.6 | 6.5 | 7.3 | 6.9 | 6.9 | 7.1 | 7.1 | 7.1 | 6.9 | 7.1 | 7.1 | 7.2 | 6.9 | 6.9 | 7.1 | 5.5 | 5.4 | 5.6 | 5.7 | 6.3 | 6.6 | 6.55
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.5 | 23.7 | 24 | 24.3 | 24.5 | 25.8 | 25.3 | 25.5 | 25.4 | 25.4 | 25.4 | 25.2 | 24.8 | 24.7 | 24.4 | 24.4 | 24.3 | 24.2 | 24.6 | 24.6 | 24.6 | 24.7 | 24.7 | 25.2 | 24.7167
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.6 | 28.6 | 28.7 | 28.7 | 29.5 | 30.4 | 29.9 | 29.8 | 29.7 | 29.9 | 29.9 | 29.7 | 28.7 | 28.6 | 28.3 | 28.5 | 28.2 | 28.3 | 29.4 | 30.2 | 29 | 29.8 | 30 | 30.3 | 29.2792
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2536.6733 | 2440.3439 | 2279.795 | 2215.5754 | 2440.3439 | 2344.0146 | 2279.795 | 2215.5754 | 2119.246 | 2151.3558 | 2215.5754 | 2215.5754 | 1990.8069 | 1926.5873 | 1926.5873 | 2087.1362 | 2022.9167 | 1926.5873 | 2344.0146 | 2151.3558 | 2215.5754 | 2504.5635 | 2536.6733 | 2568.7831 | 53655.4563
15 | Power Consumption of Chiller | KWH |  | 1500 | 1400 | 1400 | 1400 | 1500 | 1300 | 1400 | 1300 | 1300 | 1400 | 1300 | 1200 | 1200 | 1100 | 1300 | 1200 | 1200 | 1500 | 1300 | 1300 | 1600 | 1500 | 1600 | 1500 | 32700
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.59133 | 0.57369 | 0.61409 | 0.63189 | 0.61467 | 0.5546 | 0.61409 | 0.58676 | 0.61343 | 0.65075 | 0.58676 | 0.54162 | 0.60277 | 0.57096 | 0.67477 | 0.57495 | 0.5932 | 0.77858 | 0.5546 | 0.60427 | 0.72216 | 0.59891 | 0.63075 | 0.58393 | 0.61098
17 | Average iKW/TR |  |  | Hours 7: 0.61098 | 0.61098
18 | COP of chiller |  |  | 5.946 | 6.1287 | 5.7255 | 5.5643 | 5.7202 | 6.3397 | 5.7255 | 5.9923 | 5.7317 | 5.403 | 5.9923 | 6.4916 | 5.8331 | 6.1581 | 5.2107 | 6.1153 | 5.9271 | 4.5159 | 6.3397 | 5.8186 | 4.8687 | 5.8707 | 5.5743 | 6.0212 | 5.7923
19 | EER of Chiller |  |  | 20.2936 | 20.9174 | 19.5413 | 18.9908 | 19.5229 | 21.6373 | 19.5413 | 20.4516 | 19.5624 | 18.4404 | 20.4516 | 22.156 | 19.9082 | 21.0175 | 17.784 | 20.8716 | 20.2293 | 15.4128 | 21.6373 | 19.8588 | 16.617 | 20.0367 | 19.0252 | 20.5504 | 19.769
20 | LMTD of Condenser | ºC |  | 2.2654 | 2.2116 | 2.007 | 1.7707 | 2.0852 | 1.9807 | 1.9807 | 1.9012 | 2.0476 | 2.1027 | 2.1027 | 1.9543 | 1.9356 | 1.7933 | 1.6422 | 1.694 | 1.7933 | 1.9918 | 2.0332 | 2.0679 | 2.0752 | 2.2654 | 2.4669 | 2.2654 | 2.0181
21 | LMTD of Evaporator | ºC |  | 4.435 | 4.0844 | 3.9366 | 3.8769 | 3.9507 | 3.9959 | 3.9366 | 3.8769 | 3.7866 | 3.6872 | 3.7464 | 3.7464 | 3.5377 | 3.3487 | 3.3487 | 3.4967 | 3.4378 | 3.2175 | 3.7288 | 3.6872 | 3.8769 | 4.275 | 4.435 | 4.4649 | 3.8298
Performance Sheet Chiller
Date :- 27/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.2 | 1.1 |  |  | 1 | 1 | 1.1 | 1.1 | 1.2 | 1.2 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.3 | 0.9 | 1 | 1.2 |  |  |  | 1.2 | 1.1316
2 | Small temperature difference of evaporator | ºC |  | 0.8 | 0.9 | 0.8 |  |  | 0.9 | 0.9 | 0.7 | 0.8 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.9 | 1 | 1.4 | 1.3 | 1.5 | 1.7 |  |  |  | 2.1 | 1.0158
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.9 | 13.5 | 12.7 |  |  | 14.5 | 13.8 | 13.7 | 13.6 | 13.6 | 14 | 13.9 | 13.2 | 13.1 | 13.1 | 13.3 | 13.2 | 13.1 | 12.8 | 12.1 |  |  |  | 14.4 | 13.5
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.1 | 6.1 | 5.6 |  |  | 7.3 | 7 | 7 | 7 | 7 | 7 | 6.9 | 7.1 | 7 | 7.1 | 7 | 7.2 | 6.9 | 6.3 | 6.3 |  |  |  | 7.6 | 6.8684
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.2 | 23.4 | 23.9 |  |  | 25.6 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.1 | 24.4 | 24.4 | 24.2 | 24.4 | 24.1 | 24.1 | 24.2 | 24.3 |  |  |  | 25 | 24.5421
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.3 | 29.1 | 29.6 |  |  | 31.4 | 30.4 | 30.4 | 30.4 | 30.4 | 30.3 | 30.3 | 29.3 | 29.1 | 28.9 | 29.6 | 29.2 | 29.2 | 30.1 | 25.4 |  |  |  | 31.1 | 29.6579
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 |  |  |  | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 |  |  |  | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2504.5635 | 2376.1243 | 2279.795 |  |  | 2311.9048 | 2183.4656 | 2151.3558 | 2119.246 | 2119.246 | 2247.6852 | 2247.6852 | 1958.6971 | 1958.6971 | 1926.5873 | 2022.9167 | 1926.5873 | 1990.8069 | 2087.1362 | 1862.3677 |  |  |  | 2183.4656 | 40458.3333
15 | Power Consumption of Chiller | KWH |  | 1500 | 1500 | 1500 |  |  | 1400 | 1300 | 1400 | 1300 | 1400 | 1300 | 1200 | 1200 | 1300 | 1400 | 1300 | 1400 | 1600 | 800 | 1200 |  |  |  | 1500 | 25500
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.59891 | 0.63128 | 0.65795 |  |  | 0.60556 | 0.59538 | 0.65075 | 0.61343 | 0.66061 | 0.57837 | 0.53388 | 0.61265 | 0.66371 | 0.72667 | 0.64264 | 0.72667 | 0.80369 | 0.3833 | 0.64434 |  |  |  | 0.68698 | 0.63246
17 | Average iKW/TR |  |  | Hours 7: 0.63246 | 0.63246
18 | COP of chiller |  |  | 5.8707 | 5.5696 | 5.3438 |  |  | 5.8062 | 5.9054 | 5.403 | 5.7317 | 5.3223 | 6.0791 | 6.5857 | 5.739 | 5.2975 | 4.8385 | 5.4712 | 4.8385 | 4.3748 | 9.173 | 5.4567 |  |  |  | 5.118 | 5.6803
19 | EER of Chiller |  |  | 20.0367 | 19.0092 | 18.2385 |  |  | 19.8165 | 20.1552 | 18.4404 | 19.5624 | 18.1651 | 20.748 | 22.4771 | 19.5871 | 18.0804 | 16.5138 | 18.6732 | 16.5138 | 14.9312 | 31.3073 | 18.6238 |  |  |  | 17.4679 | 19.3867
20 | LMTD of Condenser | ºC |  | 3.3785 | 3.2586 | 3.1291 |  |  | 3.0257 | 2.85 | 2.9795 | 2.9795 | 3.1064 | 3.0756 | 2.9795 | 2.8884 | 2.9511 | 2.9511 | 3.1064 | 3.1996 | 2.6883 | 3.0546 | 1.6908 |  |  |  | 3.3785 | 2.9827
21 | LMTD of Evaporator | ºC |  | 3.2843 | 3.3309 | 3.1004 |  |  | 3.2769 | 3.1678 | 2.8412 | 2.9668 | 2.815 | 2.9192 | 2.9192 | 2.8311 | 2.683 | 2.9457 | 3.1692 | 3.6036 | 3.5377 | 3.883 | 3.9076 |  |  |  | 4.7088 | 3.2574
z
z

## 28-03-2023
Performance Sheet Chiller
Date :- 28/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.7 | 0.5 | 0.5 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.6 | 0.5 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.6 | 0.57917
2 | Small temperature difference of evaporator | ºC |  | 1.6 | 1.4 | 1.3 | 1.2 | 1.2 | 1.3 | 1.6 | 1.6 | 1.5 | 1.6 | 1.5 | 1.3 | 1.2 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.2 | 1.1 | 1.2 | 1.1 | 1.1 | 1.1 | 1.3083
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13.1 | 12.6 | 12.2 | 12 | 13.6 | 14.9 | 15.3 | 14.6 | 14.1 | 13.9 | 13.8 | 13.9 | 13.9 | 13.7 | 13.5 | 13.4 | 13.4 | 13.4 | 12.8 | 12.4 | 12.1 | 11.9 | 11.9 | 11.9 | 13.2625
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 5.6 | 5.4 | 5.3 | 5.4 | 5.9 | 6.8 | 7.5 | 6.9 | 6.4 | 6.9 | 7 | 7.1 | 7 | 7 | 6.9 | 6.9 | 7.1 | 7 | 6.8 | 6.9 | 7 | 6.9 | 7.1 | 6.9 | 6.6542
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.6 | 24.6 | 24.7 | 24.6 | 24.9 | 25.8 | 25.9 | 25.9 | 25.5 | 25.6 | 25.4 | 24.8 | 24.7 | 24.8 | 24.6 | 24.6 | 24.5 | 24.7 | 24.5 | 24.2 | 24.1 | 24.2 | 24.1 | 24.4 | 24.8208
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 29.3 | 29.2 | 29.2 | 28.8 | 29.9 | 30.9 | 31.1 | 30.9 | 30.4 | 30.2 | 29.7 | 29.3 | 28.9 | 29.2 | 28.9 | 28.7 | 28.7 | 28.8 | 28.3 | 27.7 | 27.2 | 27.3 | 27.2 | 27.3 | 29.0458
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2311.9048 | 2215.5754 | 2119.246 | 2472.4537 | 2600.8929 | 2504.5635 | 2472.4537 | 2472.4537 | 2247.6852 | 2183.4656 | 2183.4656 | 2215.5754 | 2151.3558 | 2119.246 | 2087.1362 | 2022.9167 | 2055.0265 | 1926.5873 | 1766.0384 | 1637.5992 | 1605.4894 | 1541.2698 | 1605.4894 | 50926.1243
15 | Power Consumption of Chiller | KWH |  | 1500 | 1400 | 1200 | 1600 | 1600 | 1600 | 1500 | 1500 | 1500 | 1300 | 1200 | 1300 | 1300 | 1300 | 1300 | 1200 | 1300 | 1200 | 1100 | 1000 | 1000 | 1000 | 1000 | 1000 | 30900
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.62286 | 0.60556 | 0.54162 | 0.75499 | 0.64713 | 0.61517 | 0.59891 | 0.60668 | 0.60668 | 0.57837 | 0.54959 | 0.59538 | 0.58676 | 0.60427 | 0.61343 | 0.57495 | 0.64264 | 0.58393 | 0.57096 | 0.56624 | 0.61065 | 0.62286 | 0.64882 | 0.62286 | 0.60714
17 | Average iKW/TR |  |  | Hours 7: 0.60714 | 0.60714
18 | COP of chiller |  |  | 5.6449 | 5.8062 | 6.4916 | 4.657 | 5.4332 | 5.7155 | 5.8707 | 5.7954 | 5.7954 | 6.0791 | 6.3976 | 5.9054 | 5.9923 | 5.8186 | 5.7317 | 6.1153 | 5.4712 | 6.0212 | 6.1581 | 6.2094 | 5.7578 | 5.6449 | 5.4191 | 5.6449 | 5.8157
19 | EER of Chiller |  |  | 19.266 | 19.8165 | 22.156 | 15.8945 | 18.5436 | 19.5069 | 20.0367 | 19.7798 | 19.7798 | 20.748 | 21.8349 | 20.1552 | 20.4516 | 19.8588 | 19.5624 | 20.8716 | 18.6732 | 20.5504 | 21.0175 | 21.1927 | 19.6514 | 19.266 | 18.4954 | 19.266 | 19.849
20 | LMTD of Condenser | ºC |  | 2.3005 | 1.9807 | 1.9543 | 2.1584 | 2.3842 | 2.2654 | 2.2921 | 2.2385 | 2.3564 | 2.2723 | 2.0476 | 1.9543 | 2.0198 | 2.0752 | 1.9012 | 1.9918 | 2.0198 | 1.9918 | 1.9072 | 1.6831 | 1.5704 | 1.4292 | 1.4292 | 1.6444 | 1.9945
21 | LMTD of Evaporator | ºC |  | 4.3146 | 3.9663 | 3.7464 | 3.526 | 3.8428 | 4.0943 | 4.405 | 4.375 | 4.2454 | 4.1623 | 3.9748 | 3.7169 | 3.6134 | 3.6872 | 3.6575 | 3.6277 | 3.4378 | 3.4673 | 3.3487 | 3.0696 | 3.0756 | 2.9189 | 2.8578 | 2.9189 | 3.6688
Performance Sheet Chiller
Date :- 28/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.2 | 1.2 | 1.3 |  |  |  | 1.1 | 1.2 | 1.2 | 1.3 | 1 | 0.9 | 1 | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.4 | 1.1381
2 | Small temperature difference of evaporator | ºC |  | 2.1 | 2.2 | 2.4 |  |  |  | 0.8 | 0.8 | 0.7 | 0.9 | 0.8 | 0.7 | 0.8 | 0.8 | 0.6 | 0.7 | 0.7 | 0.7 | 0.9 | 1.2 | 1.6 | 2.2 | 2.6 | 2.6 | 1.2762
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 13 | 12.8 | 12.1 |  |  |  | 15.2 | 14.4 | 14 | 13.7 | 13.7 | 13.8 | 13.7 | 13.8 | 13.4 | 13.3 | 13.4 | 13.3 | 12.8 | 12.5 | 12.1 | 11.7 | 11.6 | 11.8 | 13.1476
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7 | 6.8 | 6.1 |  |  |  | 7.7 | 7.1 | 6.5 | 7 | 7.1 | 7.2 | 7.2 | 7.1 | 6.8 | 7.1 | 7.1 | 7.2 | 6.9 | 7 | 7.1 | 6.9 | 7 | 7.1 | 7
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.4 | 24.3 | 24.5 |  |  |  | 25.8 | 25.8 | 25.6 | 25.6 | 25.2 | 24.8 | 24.4 | 24.4 | 24.5 | 24.5 | 24.2 | 24.7 | 24.5 | 23.9 | 23.7 | 24.1 | 23.7 | 23.7 | 24.5857
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30 | 29.9 | 30 |  |  |  | 31.7 | 31.4 | 31.1 | 30.8 | 30.3 | 30.1 | 29.7 | 29.7 | 29.4 | 29.3 | 29.3 | 29.4 | 28.9 | 28.1 | 28 | 28.3 | 28.3 | 28.6 | 29.6333
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 |  |  |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 |  |  |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 |  |  |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 1926.5873 | 1926.5873 | 1926.5873 |  |  |  | 2408.2341 | 2344.0146 | 2408.2341 | 2151.3558 | 2119.246 | 2119.246 | 2087.1362 | 2151.3558 | 2119.246 | 1990.8069 | 2022.9167 | 1958.6971 | 1894.4775 | 1766.0384 | 1605.4894 | 1541.2698 | 1477.0503 | 1509.1601 | 41453.7368
15 | Power Consumption of Chiller | KWH |  | 1500 | 1700 | 1500 |  |  |  | 1500 | 1500 | 1500 | 1300 | 1400 | 1400 | 1300 | 1300 | 1200 | 1300 | 1300 | 1200 | 1100 | 1200 | 1200 | 1200 | 1200 | 1200 | 28000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.77858 | 0.88239 | 0.77858 |  |  |  | 0.62286 | 0.63993 | 0.62286 | 0.60427 | 0.66061 | 0.66061 | 0.62286 | 0.60427 | 0.56624 | 0.653 | 0.64264 | 0.61265 | 0.58064 | 0.67949 | 0.74744 | 0.77858 | 0.81243 | 0.79514 | 0.68315
17 | Average iKW/TR |  |  | Hours 7: 0.68315 | 0.68315
18 | COP of chiller |  |  | 4.5159 | 3.9846 | 4.5159 |  |  |  | 5.6449 | 5.4944 | 5.6449 | 5.8186 | 5.3223 | 5.3223 | 5.6449 | 5.8186 | 6.2094 | 5.3844 | 5.4712 | 5.739 | 6.0554 | 5.1745 | 4.7041 | 4.5159 | 4.3278 | 4.4218 | 5.2253
19 | EER of Chiller |  |  | 15.4128 | 13.5996 | 15.4128 |  |  |  | 19.266 | 18.7523 | 19.266 | 19.8588 | 18.1651 | 18.1651 | 19.266 | 19.8588 | 21.1927 | 18.3768 | 18.6732 | 19.5871 | 20.6672 | 17.6605 | 16.055 | 15.4128 | 14.7706 | 15.0917 | 17.8339
20 | LMTD of Condenser | ºC |  | 3.2284 | 3.2284 | 3.3241 |  |  |  | 3.1882 | 3.2284 | 3.1981 | 3.2309 | 2.8203 | 2.7462 | 2.8796 | 3.1371 | 2.8884 | 2.8578 | 2.9493 | 2.827 | 2.7339 | 2.6711 | 2.7026 | 2.6711 | 2.7961 | 3.2578 | 2.9793
21 | LMTD of Evaporator | ºC |  | 4.4447 | 4.5604 | 4.7894 |  |  |  | 3.206 | 3.1533 | 3.0478 | 3.1404 | 2.9668 | 2.815 | 2.9398 | 2.9937 | 2.656 | 2.7096 | 2.7361 | 2.683 | 2.9175 | 3.1981 | 3.5284 | 4.147 | 4.5161 | 4.5527 | 3.4144
z
z

## 29-03-2023
Performance Sheet Chiller
Date :- 29/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.4 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.6 | 0.7 | 0.6 | 0.6 | 0.5 | 0.6 | 0.55
2 | Small temperature difference of evaporator | ºC |  | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 1.2 | 1.3 | 1.3 | 1.2 | 1.3 | 1.2 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1.1625
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 11.9 | 11.9 | 12.1 | 12.7 | 12.9 | 12.9 | 13.2 | 13.4 | 13.6 | 13.6 | 13.6 | 13.7 | 13.2 | 13.3 | 13.2 | 13.2 | 13.1 | 12.3 | 11.9 | 11.7 | 11.6 | 11.4 | 11.5 | 11.3 | 12.6333
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.9 | 6.9 | 7.2 | 7.2 | 7.3 | 7.1 | 7.1 | 7.1 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 7.1 | 7.2 | 7.1 | 7 | 6.9 | 7 | 7 | 7 | 7 | 7 | 7 | 7.025
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.3 | 24.6 | 24.7 | 24.6 | 25.9 | 25.8 | 25.6 | 25.7 | 25.5 | 25.3 | 25.1 | 25 | 25 | 25.1 | 24.8 | 24.8 | 24.5 | 24.6 | 24.4 | 24.1 | 24 | 23.8 | 23.6 | 24.1 | 24.7875
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 27.5 | 27.6 | 27.9 | 28.1 | 29.6 | 29.6 | 29.6 | 29.8 | 29.8 | 29.6 | 29.3 | 29.3 | 29 | 29.1 | 29 | 28.7 | 28.4 | 28.1 | 27.4 | 27.2 | 26.9 | 26.6 | 26.4 | 26.9 | 28.3917
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 1605.4894 | 1605.4894 | 1573.3796 | 1766.0384 | 1798.1481 | 1862.3677 | 1958.6971 | 2022.9167 | 2151.3558 | 2151.3558 | 2151.3558 | 2183.4656 | 2022.9167 | 1990.8069 | 1926.5873 | 1958.6971 | 1958.6971 | 1733.9286 | 1573.3796 | 1509.1601 | 1477.0503 | 1412.8307 | 1444.9405 | 1380.7209 | 43219.7751
15 | Power Consumption of Chiller | KWH |  | 1000 | 1000 | 1100 | 1200 | 1200 | 1200 | 1300 | 1300 | 1200 | 1300 | 1300 | 1300 | 1200 | 1300 | 1200 | 1100 | 1100 | 1000 | 1000 | 900 | 1000 | 900 | 900 | 1000 | 27000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.62286 | 0.62286 | 0.69913 | 0.67949 | 0.66735 | 0.64434 | 0.66371 | 0.64264 | 0.55779 | 0.60427 | 0.60427 | 0.59538 | 0.5932 | 0.653 | 0.62286 | 0.5616 | 0.5616 | 0.57673 | 0.63557 | 0.59636 | 0.67703 | 0.63702 | 0.62286 | 0.72426 | 0.62776
17 | Average iKW/TR |  |  | Hours 7: 0.62776 | 0.62776
18 | COP of chiller |  |  | 5.6449 | 5.6449 | 5.0291 | 5.1745 | 5.2686 | 5.4567 | 5.2975 | 5.4712 | 6.3035 | 5.8186 | 5.8186 | 5.9054 | 5.9271 | 5.3844 | 5.6449 | 6.2607 | 6.2607 | 6.0965 | 5.532 | 5.8958 | 5.1933 | 5.5195 | 5.6449 | 4.8546 | 5.627
19 | EER of Chiller |  |  | 19.266 | 19.266 | 17.1643 | 17.6605 | 17.9816 | 18.6238 | 18.0804 | 18.6732 | 21.5138 | 19.8588 | 19.8588 | 20.1552 | 20.2293 | 18.3768 | 19.266 | 21.3678 | 21.3678 | 20.8073 | 18.8807 | 20.1223 | 17.7248 | 18.8379 | 19.266 | 16.5688 | 19.2049
20 | LMTD of Condenser | ºC |  | 1.4564 | 1.4018 | 1.4564 | 1.8212 | 1.8787 | 1.766 | 1.8205 | 1.8475 | 1.7452 | 2.0476 | 2.0198 | 2.0476 | 2.1006 | 1.9638 | 2.0198 | 1.9356 | 1.7933 | 1.6831 | 1.6743 | 1.8325 | 1.6444 | 1.6142 | 1.4838 | 1.6142 | 1.7778
21 | LMTD of Evaporator | ºC |  | 2.9189 | 2.9189 | 2.8884 | 3.0696 | 3.2284 | 3.2887 | 3.3785 | 3.4378 | 3.5552 | 3.6872 | 3.5552 | 3.7169 | 3.5678 | 3.4082 | 3.4772 | 3.3785 | 3.2468 | 3.0397 | 2.8884 | 2.827 | 2.7961 | 2.7339 | 2.7651 | 2.5784 | 3.1813
Performance Sheet Chiller
Date :- 29/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1 | 1 | 1 | 1.2 | 1.3 | 1.2 | 1.1 | 1.1 | 1.1 | 1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.3 | 1.4 | 1.2 | 1.1 | 1.2 | 1.2 | 1.3 | 1.3 | 1.5 | 1.3 | 1.1875
2 | Small temperature difference of evaporator | ºC |  | 2.3 | 2.4 | 2.4 | 2.4 | 2.6 | 2.2 | 2.2 | 2.5 | 2.1 | 3.1 | 3 | 2.6 | 2.5 | 2.4 | 2.6 | 2.8 | 2.9 | 2.9 | 2.7 | 2.9 | 3.1 | 3.2 | 3.2 | 3.2 | 2.675
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 11.8 | 11.8 | 12 | 12.7 | 12.9 | 12.7 | 13.1 | 13.4 | 13.5 | 13.4 | 13.5 | 13.6 | 13.2 | 13.5 | 13.4 | 13.2 | 12.9 | 12.4 | 11.9 | 11.6 | 11.5 | 11.5 | 11.4 | 11.2 | 12.5875
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.8 | 7.2 | 6.4 | 6.9 | 7.2 | 7.6 | 7.8 | 8 | 8.6 | 8 | 8.4 | 8.1 | 7.9 | 7.8 | 8.8 | 8.2 | 7.7 | 7.1 | 6.7 | 7 | 7.1 | 7.1 | 7 | 7.6 | 7.5417
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.2 | 24.2 | 24.5 | 24.3 | 25.4 | 25.6 | 25.4 | 25.6 | 25.3 | 25.2 | 25.1 | 24.8 | 24.9 | 25.1 | 24.6 | 24.6 | 24.3 | 24.5 | 24.1 | 24 | 23.8 | 23.5 | 23.4 | 23.9 | 24.5958
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.9 | 28.8 | 29.6 | 29.7 | 31.2 | 30.8 | 30.9 | 30.9 | 30.7 | 30.6 | 30.4 | 30.4 | 30.4 | 30.3 | 30.4 | 30 | 30.1 | 29.9 | 29.3 | 29.3 | 28.8 | 28.4 | 28.3 | 28.6 | 29.8625
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 1605.4894 | 1477.0503 | 1798.1481 | 1862.3677 | 1830.2579 | 1637.5992 | 1701.8188 | 1733.9286 | 1573.3796 | 1733.9286 | 1637.5992 | 1766.0384 | 1701.8188 | 1830.2579 | 1477.0503 | 1605.4894 | 1669.709 | 1701.8188 | 1669.709 | 1477.0503 | 1412.8307 | 1412.8307 | 1412.8307 | 1155.9524 | 38884.9537
15 | Power Consumption of Chiller | KWH |  | 1300 | 1300 | 1500 | 1600 | 1300 | 1400 | 1500 | 1400 | 1500 | 1400 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1400 | 1300 | 1200 | 1400 | 1300 | 1300 | 34100
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.80972 | 0.88013 | 0.83419 | 0.85912 | 0.71028 | 0.85491 | 0.88141 | 0.80742 | 0.95336 | 0.80742 | 0.91598 | 0.84936 | 0.88141 | 0.81956 | 1.0155 | 0.93429 | 0.89836 | 0.88141 | 0.83847 | 0.88013 | 0.84936 | 0.99092 | 0.92014 | 1.1246 | 0.88323
17 | Average iKW/TR |  |  | Hours 7: 0.88323 | 0.88323
18 | COP of chiller |  |  | 4.3422 | 3.9949 | 4.2149 | 4.0926 | 4.9501 | 4.1127 | 3.9891 | 4.3546 | 3.688 | 4.3546 | 3.8385 | 4.1396 | 3.9891 | 4.2901 | 3.4622 | 3.7633 | 3.9138 | 3.9891 | 4.1934 | 3.9949 | 4.1396 | 3.5482 | 3.8212 | 3.1264 | 4.0126
19 | EER of Chiller |  |  | 14.82 | 13.6344 | 14.3853 | 13.9679 | 16.8948 | 14.0367 | 13.6147 | 14.8624 | 12.5872 | 14.8624 | 13.1009 | 14.1284 | 13.6147 | 14.6422 | 11.8165 | 12.844 | 13.3578 | 13.6147 | 14.3119 | 13.6344 | 14.1284 | 12.1101 | 13.0416 | 10.6704 | 13.6951
20 | LMTD of Condenser | ºC |  | 2.7004 | 2.6701 | 2.8203 | 3.1676 | 3.4163 | 3.1064 | 3.0696 | 3.0097 | 3.0397 | 2.909 | 3.0097 | 3.2284 | 3.1981 | 3.1064 | 3.4163 | 3.4167 | 3.2887 | 3.0397 | 3.1064 | 3.1371 | 3.1682 | 3.1366 | 3.3774 | 3.0731 | 3.1088
21 | LMTD of Evaporator | ºC |  | 4.3291 | 4.2973 | 4.6513 | 4.7206 | 4.9106 | 4.2521 | 4.3214 | 4.6933 | 4.0699 | 5.3536 | 5.1346 | 4.84 | 4.658 | 4.686 | 4.5161 | 4.8804 | 5.0625 | 5.099 | 4.8435 | 4.8411 | 4.9802 | 5.0867 | 5.0867 | 4.776 | 4.7538
z
z

## 30-03-2023
Performance Sheet Chiller
Date :- 30/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.6 | 0.5 | 0.6 | 0.6 | 0.7 | 0.55
2 | Small temperature difference of evaporator | ºC |  | 1 | 0.9 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.2 | 1.1 | 1.1 | 1.7 | 1.2 | 1.1625
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 11.2 | 11.3 | 11.6 | 12.1 | 12.2 | 12.4 | 12.7 | 12.8 | 12.9 | 13.1 | 13.2 | 13.4 | 13.3 | 13.2 | 13.1 | 12.8 | 12.6 | 12.4 | 12.3 | 11.9 | 12.5 | 13.6 | 14.4 | 15.4 | 12.7667
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7 | 7 | 7.1 | 7 | 7 | 7 | 7 | 7.1 | 7 | 7 | 7.1 | 7.1 | 7.1 | 7 | 7 | 7 | 6.9 | 7 | 7 | 5.6 | 5.8 | 5.8 | 6.1 | 7.4 | 6.8375
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.2 | 24.2 | 24.1 | 24.1 | 25.1 | 24.9 | 25 | 25 | 24.9 | 24.9 | 25.2 | 25.2 | 24.9 | 24.9 | 24.8 | 24.8 | 24.6 | 24.6 | 24.4 | 24.9 | 24.7 | 24.9 | 25.2 | 25.1 | 24.775
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 26.9 | 26.9 | 27 | 27.3 | 28.4 | 28.4 | 28.7 | 28.7 | 28.7 | 28.8 | 29.2 | 29.2 | 29 | 28.8 | 28.8 | 28.6 | 28.4 | 28.1 | 27.9 | 29.1 | 29.1 | 30.1 | 30.8 | 30.4 | 28.6375
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 1348.6111 | 1380.7209 | 1444.9405 | 1637.5992 | 1669.709 | 1733.9286 | 1830.2579 | 1830.2579 | 1894.4775 | 1958.6971 | 1958.6971 | 2022.9167 | 1990.8069 | 1990.8069 | 1958.6971 | 1862.3677 | 1830.2579 | 1733.9286 | 1701.8188 | 2022.9167 | 2151.3558 | 2504.5635 | 2665.1124 | 2568.7831 | 45692.2288
15 | Power Consumption of Chiller | KWH |  | 900 | 1000 | 1000 | 1100 | 1100 | 1100 | 1200 | 1200 | 1100 | 1300 | 1200 | 1200 | 1200 | 1200 | 1200 | 1100 | 1100 | 1100 | 1300 | 1300 | 1600 | 1400 | 1600 | 1500 | 29000
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.66735 | 0.72426 | 0.69207 | 0.67172 | 0.6588 | 0.6344 | 0.65565 | 0.65565 | 0.58064 | 0.66371 | 0.61265 | 0.5932 | 0.60277 | 0.60277 | 0.61265 | 0.59065 | 0.60101 | 0.6344 | 0.76389 | 0.64264 | 0.74372 | 0.55898 | 0.60035 | 0.58393 | 0.63949
17 | Average iKW/TR |  |  | Hours 7: 0.63949 | 0.63949
18 | COP of chiller |  |  | 5.2686 | 4.8546 | 5.0804 | 5.2344 | 5.337 | 5.5423 | 5.3627 | 5.3627 | 6.0554 | 5.2975 | 5.739 | 5.9271 | 5.8331 | 5.8331 | 5.739 | 5.9528 | 5.8502 | 5.5423 | 4.6028 | 5.4712 | 4.7276 | 6.29 | 5.8566 | 6.0212 | 5.5326
19 | EER of Chiller |  |  | 17.9816 | 16.5688 | 17.3394 | 17.8649 | 18.2152 | 18.9158 | 18.3027 | 18.3027 | 20.6672 | 18.0804 | 19.5871 | 20.2293 | 19.9082 | 19.9082 | 19.5871 | 20.3169 | 19.9666 | 18.9158 | 15.7092 | 18.6732 | 16.1353 | 21.4679 | 19.9885 | 20.5504 | 18.8826
20 | LMTD of Condenser | ºC |  | 1.4545 | 1.3186 | 1.3743 | 1.5988 | 1.763 | 1.6831 | 1.7385 | 1.8787 | 1.766 | 1.7933 | 1.9638 | 1.9638 | 1.9918 | 1.9356 | 1.9638 | 1.9072 | 1.9072 | 1.8212 | 1.5369 | 2.0198 | 1.9278 | 2.2921 | 2.3979 | 2.4669 | 1.8527
21 | LMTD of Evaporator | ºC |  | 2.5475 | 2.4515 | 2.6397 | 2.9493 | 2.9795 | 3.0397 | 3.1291 | 3.2586 | 3.3188 | 3.3785 | 3.3785 | 3.4378 | 3.4082 | 3.4082 | 3.3785 | 3.2887 | 3.2586 | 3.1676 | 3.0097 | 3.4378 | 3.4204 | 3.7307 | 4.6841 | 3.9276 | 3.2762
Performance Sheet Chiller
Date :- 30/03/2023
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC | [25 empty] | 1 | bar: Hours 5 to Hours 6
2 | Small temperature difference of evaporator | ºC |  | Hours 5: 1.1; Hours 6: 1.1 | 1.1
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | Hours 5: 14.7; Hours 6: 14.7 | 14.7
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | Hours 5: 7; Hours 6: 7 | 7
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | Hours 5: 24.9; Hours 6: 24.9 | 24.9
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | Hours 5: 31.4; Hours 6: 31.4 | 31.4
7 | Chilled water inlet pressure | (Kg/Cm2) |  | Hours 5: 4.3; Hours 6: 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | Hours 5: 3.8; Hours 6: 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | Hours 5: 3.8; Hours 6: 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | Hours 5: 3; Hours 6: 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | Hours 5: 0.5; Hours 6: 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | Hours 5: 0.8; Hours 6: 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | Hours 5: 971; Hours 6: 971 | 971
14 | TR Genrated by Chiller | TR |  | Hours 5: 2472.4537; Hours 6: 2472.4537 | 4944.9074
15 | Power Consumption of Chiller | KWH |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 1400 | 1400 | 3000
16 | Specific power consumption of Chiller | (iKW/TR) |  | Hours 5: 0.56624; Hours 6: 0.56624 | 0.56624
17 | Average iKW/TR |  |  | Hours 7: 0.56624 | 0.56624
18 | COP of chiller |  |  | Hours 5: 6.2094; Hours 6: 6.2094 | 6.2094
19 | EER of Chiller |  |  | Hours 5: 21.1927; Hours 6: 21.1927 | 21.1927
20 | LMTD of Condenser | ºC |  | Hours 5: 3.226; Hours 6: 3.226 | 3.226
21 | LMTD of Evaporator | ºC |  | Hours 5: 3.7029; Hours 6: 3.7029 | 3.7029
Performance Sheet Chiller
Date :- 30/03/2023
CHILLER NO. 6
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 1.3 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.1 | 1.4 | 1 | 1.3 | 1.3 | 1.2 | 1.3 | 1.6 | 1.2 | 1.2 | 1.2 | 1.1 | 1.1 | [5 empty] | 1.2211
2 | Small temperature difference of evaporator | ºC |  | 3.2 | 2.7 | 2.9 | 3.1 | 3.2 | 3.4 | 3 | 3.4 | 2.7 | 2.8 | 2.8 | 2.4 | 3.3 | 3.3 | 3.3 | 3.2 | 3.3 | 2.3 | 3.4 | [5 empty] | 3.0368
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 11.3 | 11.3 | 11.6 | 11.8 | 12.2 | 12.5 | 12.6 | 12.7 | 12.9 | 13.1 | 13.1 | 13.3 | 13.3 | 13.1 | 13.1 | 12.8 | 12.4 | 12.4 | 12.2 | [5 empty] | 12.5105
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.9 | 7 | 7.1 | 7.2 | 7.2 | 7.6 | 7.4 | 7.7 | 7.7 | 7.8 | 7.8 | 8.1 | 8 | 7.9 | 8.1 | 7.7 | 8.2 | 7.7 | 7.8 | [5 empty] | 7.6263
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 23.9 | 23.9 | 23.8 | 24 | 24.7 | 24.7 | 24.9 | 24.7 | 24.7 | 24.7 | 25.1 | 25 | 24.7 | 24.8 | 24.6 | 24.7 | 24.6 | 24.6 | 24.3 | [5 empty] | 24.5474
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 28.9 | 28.9 | 28.9 | 29.3 | 30.3 | 30.7 | 30.3 | 30 | 30.2 | 30.3 | 30.6 | 30.6 | 30.4 | 30.2 | 30.4 | 30.2 | 30.1 | 29.9 | 29.8 | [5 empty] | 30
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | [5 empty] | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [5 empty] | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | [5 empty] | 3.8 | z
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [5 empty] | 3 |  | z
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [5 empty] | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | [5 empty] | 971
14 | TR Genrated by Chiller | TR |  | 1412.8307 | 1380.7209 | 1444.9405 | 1477.0503 | 1605.4894 | 1573.3796 | 1669.709 | 1605.4894 | 1669.709 | 1701.8188 | 1701.8188 | 1669.709 | 1701.8188 | 1669.709 | 1605.4894 | 1637.5992 | 1348.6111 | 1509.1601 | 1412.8307 | [5 empty] | 29797.8836
15 | Power Consumption of Chiller | KWH |  | 1300 | 1400 | 1400 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1600 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1400 | 1000 | 0 | 0 | 0 | 0 | 0 | 27600
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.92014 | 1.014 | 0.9689 | 1.0155 | 0.93429 | 0.95336 | 0.89836 | 0.93429 | 0.89836 | 0.88141 | 0.94017 | 0.89836 | 0.88141 | 0.89836 | 0.93429 | 0.91598 | 1.1123 | 0.92767 | 0.7078 | [5 empty] | 0.92815
17 | Average iKW/TR |  |  | Hours 7: 0.92815 | 0.92815
18 | COP of chiller |  |  | 3.8212 | 3.4676 | 3.6289 | 3.4622 | 3.7633 | 3.688 | 3.9138 | 3.7633 | 3.9138 | 3.9891 | 3.7397 | 3.9138 | 3.9891 | 3.9138 | 3.7633 | 3.8385 | 3.1611 | 3.7901 | 4.9675 | [5 empty] | 3.8152
19 | EER of Chiller |  |  | 13.0416 | 11.8349 | 12.3853 | 11.8165 | 12.844 | 12.5872 | 13.3578 | 12.844 | 13.3578 | 13.6147 | 12.7638 | 13.3578 | 13.6147 | 13.3578 | 12.844 | 13.1009 | 10.789 | 12.9358 | 16.9541 | [5 empty] | 13.0211
20 | LMTD of Condenser | ºC |  | 3.1682 | 2.9189 | 3.0756 | 3.1371 | 3.2284 | 3.3487 | 3.0397 | 3.3852 | 2.9383 | 3.355 | 3.3241 | 3.2284 | 3.3857 | 3.6588 | 3.2887 | 3.1981 | 3.1981 | 3.0097 | 3.0696 | [5 empty] | 3.2082
21 | LMTD of Evaporator | ºC |  | 5.0867 | 4.5137 | 4.8037 | 5.056 | 5.3136 | 5.4903 | 5.1714 | 5.5282 | 4.8435 | 4.9894 | 4.9894 | 4.5112 | 5.5333 | 5.496 | 5.421 | 5.3509 | 5.1158 | 4.2228 | 5.299 | [5 empty] | 5.0914

## 31-03-2-2023
Performance Sheet Chiller
Date :- 31/03/2023
CHILLER NO. 3
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours | [23 empty] | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.6 | 0.6 | 0.7 | 0.6 | 0.7 | 0.6 | 0.6 | 0.6375
2 | Small temperature difference of evaporator | ºC |  | 1.4 | 1.4 | 1.4 | 1.3 | 1.2 | 1.2 | 1.2 | 1.3 | 1.4 | 1.6 | 1.6 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.6 | 1.4 | 1.3 | 1.2 | 1.2 | 1.4 | 1.2 | 1.1 | 1.4125
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.4 | 13.9 | 13.8 | 13.6 | 13.3 | 13.4 | 13.2 | 14 | 14.7 | 14.5 | 14.4 | 14.4 | 14.4 | 14.6 | 14.2 | 14 | 13.8 | 13.4 | 13.1 | 12.9 | 13.3 | 13.3 | 13.3 | 13.3 | 13.8
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 6.9 | 6.8 | 6.9 | 6.9 | 7.1 | 7.2 | 7.2 | 7.4 | 7.4 | 7.3 | 7.2 | 7.1 | 7.1 | 6.8 | 6.6 | 6.4 | 6.6 | 6.4 | 6.4 | 7.3 | 7.6 | 7.6 | 7.4 | 7.3 | 7.0375
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 25.1 | 25.1 | 25.5 | 25.6 | 25.7 | 25.7 | 25.6 | 25.8 | 26.3 | 25.8 | 25.6 | 25.7 | 25.3 | 25.2 | 25.3 | 25.2 | 25.2 | 25 | 24.8 | 24.5 | 24.3 | 24.2 | 24.3 | 24.1 | 25.2042
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.1 | 29.8 | 30 | 29.9 | 29.8 | 29.7 | 29.5 | 30.1 | 31.1 | 30.6 | 30.3 | 30.7 | 30.2 | 30.3 | 30.5 | 30.2 | 29.9 | 29.6 | 29.2 | 28.1 | 28.1 | 28 | 28.1 | 27.8 | 29.65
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2408.2341 | 2279.795 | 2215.5754 | 2151.3558 | 1990.8069 | 1990.8069 | 1926.5873 | 2119.246 | 2344.0146 | 2311.9048 | 2311.9048 | 2344.0146 | 2344.0146 | 2504.5635 | 2440.3439 | 2440.3439 | 2311.9048 | 2247.6852 | 2151.3558 | 1798.1481 | 1830.2579 | 1830.2579 | 1894.4775 | 1926.5873 | 52114.1865
15 | Power Consumption of Chiller | KWH |  | 1400 | 1300 | 1400 | 1200 | 1300 | 1300 | 1300 | 1400 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1600 | 1500 | 1400 | 1300 | 1100 | 1100 | 1200 | 1100 | 1200 | 1100 | 32200
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.58134 | 0.57023 | 0.63189 | 0.55779 | 0.653 | 0.653 | 0.67477 | 0.66061 | 0.63993 | 0.64882 | 0.64882 | 0.63993 | 0.63993 | 0.59891 | 0.65565 | 0.61467 | 0.60556 | 0.57837 | 0.51131 | 0.61174 | 0.65565 | 0.60101 | 0.63342 | 0.57096 | 0.61822
17 | Average iKW/TR |  |  | Hours 7: 0.61822 | 0.61822
18 | COP of chiller |  |  | 6.0481 | 6.166 | 5.5643 | 6.3035 | 5.3844 | 5.3844 | 5.2107 | 5.3223 | 5.4944 | 5.4191 | 5.4191 | 5.4944 | 5.4944 | 5.8707 | 5.3627 | 5.7202 | 5.8062 | 6.0791 | 6.8765 | 5.7475 | 5.3627 | 5.8502 | 5.5508 | 6.1581 | 5.7121
19 | EER of Chiller |  |  | 20.6422 | 21.0445 | 18.9908 | 21.5138 | 18.3768 | 18.3768 | 17.784 | 18.1651 | 18.7523 | 18.4954 | 18.4954 | 18.7523 | 18.7523 | 20.0367 | 18.3027 | 19.5229 | 19.8165 | 20.748 | 23.4695 | 19.6163 | 18.3027 | 19.9666 | 18.9449 | 21.0175 | 19.4953
20 | LMTD of Condenser | ºC |  | 2.2385 | 2.1574 | 1.9543 | 2.0476 | 1.9918 | 1.9638 | 1.9356 | 2.0476 | 2.1846 | 2.1846 | 2.3005 | 2.3842 | 2.3564 | 2.4119 | 2.4395 | 2.524 | 2.3005 | 2.1301 | 2.0752 | 1.9832 | 1.9072 | 2.0422 | 1.9072 | 1.8787 | 2.1394
21 | LMTD of Evaporator | ºC |  | 4.055 | 3.9366 | 3.8769 | 3.6872 | 3.4082 | 3.4082 | 3.3487 | 3.6575 | 3.9959 | 4.2235 | 4.2235 | 4.3802 | 4.3802 | 4.5331 | 4.4722 | 4.4722 | 4.2235 | 3.9068 | 3.6872 | 3.2284 | 3.2586 | 3.5107 | 3.3188 | 3.2175 | 3.8504
Performance Sheet Chiller
Date :- 31/03/2023
CHILLER NO. 5
Design Chilled Water Flow Qed(m3/hr): 971
Design pressure drop across evaporator(ΔPed) Kg/Cm2: 0.53
Design pressure drop across Condenser (ΔPcd) Kg/Cm2: 0.73
Design condenser water Flow Qcd(m3/hr): 1704
Water density(þw): 1000kg/m3
Specific Heat of Water (Cw): 1Kcal/Kg°C
Sl. No. | PERFORMANCE CONCERN AND RELATED INDICATOR | UOM | TARGET / Base Line | Hours 7: Hours | Average/Total
|  |  |  | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | Small temperature difference of condenser | ºC |  | 0.8 | 0.09 | 0.8 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.8 | 0.8 | 0.83292
2 | Small temperature difference of evaporator | ºC |  | 1 | 0.8 | 0.9 | 0.8 | 0.7 | 0.6 | 0.9 | 1.3 | 1.3 | 1.3 | 1.4 | 1.3 | 1.4 | 1.5 | 1.3 | 1.3 | 1.3 | 1.3 | 1.2 | 0.7 | 0.8 | 0.8 | 1 | 1 | 1.0792
3 | Entering Chilled Water Temp. (tchwe) | ºC |  | 14.4 | 13.8 | 13.7 | 13.6 | 13.4 | 13.3 | 13.2 | 13.9 | 14.6 | 14.4 | 14.4 | 14.4 | 14.4 | 14.3 | 14.2 | 13.9 | 13.7 | 13.4 | 12.9 | 12.8 | 13.2 | 13.2 | 13.3 | 13.2 | 13.7333
4 | Leaving Chilled Water Temp. (tchwl) | ºC |  | 7.3 | 7 | 7 | 7 | 7.1 | 7.2 | 7.2 | 7.3 | 7.7 | 7.4 | 7.3 | 7.4 | 7.3 | 7.1 | 7.2 | 7.1 | 6.9 | 6.6 | 6.4 | 7.4 | 7.5 | 7.5 | 7.5 | 7.5 | 7.2042
5 | Entering Condenser Water Temp. (tcwe) | ºC |  | 24.9 | 24.9 | 25.3 | 25.5 | 25.5 | 25.6 | 25.4 | 25.6 | 26.2 | 25.7 | 25.4 | 25.6 | 25.2 | 25.1 | 25.2 | 25.2 | 25.1 | 24.9 | 24.7 | 24.4 | 24.2 | 24.2 | 24.3 | 23.9 | 25.0833
6 | Leaving Condenser Water Temp. (tcwl) | ºC |  | 30.2 | 30.1 | 30.3 | 30.3 | 30.2 | 30.1 | 29.8 | 30.7 | 31.4 | 31.1 | 30.8 | 31 | 30.6 | 30.6 | 30.6 | 30.3 | 30.3 | 30 | 29.7 | 28.4 | 28.5 | 28.5 | 28.5 | 28.3 | 30.0125
7 | Chilled water inlet pressure | (Kg/Cm2) |  | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
8 | Chilled water outlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
9 | Condenser water inlet pressure | (Kg/Cm2) |  | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
10 | Condenser water outlet pressure | (Kg/Cm2) |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
11 | Actual Pressure Drop Across Evaporator (ΔPea) | (Kg/Cm2) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
12 | Actual Pressure Drop Across Condenser (ΔPca) | (Kg/Cm2) |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
13 | Actual chilled water flow (Qea) based on ΔPea | (m3/hr.) |  | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971 | 971
14 | TR Genrated by Chiller | TR |  | 2279.795 | 2183.4656 | 2151.3558 | 2119.246 | 2022.9167 | 1958.6971 | 1926.5873 | 2119.246 | 2215.5754 | 2247.6852 | 2279.795 | 2247.6852 | 2279.795 | 2311.9048 | 2247.6852 | 2183.4656 | 2183.4656 | 2183.4656 | 2087.1362 | 1733.9286 | 1830.2579 | 1830.2579 | 1862.3677 | 1830.2579 | 50316.0384
15 | Power Consumption of Chiller | KWH |  | 1400 | 1400 | 1300 | 1300 | 1300 | 1200 | 1500 | 1400 | 1500 | 1500 | 1500 | 1400 | 1500 | 1500 | 1400 | 1500 | 1400 | 1400 | 1100 | 1100 | 1200 | 1100 | 1200 | 1200 | 32300
16 | Specific power consumption of Chiller | (iKW/TR) |  | 0.61409 | 0.64118 | 0.60427 | 0.61343 | 0.64264 | 0.61265 | 0.77858 | 0.66061 | 0.67703 | 0.66735 | 0.65795 | 0.62286 | 0.65795 | 0.64882 | 0.62286 | 0.68698 | 0.64118 | 0.64118 | 0.52704 | 0.6344 | 0.65565 | 0.60101 | 0.64434 | 0.65565 | 0.64207
17 | Average iKW/TR |  |  | Hours 7: 0.64207 | 0.64207
18 | COP of chiller |  |  | 5.7255 | 5.4836 | 5.8186 | 5.7317 | 5.4712 | 5.739 | 4.5159 | 5.3223 | 5.1933 | 5.2686 | 5.3438 | 5.6449 | 5.3438 | 5.4191 | 5.6449 | 5.118 | 5.4836 | 5.4836 | 6.6712 | 5.5423 | 5.3627 | 5.8502 | 5.4567 | 5.3627 | 5.4999
19 | EER of Chiller |  |  | 19.5413 | 18.7156 | 19.8588 | 19.5624 | 18.6732 | 19.5871 | 15.4128 | 18.1651 | 17.7248 | 17.9816 | 18.2385 | 19.266 | 18.2385 | 18.4954 | 19.266 | 17.4679 | 18.7156 | 18.7156 | 22.769 | 18.9158 | 18.3027 | 19.9666 | 18.6238 | 18.3027 | 18.7711
20 | LMTD of Condenser | ºC |  | 2.609 | 1.2765 | 2.524 | 2.6005 | 2.5709 | 2.3799 | 2.4816 | 2.6883 | 2.7173 | 2.7751 | 2.7751 | 2.7751 | 2.7751 | 2.8037 | 2.909 | 2.6883 | 2.7173 | 2.6883 | 2.6591 | 2.2324 | 2.3213 | 2.1871 | 2.2918 | 2.3507 | 2.5332
21 | LMTD of Evaporator | ºC |  | 3.3941 | 3.0205 | 3.1404 | 2.9668 | 2.7361 | 2.528 | 2.9457 | 3.6575 | 3.7464 | 3.7758 | 3.9366 | 3.7758 | 3.9366 | 4.0959 | 3.7758 | 3.7169 | 3.7169 | 3.7169 | 3.4967 | 2.4943 | 2.7208 | 2.7208 | 3.0257 | 2.9967 | 3.3349